## Inspection RWHS (5 Star Hotels)
S.No | Name of Hotel | Address of Hotel | Inspected by (Committee No.) | Date of Inspection | Status of RWHS as per Inspection | Remarks/ Suggestions
1 | A. B. Hotels Ltd.(Raddisson) | N.H. 8, Mahipalpur, New Delhi-37 | I | 25.02.2015 | Satisfactory
2 | Ashok Hotel | 50-B, Chanakyapuri, New Delhi-21 | VII | 13.04.2015 | Satisfactory | (i) Display Boards indicating RWH No. be provided. (ii) Routine maintenance required
3 | Asian Hotels Ltd. (Hyatt Regency Delhi) | Bhikaji Cama Place, Ring Road, New Delhi-66 | I | 30.03.2015 | Not Satisfactory | (i) All 3 structures stagnant water was found, indicating filter media choked. Poor maintenance. (ii) The pit near new tower and swimming pool is completely covered, so not possible to inspect.
4 | Centaur Hotel & Chef Air Flight Catering | IGI Airport, New Delhi-70 | I | 21.04.2015 | Satisfactory | (i) Requires periodic cleaning and yearly maintenance.
5 | Hotel Excelsior Ltd.(Hotel Shangri -La) | 19, Ashoka Road, New Delhi-21 | III | 17.04.2015 | Not Satisfactory | (i) In RWH structure 1 stagnant water observed, dimension neither measurable nor made available by the contacted person. (ii)RWH Structure No. 2 Could not be inspected as scrap is lying over the RWH structure. The hotel submitted a reply on 22.04.2015 informing that pit no 1 has been cleaned and scrap has been removed from pit no 2 and the same has been cleaned too.
6 | Hotel Imperial | Janpath, New Delhi-01 | III | 17.04.2015 | Satisfactory | (i) Surface storm water drain also found connected with RWH systems. (ii) Advised to disconnect the same from RWH Systems.
7 | Jaypee Vasant Continental | Basant lok Vasant Vihar,New Delhi- 57 | I | 30.03.2015 | Satisfactory | (i) Well maintained.
8 | Sunair Hotels Ltd.(Nikko Hotel), | Bangla Sahib Road, New Delhi -01 | VII | 01.04.2015 | Satisfactory | (i) Minor cleaning is required in one pit on regular basis
9 | Lalit Hotel (A Unit of Bharat Hotels Limited) | Barakhamba Avenue, New Delhi-01 | VII | 15.04.2015 | Satisfactory | (i) Regular maintenance of filter media to be done
10 | Jaypee Siddharth Hotel | 3, Rajendra Place, New Delhi-08 | III | 09.04.2015 | Partially Satisfactory | (i) Stagnant water observed in R.W.H near entry gate and admitted to get clean filter media and make functional. (iii) Advised to disconnect surface drainage from R.W.H System and Roof top rainwater only to be allowed in RWH System. The Hotel submitted a representation on 15.04.2015 stating that they have rectified the deficiencies as advised by the inspecting team and now both the pits are functional.
11 | Eros Resorts & Hotels Pvt. Ltd. | Nehru Place, New Delhi -19 | I | 01.04.2015 | Satisfactory
12 | CHL Ltd.(Hotel Crowne Plaza Surya) | New Friends Colony, New Delhi-65 | I | 20.04.2015 | Satisfactory | (i) Periodoc maintenance & W/L monitoring should be taken up regularly.
13 | Sheraton New Delhi Hotel ( A unit of ITC Limited ) | District Centre, Saket, Delhi-17 | I | 24.02.2015 | Satisfactory | (i) Water level should be recorded. Tube well should be placed closer to surface for monitoring water levels.
14 | Jaksons Developers Pvt. Ltd.(Hotel Crowne Plaza) | Plot No.-3B1, District Center, Sector-10, Rohini, New Delhi -85 | II | 04.02.2015 | Satisfactory | (i) Keep the system neat and clean and leak proof with periodic checking and maintenance.
15 | Piccadily Hotel | District Centre Janakpuri, New Delhi -58 | III | 10.04.2015 | Partially Satisfactory | (i) Stagnant water observed in RWH system No. 2& 4. Advised to get clean filter media and make RWH systems functional. (ii) Surface drains also found connected with RWH systems. Advised to disconnect surface drains and only roof top rain water to be allowed in RWH systems.
16 | Divine Infrastructure Pvt. Ltd.( Indus Hotel & Spa) . | Plot No.4, Sector-13, Dwarka,New Delhi -75 | V | 31.03.2015 | Satisfactory | (i) Out of three RWH structure, one is functional Annual maintenance/ work in progress in 2 structures. One borewell, STP, ETP exist.DJB Connection exist, but no water supply, water supply through private tankers.
17 | Unison Hotels Ltd. | Plot No. 2, Nelson Mandela Road,Vasant kunj, New Delhi-70 | V | 27.03.2015 | Satisfactory | (i) Water is stagnant in 2 pits. Filter media should change. No DJB Water connection. 06 Nos.TWs. One STP: ETP exist. RWH pit are also being used as surface water storage tank, excess water diverted to STP Plant through pumps.
18 | Tirupati Infraprojects Pvt. Ltd.(Indus Hotels & Spa) | Plot No D , District Centre , Paschim Vihar, New Delhi-63. | III | 16.04.2015 | Partially Satisfactory | (i) Stagnanat water observed in the second RWH Sysytems ( Sr. No. 2). (ii) Needs cleaning and regular maintenance of RWH Systems.
19 | Today's Hotel (Crowne Plaza) | Plot No 1, Community Centre, Okhla Industrial Area, Delhi -20 | I | 21.04.2015 | Satisfactory | (i) The recharge well above the filter bed should be blind (not slotted). The pit near the out gate needs to be cleaned.
20 | Aman Hospitality (Kempinski Ambiance Hotel Delhi) | 1, Central Business, District Karkardoma,New Delhi 32 | VIII | 20.04.2015 | Not Satisfactory | (i) RWH structures could not be inspected as all the mainholes of RWH was found fixed. (ii) Layout plan andd drawings of RWH was not present at sie as reported. (iii) Civil mantenance team were not present at this site to opem or break the fixed mainholes of the pits.
21 | Eros Resorts & Hotels Pvt. Ltd.(Double Tree by Hilton) | A-13, Mayur Vihar,District Centre, New Delhi-92 | VIII | 25.03.2015 | Not Satisfactory | (i) All the three Rain Water Harvesting structure found filled/ submerged with stale water (ii)Overflow outlets of all the three structure are connected with municipal drain.
22 | Eros Resorts & Hotels Pvt. Ltd. ( Hilton) | 13 B , Mayur Vihar,District Centre, New Delhi-92 | VIII | 25.03.2015 | Not Satisfactory | (i) Out of Three RWH structure two were found filled/ submerged with water (ii)All the three structure overflow outlets are connected with municipal drain.
23 | Hotel JW Marriot | Hospitality District, Aerocity, New Delhi-37 | V | 31.03.2015/ 17.04.2015 | Not Satisfactory (31.03.2015)/ Satisfactory (17.04.2015) | (i) One structure is satisfactory. Two nos. structures filled with waste water looking like garbage drain.. Need immediate maintenance & removal of garbage and waste water which pollutes groundwater. No DJB water connection, no ground water connection.Water supply through DIAL & Water tanker as per requirement. The unit submitted its reply on 10.04.2015 regarding reinspection of RWHS. Reinspected on 17.04.2015 (i) All three structures are cleaned and filter media replaced. Strucutres are dry. Water takes through recharge well. Sewer manhole are constructed adjacent to RWH structures. Water supply through DIAL. No DJB Water connection, no ground water boring.
24 | Holiday Inn Hotel | Hospitality District, Aerocity, New Delhi-37 | V | 27.03.2015 | Satisfactory | (i) Filter media should be cleaned regularly. In one pit water is stagnant. No DJB Connection, no ground water boring. One STP exist. Water is being supplied by DIAL and through Water tankers as required by Private Agency
25 | Lemon Tree & Red Fox Hotel | Hospitality District, Aerocity, New Delhi-37 | V | 31.03.2015 | Satisfactory | (i) Water is stagnant in the strucutres.In one structure, water come to RWH structure after desilting chamber. Other than rain water also come to the strucutre. No DJB connection, no borewell. Water supply through DIAL as well as through water tankers.Only rain water should diverted to the strucutre. All storm water drain should be cleaned.
26 | Ibis Hotel | Hospitality District, Aerocity, New Delhi-37 | V | 27.03.2015 | Not Satisfactory | (i) Water is stagnant in both pits. No groundwater boring. Water supply by DIAL, no DJB connection. In case of emergency water bought by tankers. STP exist.