  DECISIONS TAKEN BY  BMW COMMITTEE NO.1 IN THE MEETING HELD ON 4TH & 8th SEPTEMBER 2009, W.R.T AGENDA NO 2  (58 CASES OF GOVT.HOSPITALS/RESEARCH INSTITUTES)   (ANNEXURE -2 )


	Sl.No
	Name and Address of Unit 
	Bed (No.)
	Date of application for Authorisation
	Date of application under Water/Air Acts
	Brief Status 
	Decision Taken on 01.06.09
	ATR/status
	Decision Taken on 4th ,7th & 8th Sept,2009

	1
	Maharaja Agrasen Hospital, West Punjabi Bagh, New Delhi- 26
	350
	01.06.07
	10.09.05 (CTO), 04.04.08 (CTE)
	1. Applied for CTO on 10.09.05,Authorisation on 01.06.07 & CTE on 04.04.08.
2.Letter issued on 26.05.08 for the installation of (a) SWHS (b) RWHS (c) CFL (d) ETP (e) Plantation of trees along side of the periphery of the Hospital building.Affidavit submitted. 
3. Reply received  giving pointwise compliance of 5 points, 
SWHS-Yes, 
RWHS-Yes, 
CFL-Yes,
ETP- In Progress & near completion.
4. Reply received on 31.08.09 informing that they have now engaged M/s Watchem Ions engineers Pvt. Ltd for remaining work of ETP in place of M/s Biotech Services since the letter 1 was filled to operationalise the ETP & submit the treated water testing report by authorised agency. 
	Ask the unit to file adequacy report of the ETP from empanelled consultant of DPCC within one month.
	1.Letter issued    on 03.06.09. 
2.Reply recevied on 31.08.09.
	CTE granted . Ask for fresh CTO & also for Adequacy report for ETP.

	2
	Tirath Ram Hospital,  2, RBL, Ishwar Das Sawhney Marg, Rajpur Road, New Delhi-54.
	165
	28.07.06
	11.01.07
(CTO) 11.4.08
(CTE)
	1. Applied  for Authorisation on 28.07.06, CTO on 11.01.07 &  CTE on 11.04.08.
2. As per the general decision taken on 06.05.08, letter issued for installation of:(a) SWHS (b) RWHS (c) CFL (d) ETP (e) Plantation of trees along side of the periphery of the Hospital building.
3.As per the decision taken in meeting on 13.06.08 CTE granted
4.Reply received on 28.05.09
SWHS-Yes
RWHS-Yes
ETP-will be completed by 15th July.
CFL-Yes
Mercurybsaed instrutment are phased out.
	Call on in next meeting.
	________
	Ask for fresh Authorization application & adequacy report for ETP.

	3
	Shanti Mukund Hospital, 2, Institutional Area, Vikas Marg Extension, Delhi-92
	144
	07.11.07
(Renewal)
	09.03.07
(CTO)
	1.Applied for CTO on 09.03.07 & renewal of Authorisation on 07.11.07 & not Applied for CTE.
2.NMR submitted from RITES Limited which is not an approved laboratory from DPCC and results do not indicate Insertion Loss. 
3.Not Applied for Consent to Establish.
4. As per the general decision taken on 06.05.08, letter issued for 5 point compliance.
5.As per the decision taken in the meeting on 13.06.08 the quantity of the waste water was ascertained by EE.
6.Called for personal hearing on 02.03.09
7. As decided in the meeting held on 02.03.09 unit was asked to apply for CTE. Letter issued.
8.Reply received on 29.04.09 about the 5 points:
ETP- ask for exempetion
Mercury based instrutment will be phaseout.
	Issue SCN u/s 5 for non compliance of directions issued to the unit earlier. 
	1.SCN Issued on 03.07.09. 
2.No reply recevied
	Show Cause Notice u/s 21 of the Air Act for prosecution.

	4
	Max Balaji Hospital, 108-A ,  IP Extension, Patparganj, Delhi-92
	134
	Granted
(17.08.10)
	30.06.08
Issued
(CTE)  24.03.09
Issued
 (CTO)
	1.Authorisation granted & valid upto 17.08.10,CTO Granted on 24.03.09 & CTE granted on 30.06.08.
Reply  received 29.10.08 stating that ETP already installed.
2.Reply recevied on 24.02.09 stating that SWHS has been installed & also submitted Adcquecy report from GGSIPU.
3.Reply 24.4.09 received alongwith affidavit regarding built up area, layout plan of STP
4.As decided in the meeting held on 02.03.09 it was decided to issue CTO & Authorisation. CTO & Authorisation issued.
	No action.
	________
	No action

	5
	Balaji Medical  & Diagnostic Research Centre, 108-A, I.P. Etxn., Patparganj, Delhi-92 
	260
	 
	31.03.08
(CTE)
	1.Applied for CTE on 31.03.08,
2.Reply received informing total plot area 4000sq m, expected built up area 15000-16000sq. M(appox), SWHS will be installed,                                                                            affidavit submitted. 
2. As decided in the meeting held on 02.03.09 it was decided that unit be inspected by Dr. T.K Joshi's team. unit was inspected & the it was observed that building construction for the hospital was going on. 
3. Reply received on 6.07.09 stating that they have alot a sepreate plot of land & enclose a copy of letter issued by DDA .                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                           
	Since there is already constructed area in plot no 108-A by the name Max Balaji Hospital, it is found that this additional construction for covered area to 15000 -16000 sqm for Balaji Medical & Diagnostic Research Centre on the same plot will be integral part of Max Balaji Hospital. The total area is  more than 20000 sqm hence
	1. Letter issued on 08.06.09. 
2. Reply received on 06.07.09 requesting for issuance of CTE
	The matter may be reffered to SEIAA for the confirmation w.r.t Environmental Clearance.

	 
	 
	 
	 
	 
	 
	environmental clearnace will be required. Unit be asked to apply for E.C before the SEAC and not to proceed any activity without  environmental clearnace. This may be informed to the unit without waiting for the minutes. 
	 
	 

	6
	Pushpawati Singhania Research Institute, Sheikh Sarai Ph-II , Press Enclave Marg, New Delhi-17
	114
	02.06.06
	12.08.08 
(CTE)      29.02.08.
(CTO)   
	 1.Applied for Authorisation on  02.06.06, CTE on 12.08.08, CTO on 29.02.08.
2.As per the general decision taken on 06.05.08, letter issued for installation of:
(a) SWHS (b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees. 
3.Reply received on 28.05.09 regarding 
SWHS-Yes
RWHS-under process 
CFL-Yes
PLANTATION-Yes
ETP/STP-under process
Mercury based instrutment are removed in phased manner.
4.Reply received 13.07.09 asking for the alternatives for PVC blood bags 
	Call for personal hearing in next meeting.
	1.Letter issued for personal hearing.
	Unit attended personal hearing on 04.09.09. The unit will apply for CTO and submit the  present status alongwith time bound programmew.r.tinstallation of ETP ,within 15 days. 


Granted


Issued

26.12.07

(CTO)

Issued

(17.03.08)


1.Authorisation granted on 26.12.07, CTO on 26.12.07 & CTE on 17.03.08.

2. As per the general decision taken on 06.05.08, letter issued for installation of:

(a) SWHS (b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees

3.Reply received on 26.07.09 regarding 

SWHS-Yes

RWHS-under process

CFL-Yes

PLANTATION-Yes

ETP-under process


1. Reminder issued on 23.06.09. 

	2. Reply received on 26.06.09 regarding replacing of mercury based thermometers etc., installation of solar water heating system & progress of rain water harvesting system & ETP.
	Ask for  adequacy report for ETP.

	8
	Vidyasagar Institute of Mental  Health and Nuero Sciences, 1, Institutional Area, Nehru Nagar, New Delhi – 65
	110
	06.11.07
	21.08.08 (CTE)
06.11.08
(CTO)
	1. Applied  for Authorisation on 06.11.07, CTRon 06.11.08 &  CTE on 21.08.08.
Reply dated 12-06-08.was received along with copies of registrartion for certificate and noise monitoring report.  
2. As per the general decision taken on 06.05.08, letter issued for installation for installation of:
(a) SWHS (b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees
3.EE(BMW)  talked to the official (s) of the hospital .
4.Reply received on 06.10.08 satating that 
RWHS- having own water harvesting system with owm R.C.C under ground water tank.
Taken permission from CGWA for 2bore wells, 
For Noise monitoring report on 21.11.08
ETP- negotiations are going on.
5.Reply received on 27.05.09 regarding Mercury based instrutments has been phased out.
	Call on in next meeting.
	_______
	Show Cause Notice  for refusal of authorization under BMW Rules.

	9
	Brahm Shakti Hospital & Research Centre, U-1/78, Budh Vihar, Rohini, Delhi – 41
	105
	13.10.08
	23.06.09
(CTE) 
06.02.09 (CTO)
	1. Applied  for Authorisation on 13.10.08 CTO on 06.02.09 &  CTE on 23.06.09. 
2.As per the general decision taken on 06.05.08, letter issued for installation of SWHS, RWHS, ETP, Replacement of ordinary Bulbs with CFL 
3.The unit came for personal hearing on 02.03.09.. Reply received dated 16.5.09 regarding 5 points, SWHS-Yes, RWHS-Yes, CFL-Yes, ETP-Under process(Will be completed by june-09).
4.Reply received on 17.06.09 stating that STP- Under process & apporach GGSIPU for adquecy of design of STP.
	Call on in next meeting.
	1. Reply received on 17.06.09 informing that they are in the process for installation of STP & getting the adequecy report from Guru Govind singh Inderprastha University
	Show Cause Notice  for refusal of authorization under BMW Rules.

	10
	R.L.K.C  Hospital ( A Unit of Dr. R.L.Khera Charitable Trust )   Pandav nagar, near . Shadipur Depot, Delhi 08
	104
	23.02.09
(Renewal)
	08.02.07
(CTO)
26.06.08
(CTE)
	1. Applied  for Renewal of Authorisation on 23.02.09, CTO on 08.02.07 &  CTE on 26.06.08. 
2.As per the general decision taken on 06.05.08, letter issued for installation of:(a) SWHS(b)RWHS(c) Replacement of ordinary Bulbs with CFL(d)  ETP (e) Plantation of trees. 
3. NMR for DG Set submitted on 21.05.08
4..Reply received on 24.11.08, informing that patel nagar area does not fall in notified areas & CGWA permission is not necessary.Regarding ETP/STP quatations have been called for. letter along with copy of valid agreement recieved. 
5.As decided in the meeting held on 02.03.09 Matter to be referred to DJB for CGWA Clearance.
6.Reply received on 03.07.09 regarding ETP-under process, Mercury based instrutment are being phased our in gradully manner.
	Ask the unit to file interim report.
	1. Letter issued on 23.06.09. 
2. Reply received on 29.07.09 informing that they are gardually phasing out mercury based thermameters etc & ETP/STP will be completed with in 60-70 days
	Inspection

	11
	City Hospital,B-1/1, N.E.A. Pusa Road, New Delhi-60
	102
	26.05.08
	22.11.06
(CTO) 03.04.08
(CTE)
	1. Applied  for Authorisation on 26.05.08, CTO on 22.21.06 &  CTE on 03.04.08.
2. As per the general decision taken on 06.05.08, letter issued for installation of:(a) SWHS (b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees EE(BMW)  talked to the official (s)of the hospital 
3.Reply received on 17.07.09 regarding 
SWHS-Yes
RWHS-under process
CFL-Yes
ETP-Yes
PLANTATION-Yes
Mercury based instrutment has been phased out.
	Issue final reminder for full compliance.
	1. Letter issued on 23.06.09. 
2.Reply received on 17.07.09 regarding the compliance of the five points.
	CTE granted . Ask for Adequacy report for ETP & status of RWHS.

	12
	Bensups Hospital, Near K.M. Chowk, Sector-12, Dwarka, Delhi - 75 (B.R.Dhawan Charitable Trust)
	100
	22.02.07
	31.08.09(CTO) 29.02.08
(CTE)
	1. Applied  for Authorisation on 22.02.07, CTO on 31.08.09 &  CTE on 29.02.08. 
2. As per the general decision taken on 06.05.08, letter issued for installation of:(a) SWHS (b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees
3. As per the decision taken in meeting on 13.06.08 CTE granted and EE ascertained the waste water generation.
3.Reply received on 23.09.08 regarding
SWHS-Yes
RWHS-Yes
CFL-Yes
PLANTATION-Yes
4. Reply recived on 05.03.09 regarding phaseing out of mercury based thermometer and BP Instrument and installation of ETP.
5.Letter received on 16.07.09 regarding change of name of hospital in CTE.
	Call on in next meeting.
	1. Reply received on 16.07.09 informing that the CTE was applied in the name of M/s BR Dhawan Memorial Charitable Trust due to clearical mistake & M/s Bensups Hospital is the unit of M/s BR Dhawan Memorial Charitable Trust.
	Put up administratively & also inspect the unit.

	13
	Delhi Heart and Lung Institute, 3-M.M II ,Panchkuian Road,N.Delhi-55
	100
	04.09.06
	19.3.2008(CTE) 15.05.08
(CTO)
	1.Applied  for Authorisation on 04.09.06, CTO on 15.05.08 &  CTE on 19.03.08.
2. As per the general decision taken on 06.05.08, letter issued for installation of:(a) SWHS(b) RWHS (c) Replacement of ordinary Bulbs with CFL (d) ETP (e) Plantation of trees.
3. EE(BMW)  talked to the official (s) of the hospital .. 
4. Fax letter dated 04.10.08 received alongwith NMR meeting the insertion law. 
5.Reply received on  18.03.09 that the informing 
RWHS-Yes
SWHS -in the final stage of completion
 ETP- will be installed as soon as possible
Mercury waste heating system has been phased out
6.As decided in the meeting held on 02.03.09 letter for full compliance was issued on 08.04.09.
7.Reply received on 17.08.09 informing ETP has been installed, apporach GGSIPU for adquecy of design of STP& NMR for D.G set of 500 KVA submitted.
	Call on in next meeting.
	Reply received on 17.08.09 informing ETP has been installed & NMR for D.G set of 500 KVA submitted.
	CTE granted. Ask to apply for fresh authorization and to submit adequacy report for ETP.

	14
	Devki Devi Foundation ( Max Devki Devi Heart & Vascular Institute ) 2, Press Enclave Road, Saket, New .Delhi -17.
	193
	30.04.08
	26-9-06         (CTO)
18.03.08
(CTE)
	1. Applied  for Authorisation on 30.04.08, CTO on 26.09.06 &  CTE on 18.03.08.
2. As per the general decision taken on 06.05.08, letter issued for installation of:(a) SWHS (b) RWHS(c) Replacement of ordinary Bulbs with CFL 
(d)  ETP (e) Plantation of trees.
3.Reply received on 13.02.09 received asking for the present authorization status of CBMWTF. 
4.Reply dated 25.05.09 received regarding compliance on 5 points.
SWHS-Yes
RWHS-Yes
CFL-Yes
ETP-Yes
PLANTATION-Yes
5.As decidied on 02.03.09 the unit was asked to file the full compliance for the eariler decision. Letter issued
6.Adequacy report for ETP submitted on 31.08.09.
	Suitable reply be sent by the BMWM Cell for adequacy report.
	1. Letter issued on 01.07.09. 
2.Adquecy report submitted on 31.08.09.
	CTE, CTO & Authorization granted.

	15
	Max Super Specialty Hospital, 1,Press Enclave Road,Saket, New Delhi-17 
	104
	Granted
(30.10.10)
	30-10-10.
(Valid upto) 
CTO
23.09.08
(CTE)
	1.Authorization granted and valid upto 30-10-10,CTO Valid upto 30-10-10 & Applied for CTE on 23.09.08.
2. Personal hearing was given on 30.10.08.Reply received and informed that placed order for SWH System. Reg. EC, notification of MOEF dated  07.07.2004 has been quoted and claimed that said notification is not applicable.
3.Letter dated 12.02.09 received asking for the present authorization status of CBMWTF.
4.Reply dated 25.05.09 received regarding compliance on 5 points.
SWHS-Yes
RWHS-Yes
CFL-Yes
ETP-Yes
PLANTATION-Yes
5.Reply received on 07.07.09 informing that they have installated flow meter with STP. 
	Ask the unit to install flow measuring device  with STP as advised in the adequacy report. 
	1. Letter issued on 23.06.09. 
2. Reply received informing that flow meter has already been installed with the STP
	The matter may be reffered to SEIAA for the confirmation w.r.t Environmental Clearance.

	16
	Jessa Ram Hospital (A unit of R.B.Seth Jessa Ram & Bros Charitable Hospital)  WEA Karol Bagh,New Delhi -05
	79
	12.03.07
	30.10.07
(CTO) 23.5.2008(CTE)
	1. Applied  for Authorisation on 12.03.07, CTO on 30.10.07 &  CTE on 25.05.08.
2. As per the general decision taken on 06.05.08, letter issued for installation of:(a) SWHS (b) RWHS(c)Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees.
3.Unit was inspected on 15.09.08, defeciences observed were no seprate record for Sharp Waste was found,less number of bins were provided at storage site.Letter issued.Reply received informing that rectification of defeciences had been done.
4. Letter dated 19.11.08 received and requested to review the decision for ETP installation since having less than 100 beds, or extend the time for installation of ETP
5.As decided in the meeting held on 29.01.09 Final Reminder was issued on 17.02.09
6.As decided in the meeting held 02.03.09 letter was issued on 21.04.09 asking the unit to install ETP & send complince within 10 days.
7.As decided in the meeting held on 27.04.09 letter was issud on 20.5.09 asking the unit to send Full Compliance of earlier Decision. 
8.In the meeting held on 02.03.09 unit was ask for ETP.Letter Issued
	Call for personal hearing in next meeting.
	1. Letter issued for personal hearing.
	Unit attended personal hearing on 04.09.09. The unit will submit the present status alongwith compliance status on the 5 points ,within 15 days. ETP & RWHS as informed , is to be installed & adequacy report for the ETP to be submitted within 3 months.

	17
	Shroff Charity Eye Hospital, 5027, Kedar Nath Road ,Daryganj, New Delhi-02
	56
	26.05.06
	22.09.06
(CTO)
09.06.08
Issued
(CTE)
	1.Applied  for Authorisation on 26.05.06, CTO on 22.08.06 &  CTE issued on 09.06.08.
2.Reply received on 01.10.08 regarding SWHS- under process, CFL- 90% done, PLANTATION-Yes
3.Reply recieved  asking for  exemption from ETP installation. as it is a 79 bedded hospital. 
4Reply recieved informining that they have contact DJB for the RWHS as initiated the process by sending letter centre groung water CGW board for the technical guidelines informing that they have phased out all murcury based thermometers and BP instruments.Informed that for RWHS 50%subsidy can be got from DJB.
6.Reply received on 22.04.09 regarding installation of RWHS.
	Call on in next meeting.
	_________
	CTO granted. Ask to apply  afresh for authorization & also to submit status of RWHS. 

	18
	MGS Hospital, West Punjabi Bagh , Rohtak Road, New Delhi,-26
	100
	21.01.08
	 08.02.08 (CTO),
13.06.08
issued
(CTE)
	1. Applied  for Authorisation on 21.01.08, CTO on 08.02.08 &  CTE on 13.06.08. 
2.As per the general decision taken on 06.05.08, letter issued for installation of:(a) SWHS (b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees.
3.EE(BMW)  talked to the official (s) of the hospital .
4. As per the decision taken in meeting of 13.06.08 CTE issued and also EE checked the waste water generation and no of trees planted.
5. Reply dated 03.01.09 received giving pointwise compliance, 
SWHS-Yes
RWHS-under process,
CGWA Clearance-applied,
ETP-Yes as per reply received on 05.06.09.
6.Adequacy report submitted on 02.09.09. 
	Ask the unit to file adequacy report and permission from DJB for ground water extraction as per new orders.
	1.Letter 
issued on 23.06.09 
2.Adequacy report submitted..
	CTO & Authorization granted. Well drafted letter to be sent to GGSIP University regarding their comments w.r.t Haz. Waste in the Adequacy report. 

	19
	Kalra Hospital, A- 5 & 6, Kirti Nagar, New Delhi-15
	100
	04.06.07
	14.09.09.
(valid upto)
CTO   29.01.09
(CTE)
	1. Applied  for Authorisation on 04.06.07, CTO valid till  14.09.09 & Applied for  CTE on 11.04.08.
2.As per the general decision taken on 06.05.08, letter issued for installation of:(a) SWHS b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees
3. Personal hearing was given on 30.10.08.Reply dated 03.01.09 received stating that CTE will be applied shortly, quotations are finalized for installation of SWHS & ETP.
4.Reply received on 18.05.09 compliance of 5 points.
 SWHS-Yes,
RWHS-Yes,
CFL-Yes,
ETP-Yes,
PLANTATION-under process
Mercury has been phased out completely.
	Ask the unit to file adequacy report from empanelled consultant of DPCC.
	1. Letter 
issued on 23.06.09. 
2.No reply received
	CTE granted.  Ask for adequacy report for ETP and also the status of remaing points..

	20
	Max  Hospital ( A unit of Max Health Care Institute Ltd.) HB Twin Towers, A 2,3,&4, Netaji Subash Place, Wazirpur, Distt. Centre, Delhi-34
	92
	29.12.06
(Renewal)
	17.01.08 (CTO), 18.3.2008
(CTE)
	1. Applied  for Renewal of Authorisation on 29.12.06, CTO on 17.01.08 &  CTE on 18.03.08.
2.Reply received on 29.05.09 stating that they have phased out mercury based instruments.
3.Adequacy Report submitted on 20.01.09.
4.Reply recieved on 22.07.09 stating that they do not require CGWA clearance & submitted copy of orders from goverment of NCT Delhi.
5.Unit was inspected on 18.08.09 BMWM was found satisfactory & ETP found operational. 
	Ask the unit to file permission from DJB for ground water extraction as per new orders. Dr. T.K. Joshi's team to inspect. 
	1. Letter issued on 23.06.06.
2.Reply reecived on 22.07.09 stating that they donot require CGWA Clerance.
	CTO & Authorization granted. Inform DJB accordingly.

	21
	National Heart Institute, 49- 50, Community Centre, East of Kailash, New Delhi-65
	80
	07.03.07
	15.07.08
(CTE)
	1.Applied for CTE on 15.07.08 & authorisation on 07.03.07.
2. EE(BMW)  talked to the official (s) of the hospital.
3.Reply dated 14.10.08 received alongwith copy of a letter asking Shriram laboratory for collection of sample of STP water for analysis, CGWA certificate enclosed
4. Reply received 04.03.09 received informing the phasing out of Mercury Based thermometer and BP instrument, also enclosed NMR  and  informing  obtaining of quatation for ETP & STP. 
5.Submitted the copy of agreement with synergy waste management received on 11.05.09
	Call on in next meeting.
	_______
	Inspection

	22
	Sitaram Bhartia Institute of Science & Research, B-16, Qutub Institutional Area, New Delhi – 16
	71
	11.10.07
	11.10.07  29.04.08(CTE)
	1. CTE issued on 02.07.08, applied for CTo on 11.10.07 & for authorisation on 11.10.07.
2. HCU had submitted the applications for Renewal of authorization under BMW Rule.
3.Reply dated 20-05-08.was received .regarding submission of balance fee of 2years  for the authorization amount.
4.Reply received 5.5.09 phasing out use of mercury.
5.Hospital was inspected on 11.08.09 and following deficiencies were observed :-Sharp waste management was not proper, Isolated storage site for BMW was not provided,Labelling was not observed, Lack of training aweranes among the staff, BMW record keeping needs improvement.    
	Dr. T.K. Joshi's team to inspect. 
	Inspected on 11.08.09 & deficiencies were observed
	Show Cause Notice for revocation of Authorization.

	23
	Deepak Memorial Hospital, 5, Institutional Area,  Vikas Marg Extn. 2 , Delhi-92
	60
	19.02.07
	29.5.2008(CTE)     29.5.2008(CTO)
	1.Applied  for Authorisation on 19.02.07, CTO on 29.05.08 &  CTE on 29.05.08.
2. As per the general decision taken on 06.05.08, letter issued for installation of SWHS, RWHS, ETP, Replacement of ordinary Bulbs with CFL 
3. EE(BMW)  talked to the official (s) of the hospital 
4. Reply received on 10.07.09 alongwith affidavit for built up area for new construction & Mercury instrutments are phased out
	Call on in next meeting.
	Reply received on 10.06.09 along with an affidavit for covered area & regarding phasing out of mercury based thermameters etc.
	Send a letter to submit proposed & existing built up area alongwith drawing approved by MCD. Unit to apply for CTE for revised/ proposed Establishments. 

	24
	Nazar Kanwar Surana Hospital(A Unit of Bram Health Care (P) LTD), 219/220, N.K. Surana Marg, Gulabi Bagh, Delhi - 07
	60
	05.05.06
	05.09.08
(CTE & CTO)
	1. Applied  for Authorisation on 05.05.06, CTO on 05.09.08 &  CTE on 05.09.08.
2.Phone  call from Mr.singh on 11-06-08.regarding action taken report.
3.Unit was called for personal hearing on 27.04.09.Letter Issued.
4.Reply recieved on 02.06.09 stating that they need time of 2 months for installation of SWHS,RWHS,ETP & CFL
	Call on in next meeting.
	Unit is asking for time of 2 months regading 5 points
	Show Cause Notice for refusal of CTE & CTO.

	25
	Venu Eye Institute & Research Centre, 1/31, Institutional Area, Phase – 2 ,  Sheikh Sarai, New Delhi-17
	60
	18.09.06
	16.03.07  (CTE)   9.07.08
(CTO) 
	1. Applied  for Authorisation on 18.09.06, CTO on 09.07.08 &  CTE on 16.03.08.
2.Noise monitoring report submittd on 03.10.08
3. it was decided on meeting held on 02.03.09 unit was ask to file CGWA clearance.Letter Issued
4.Letter received on 01.07.09 regarding change of Medical Superidentent
	Call on in next meeting.
	No information given regading CGWA clearance.
	CTE, CTO &  Authorization granted Inform DJB for withdrawl of ground water . 

	26
	Jeewan Hospital & Nursing Home Pvt. Ltd., Gali No.1  Jeewan Nagar, New Delhi-14
	60
	04.01.08
	 04.01.08 (CTO)      19.12.08
Issued
(CTE)
	1.CTE was issued on 19.12.08, applied for CTO on 04.01.08 & authorisation on 04.01.08.
2. EE(BMW)  talked to the official (s) of the hospital 
3.Letter dated 30.01.09 received stating that as they are having only 60 beds they are not reqired to install ETP & hence asking for exemption from ETP installation.
4.Reply received on 29.05.09 stating that they have not received any letter regarding 5 point compliance.
	Suitable reply be sent by the BMWM Cell.
	1. Letter
issued on 03.07.09. 
2. No reply received
	Reminder Letter

	27
	Red Cross Maternity & Child care Hospital,  New Seemapuri, Delhi-95
	57
	09.04.07
	18.09.08
Issued
(CTE) 3.12.08
(CTO)
	1.CTE granted on 18.09.08, applied for CTO on 03.12.08 & authorisation on 09.04.07.
2.NMR submitted on 02.01.09
3.Reply recived on 22.05.09 stating that they have started phasing out of mercury based thermometers, the total waste water generation is 7-8 kl so they donot require  ETD.
4.It was decided in the meeting held on 02.03.09 that unit be ask to install ETP.Letter Issued
                                                                                
	Ask the unit to file interim report.
	1.Letter
issued on 23.06.09. 
2.No Reply received
	Reminder Letter

	28
	Metro Hospital & Cancer Institute ( Earlier Anand Hospital,) 21, Community Centre, Preet Vihar, Delhi-92
	52
	06.08.2007
	18.09.08
issued
(CTE)
23.06.08
(CTO)
	1.CTE issued on 18.09.08. applied for CTO on 23.06.08 & authorisation on 06.08.07.
2.Reply received on 03.01.09 stating that they are in the process of buying an ETP unit for the hospital, phasing out mercuy based instrument have been initiatied
3.As decided in the meeting held on 29.12.08 letter issued on 22.01.09 unit was asked to submit interim report. 
4.As decided in the meeting held on 02.03.09 letter issued on 08.04.09 for full compliance of earlier decision.
	Call for personal hearing in next meeting.
	Letter issued  for personal hearing.
	Call for the personal hearing in the next meeting

	29
	Jeevan Anmol Hospital, Mayur Vihar Phase-I , Delhi-91
	51
	15.01.09
	19.11.07
(CTO) 03.07.08
issued (CTE)
	1. CTE issued on 03.07.08 Applied  for Authorisation on 15.01.09 &  CTO on 19.11.07.
2. Personal hearing given on 28.11.08 and letter issued 
3.Reply received on 15.01.09, SWHS will be installed, RWHa will be installed.
4.Inspected on 11.08.09 and deficiencies observed are sharp waste management needs improvement, storage site needs imporvement, labelling is not proper, record keeping is not proper.
	The unit came for personal hearing today. The unit was asked earlier in the meeting to install  RWHS & ETP by 31.12.2008. However, it is found as per his statement that same is still to be done & it appears that there is not much progress on the ground. He was asked to get the bore-well permission from DJB. Dr. Joshi’s team to visit & found out the exact status of the unit. 
	1.letter
issued on 23.60.9 
2.Unit was inspected on 11.08.09 deficiencies were observed.
	Show Cause Notice for refusal of Authorization based on the deficiencies observed during inspection.

	30
	Park Hospital, 12, Meera Enclave (Chowkhandi) Near Keshavpur Depot, Outer Ring Road, New Delhi-18
	100
	24.07.07
	25.07.07(operate) &14.03.08( Establish) &10.06.08(Establish)
	1Applied for CTE on 28.02.08 CTO on 25.07.07 & Authorisation on 24.07.07.
2.As per the general decision taken on 06.05.08, for installation of:(a) SWHS (b) RWHS(c) Replacement of ordinary Bulbs with CFL(d) ETP (e) Plantation of trees
3. Personal Hearing was given on 30.10.08.& letter was issued as decided.
4.Reply received on 06.01.09 received alongwith Noise Mointering report & CGWA Clearancce.
5.Reply received on 26.05.09 stating that SWHS-Yes, ETP- Yes ,RWHS- submit news paper cutting given CFL-Yes,Plantation-Yes, Phasing out of use of Mercury.
	Ask the unit to file permission from DJB for ground water extraction and for installation of Rain Water Harvesting System as per new orders. 
	1.Letter issued on 23.06.09.
	CTE , CTO & Authorization granted. Ask for RWHS & letter to DJB

	31
	Bhatia Global Hospital  307-308, Ambica Vihar, New Delhi-87
	50
	05.08.04 & on 22.01.08
	 23.06.08
(CTE)
	1.Applied for CTE on 23.06.08 & for authorisation on 05.08.04.
2.Reply received on 03.02.09 stating that ETP -Yes, NMR- fee deposited with GGSIPU, acoustic arrangements made, CGWA clearance -under process
3.Adquecy report not submitted.
	Call on in next meeting.
	________
	CTE granted. Ask to apply for CTO & unit to submit Adequacy Report for ETP & Noise Monitoring Report for DG Set.

	32
	Kukreja Hospital & Heart Centre, C-1, Vishal Enclave, New Delhi-27
	103
	18.01.08(rEnewal)
	27.11.07
(CTO) 13.06.08
Issued
(CTE)
	1.CTE issued on 13.06.08, applied for CTO on 27.11.07 & for  renewal of authorisation on 27.11.07.
2.As per the general decision taken on 06.05.08, letter issued for installation of (a) SWHS (b) RWHS(c) Replacement of ordinary Bulbs with CFL (d) ETP (e) Plantation of trees
3.Unit came for personal hearing on 29.01.09.
4.Reply received on 27.05.09 received stating that they have implemented all the 5 points
5.Adquecy report not submitted
	Ask the unit to file adequacy report from empanelled consultant of DPCC.
	1.Letter issued on 23.06.09.
2.No reply received
	Reminder Letter

	33
	Jivodaya Hospital, Ashok Vihar, Phase-1, Delhi-52
	65
	29.01.08
	04.02.08
(CTO)    05.05.08
(CTE)
	1.CTE issued on 03.07.08,Authorization on 24.02.09 & CTO on 24.03.09.
2.Reply received on 17.12.08 stating that RWHS will be complete within a week.labels in hindi have been put on the BMW dustbins.
3.Reply received on 28.01.09 stating that SWHS have been installed and Mercury based instruments will be phased out in due course of time. 
	No action.
	_________
	No action

	34
	Mai Kamliwali Hospital, J-block, Community Centre, Rajouri Garden, New Delhi-27
	50
	 24.09.07
	29.09.08
(CTE)
	1.Applied for CTE  on 29.09.08 & Authorization on 24.09.07.
2.Reply dated 04.10.08 recieved stating : ordinary bulbs have been replaced with CFL,  Plantation of trees has been carried out, and order for DG set- sound proof with acoustic enclosure have been placed. 
3.Reply received dt. 12.12.08 asking for exemption from ETP installation, Submitted the copy of agreement with synergy. 
3.Reply dated 01.01.09 received stating SWHS installation will be completed within a weak, RWHS under process.
4.It was decided in the meeting held on 02.03.09 that unit be ask to install ETP.Letter issued
	Call for personal hearing in next meeting.
	1.Letter issued for personal hearing.
	Unit attended personal hearing on 04.09.09. The unit will apply for CTO within 15 days..Inspection of the unit by the team of  Dr. T.K.Joshi 

	35
	Shree Jeewan Hospital, 67/1, New Rohtak Road, Delhi -05
	52 nos.
	Granted
(24.02.09)
	03.03.08 (CTO) 
17.02.09
Issued
 (CTE)
	1. CTE issued on 17.02.09 & authorisation granted on 24.02.09 & applied for CTO on 03.03.08.
2.Personal hearing was given on 30.10.08 & It  was decided that unit to file CGWA clearnace within 1 month and  ETP is not required. 
3.Reply recieved on 07.01.09 submitting CGWA Clearance / cerificate of registration from CGWA. 
4.Reply received dtd 16.5.09 regarding phasing out of mercury in  B.P.instruments.
	Call on in next meeting.
	__________
	CTO granted. Issue letter to DJB regarding withdrawl of ground water.

	36
	Jaipur Golden Hospital, 2, Institutional Area , Sec-3, Rohini, Delhi-85
	256
	0.9.06.08
	08.09.08( CTO )  29.10.08
(CTE)
	1.Applied for authorisation on 09.06.08 , CTO on 08.09.08 & CTE on 29.10.08.
2.As per the general decision taken on 06.05.08, letter issued for 5 point complince.
3. Reply dated. 27.11.08 received stating that SWHS has been installed & ETP Installation is under process & will take 2-3 months time.
4. Personal hearing was given on 30.10.08. and as decided letter was issued.
5.Letter recieved on 20.05.09 submitting NMR.
6.Reply recieved on 17.06.09 stating
RWHS-yes
Replacement with CFL-yes
ETP-under process
                                                                                                                                
	Suitable reply to be sent to the unit by the BMWM Cell.
	1.Letter issued on 23.07.09. 2.Reply received on 17.07.09 regarding compliance& ETP will be completed in another 4months
	Show Cause Notice for refusal of autorization & CTO.

	37
	Sunder Lal Jain Charitable  Hospital, Ashok Vihar, Phase III, Delhi-52
	178
	04.12.06.
	30.05.08
(CTE)
10.01.07
(CTE)
	1.Applied for CTE  on 30.05.08, CTO on 10.01.07 Authorization on 04.12.06.
2.NMR submitted on 3.10.08.
3.As per the general decision taken on 06.05.08, letter issued for installation of (a) SWHS (b) RWHS(c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees .
4.Reply recieved on 25.02.09 recieved stating  that Mercury based  thermometers & B.P instruments have been phased out. 
5.Letter recieved on 11.07.09 stating
ETP-under process
RWHS-yes
	The unit came for personal hearing today and confirmed that RWHS is already complete and 45 % of the ETP has been done & remaining work will be completed by Aug, 2009 he has already applied for CTE. Substantial plantation has been done. A letter in this regard was handed over by himself and same be taken on the record. He was asked to submit  
	1.Letter issued on 23.06.09.
2.reply received on 13.07.09 stating that ETP will be copmleted by 31.08.09
	CTE granted. Ask for Adequacy report for ETP.

	 
	 
	 
	 
	 
	 
	an interim report about the ETP installation by 20.07.2009. 
	 
	 

	38
	Rajiv Gandhi Cancer Institute &Research Centre, Sector-VI, Rohini, New Delhi-85
	162
	01.07.09
(renewal)
	29-12-06
(CTO) 03.7.09
(CTE)
	1.CTE granted on 03.07.09, authorisation issued, valid till 2.7.09 & applied for CTO on 29.12.06 .
 2.As per the general decision taken on 06.05.08, letter issued for installation of (a) SWHS (b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees .
3. Reply received dated 18.05.09 regarding 5 points, SWHS-yes,RWHS-Yes, STP-Yes, CFL-Yes, Plantation-Yes. 
4.Adequacy report not submitted.
	Ask the unit to file adequacy report from empanelled consultant of DPCC.
	Letter issued on 23.06.09. No reply received however applied for renewal of authorization on 01.07.09
	Reminder for Adequacy report for ETP.

	39
	Indian Spinal Injuries Centre, Sector-C, Vasant Kunj, New Delhi-110 070
	115
	15.11.07
	29.02.08
(CTO)
10.07.08
(CTE)
	1.Applied for CTE  on 10.09.08, CTO on 29.02.08 & Authorization on 15.11.07.
2.As per the general decision taken on 06.05.08, letter issued for installation of (a) SWHS(b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP  (e) Plantation of trees 
3.Reply received on 01.12.08 stating that responce from CGWA is awaited regarding CGWA Clearance.
4.Letter recieved on 20.05.09 regarding 5 points compliance:
RWHS-yes
SWHS-yes
ETP-yes
CFL-yes
Plantation-yes
6.In the meeting held on 02.03.09 unit was given personal hearing. Letter Issued
	Issue final reminder for adequacy report and permission from DJB for ground water extraction as per new orders.
	1.Reminder issued on 23.06.09.  2.reply received on 22.07.09 informing they will file required documenyt shortly.
	Reminder for Adequacy report for ETP. Letter to DJB regarding ground water extraction.

	40
	Primus Ortho & Spine Hospital ( of Delhi Hospital Society ),  2, Chandergupt Marg, Chankayapuri, New Delhi-21
	100
	10.12.07
	09.07.08
Issued
( CTE)  03.12..07 (CTO ) 
	1.CTE issued on 09.07.08,1.Applied for CTE  on 03.12.07 & Authorization on 10.12.07.
2.As per decision taken on 06.05.08, letter issued for installation of (a) SWHS (b) RWHS(c) Replacement of ordinary Bulbs with CFL (d) ETP (e) Plantation of trees. 
3.Reply received vide letter  dated 21.08.08 informing that RWHS is installed.  The ordinary bulbs have been replaced by CFL.  The trees have been planted.  ETP will be installed by 31st March 2009 .
4.Reply dated 11.02.09 received stating that SWHS-yes & ETP/STP installation under process.
5.Reply recieved on 06.07.09 stating that ETP is under construction.
	Ask the unit to file interim report.
	1.Letter issued on 23.06.09.
2. Reply received on 14.07.09 stating that work for installation of ETP/STP is under  progress.
	Ask for Adequacy Report for ETP.

	41
	Batra Hospital & Medical Research Centre, 1, Tughlakabad Institutional Area,Mehrauli  Badarpur Road, Delhi
	495
	27.05.09  (renewal)
	03.11.08
(CTE)  26.05.08
(CTO)
	1.Applied for CTE  on 03.1.08, CTO on 26.05.08 & Authorization on 27.05.09.
2.As per the general decision taken on 06.05.08, letter issued for installation of (a) SWHS (b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees
3. Insepected on 27.03.09 and deficiencies observed were sharp containers need to be sealed, Bio Hazard symbols were to be provided, for STP no trained professional was their. Deficiencies letter was issued on 20.05.09.
4.Reply received on 06.07.09 regarding rate charge for disposed of BMW with Synergy.
	Call on in next meeting.
	No reply regarding correction of deficiencies received
	Letter seeking revised application for CTE & Authorization . Also inspect the hospital for ascertaining the no of  beds etc.

	42
	Holy Family hospital, Okhla Road,
	298
	13.04.07
(renewal)
	19.01.07
(CTO)  23.10.07
(CTE)
	1.Authorization vaild till 21.06.2010.1.Applied for CTE  on 19.01.07 & CTO on 19.10.07.
2. As per the general decision taken on 06.05.08, letter issued for installation of (a) SWHS (b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees. 
3. Reply dated 01.01.09 w.r.t letter dated 23.12.08 received stating that order have been placed for SWHS,adequacy report for ETP will be submitted within 6 weak time,copy of cerificates of registration with CGWA submit
4.Reply recieved on 09.03.09 regarding phasing out of mercury based thermometer and BP instruments.
5.Unit was inspected on 18.03.09 defeciencies observed were, unit having 1 incinerator which was defunctional, no bio hazard symbols were there ,inadequate stack height, BMW was not placed in trollies at final storage site,details of STP was not available at site & proper record keeping was not their.

                                                                                                        
	Call on in next meeting.
	___
	Show Cause Notice for revocation of authorization.Also inspect the hospital for ascertaining the no of  beds etc.

	43
	Sir Ganga Ram Hospital, Rajender Nagar, New Delhi - 110 008
	500
	07.07.06
	13.11.06 (CTO)
29.09.08
(CTE). Applied  CTE for additional 117 beds on 17.08.2009.  
	1. Authorization Granted, Applied for CTE  on 29.09.08 & Authorization on 13.11.06.
2.As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.
3. Reply received  dated 04-06-08 w.r.t letter dated 26-05-8.informing about doing the needful as directed.
4. As per the decision taken on 13.06.08 letter issued..5. Reply dated 01.01.09 w.r.t letter dated 23.12.08  received stating that having CGWA clearance, have phased out mercury based thermometers & in active process of phasing out mercury based instruments.                                                                                                         
	Issue letter to the unit seeking present status w.r.t. decision of CMC dated 27.04.2009.
	1.letter issued on 14.07.09. 2.Reply received on 22.07.09 stating that deficiencies has been cleared
	CTE granted for the additional 117 beds . Inspect the hospital for ascertaining the no of  beds & also for ETP.

	44
	I.P Medical Corp. Ltd.Sarita  Vihar , Mathura Road , New Delhi-44
	661
	16.07.09(renewal)
	24.03.09
Issued
(CTO) 11.06.08
(CTE)
	1.CTO Issued on 24.03.09, Applied for CTE  on 26.06.06 & Authorization on 01.05.06 and was granted. Applied for renewal on 16.07.09.
2.As per the general decision taken on 06.05.08, letter issued for installation of (a) SWHS (b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees. 
3. Reply received ,informing that ETP under trial run and will be fully commissioned by 10.11.08.6. representation dt. 10.12.08 received regarding addition of another 200 beds in view of upcoming comman wealth games.
4.Inspected on 18.03.09 it was observed that hospital is having 3 boliers which are CNG fired,& also having an incinerator which is non functional
5.Reply received on 22.07.09 along with old CTO
	It has been noticed that Consent to Operate was to be granted as per decision taken on 02.03.09, however this Consent was to be granted only for 615 beds but the Consent to Operate was issued for 615+200 (additional proposed)  beds. Consent to Operate granted to the hospital be amended and fresh Consent to Operate (Renewal) for 615 beds be issued. Ask the hospital to
	1. Letter issued on 15.07.09. 
2.reply received however applied for renewal of authorization on 16.07.09 for 615 beds. Letter dated 27.07.09 eariler CTO submitted.
	Ask for application for CTE for additional 200 beds. Issue ammended CTE  for 615 beds asking the unit to send back the original CTE issued earlier.  Inspect the hospital for ascertaining the no of  beds etc. 

	 
	 
	 
	 
	 
	 
	apply for Consent to Operate for additional 200 beds as and when applicable.
	 
	 

	45
	Fortis  Lt. Rajan Dhall Charitable Trust, Secto-B, Aruna Asaf Ali arg, Vasant Kunj
	158
	Applied on 1.05.2006
	26.06.06 (CTE) and  1.09.06
(CTO)    
	1.Applied for CTE  on 26.06.06 & Authorization on 01.05.06 & CTO on 01.09.06.
2.As per the general decision taken on 06.05.08, letter issued for installation of (a) SWHS (b) RWHS (c)  CFL (d)  ETP (e) Plantation of trees.
3.Adquecy report submitted on 19.12.08
4.Reply received on 03.09 stating SWHS-yes,RWHS-Under process,ETP-yes, CFL-yes, Plantation-yes, Mercury based instrutment are not used.
	Call on in next meeting.
	Letter dated 11.08.09 received regarding the correction of the deficiencies
	CTE granted. Ask to apply afresh for authorization & CTO since 3 years lapsed since earlier applications.

	46
	Moolchand Hospital, Lajpat Nagar-III , New Delhi-24
	150
	Granted
(30.08.10)
	23.06.04 (CTO) 
12.08.08
(CTE)
	1.Authorization vaild upto 30.08.2010, applied for CTO on 23.06.04 & CTE on 12.08.08
2.As per the general decision taken on 06.05.08, letter issued for installation of (a) SWHS (b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees.
3.Reply received on 02.02.09 regarding 5 points SWHS-yes, RWHS-yes,CFL-in process, Plantation- Yes
4.Reply received on 09.06.09 stating that ETP-under process, deficiencies observed during inspection has been corrected                                                                                               
	Call on in next meeting.
	_________
	Show Cause Notice for revocation of authorization.

	47
	Rockland  Hospital,B-33-34, Qutab institutional Area, New Delhi-16
	130
	Granted
(31.07.10)
	27-12-06
(CTO), 17.10.08
(CTE)
	1.Authorization vaild upto 31.07.2010 CTO issued on  01.07.08 CTE applied on 17.10.08.
2. As per the general decision taken on 06.05.08, letter issued on 26.05.08 for installation of (a) SWHS (b) RWHS(c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees .
3.Personal hearing was given on 30.10.08 and accordingly letter was issued.
4.Reply received on 14.08.08 stating CFL-yes,Plantation -Yes, RWHs-yes
5.Reply received on 02.06.09 stating thatETP& SWHS will be installed on completion of expansion of new building
	Call for personal hearing in next meeting.
	Letter issued  for personal hearing.
	Unit attended personal hearing on 04.09.09. The unit will  submit the  present status alongwith time bound programmew.r.tinstallation of ETP & SWHS,within 15 days. Three months time is given for installation of ETP and in case of  non

	 
	 
	 
	 
	 
	 
	 
	 
	complianceShow Cause Notice shall be issued to the unit. 

	48
	Sant Parmanand Hospital, 18, Civil Lines, Sham Nath MargDelhi-6
	120
	18-04-07
	14.06.06
(CTO)
22.10.08
(CTE)
	1.Authorization vaild upto 31.07.2010.
2.CTO issued on 10.08.07
3. As per the general decision taken on 06.05.08, letter issued on 26.05.08 for installation of (a) SWHS (b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees
4.Reply received on 03.07.09 stating that SWHS-yes,RWHS-yes,CFL-yes,ETP-yes
5.Adquecy report not submitted.
	The unit came for personal hearing today and confirmed that only Rain Water Harvesting System and ETP instatlion is to be done from their site. For completing Rain Water Harvesting System they requied one month and the delay has happened because of non submission of design by CGWA. They further told that SWHS capacity is  2 x 600 lt/day. For ETP installation they said that it will take another 6 days & they have already communicated status from time to time.  
	1.Letter issued on 23.06.09.
2. Reply received on 03.07.09 regarding the compliance of five points
	Reminder Letter

	 
	 
	 
	 
	 
	 
	 Unit was asked to submit the full compliance by 10.07.2009 along with adequacy report and advised to put desilting chamber and oil & grease facility with the Rain Water Harvesting System.
	 
	 

	49
	Mata Chanan Devi Hospital, C-1, Janak Puri,New Delhi 
	210
	27.04.09
(Renewal)
	28.04.06
(CTO)
27.10.08
(CTE)
	1.Applied for renwal of authorization on 27.04.09,CTo on 28.04.06 & CTE on 27.10.08. 
2.As per the general decision taken on 06.05.08, letter issued on 26.05.08 for installation of (a) SWHS (b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees.
3.Reply received on 27.04.09 regarding 5 point ETP-under process, SWHS-under process, RWHS-under process,CFL-yes,Plantation-yes
4.Reply received on 03.06.09 asking for time for installation of ETP. 
	Call for personal hearing in next meeting.
	Letter issued for personal hearing.
	Representative of the Hospital was present during the personal hearing on 04.09.09 ,however it was observed that he was not fully aware / not competent enough to explain the things. Issue Show Cause Notice for refusal of authorization under BMW Rules.

	50
	Sri Balaji Action Medical Institute , FC-34, A-4, Paschim Vihar, New Delhi- 63
	200
	21.06.07
	22.06.07
(CTE) 
24.03.09
issued
(CTO)
	1. CTO issued on 24.03.09,Applied for CTO on 22.06.07 & CTE on 22.06.07.
2. As per the general decision taken on 06.05.08, letter issued on 26.05.08 for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees 
3. Reply received on 06.04.09 regarding five points compliance SWHS-yes,RWHS-yes,ETP-yes,CFL-yes,Plantation-yes.
4.Adquecy report not submitted
	The unit came for personal hearing today and confirmed that all the compliance have been made except for operationaliation of Solar Water Heating System. The adequacy report of etp installed has not been provided and the consent to establish of the unit is pending. Though Consent to Operate has been granted and valid till 2010. Unit was asked to submit the adequacy report from 
	Letter issued on 23.06.09. No reply received.
	Reminder Letter.

	 
	 
	 
	 
	 
	 
	empanelled consultants of DPCC and submit the same by 10.07.2009 and also confirmation of installationof Solar Water Heating System. 
	 
	 

	51
	Jeewan Mala Hospital(P)Ltd., 67/1, New Rohtak Road.New Delhi -05
	104
	Granted
(03.10.10)
	25.10.07 (CTO)  01.08.08
(CTE)
	1.CTO issued 25.10.07 & Authorization vaild upto-03.10.2010
2. As per the general decision taken on 06.05.08, letter issued on 26.05.08 for installation of (a) SWHS (b) RWHS(c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees.
3 CGWA clearance not submitted.
4.Reply received on 27.02.09 regarding 5 point  SHWS-under process,RWHS & ETP- quatation has been called, CFL-Yes,Plantation-yes
	Call on in next meeting.
	__________
	Show Cause Notice for revocation of authorization.

	52
	G.M.Modi Hospital and Research Centre for Medical Science, Mandir Marg, Saket , New Delhi -17
	100
	Granted
03.10.10
	Granted
(25.10.07) (CTO)   04 .09.08
(CTE)
	1. CTO issued on 25.10.07,Authorization vaid upto 03.10.2010 & Applied for CTE  on 04.09.08.
2. As per the general decision taken on 06.05.08, letter issued on 26.05.08 for installation of (a) SWHS (b) RWHS (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees.
3..Reply received on 02.02.09 giving pointwise compliance of 5 pnts: SWHS -yes(3000 lpd),RWHS-yes, CFL-yes, Plantation -Yes, Mercury based instruments have been phase out, ETP under process.
4.Reply received on 08.06.09 regarding correction of deficiencies.
5.Adquecy report not submitted
	Call on in next meeting.
	________
	CTE granted. Ask for Adequacy report for ETP.

	53
	Jeewan Mala Hospital Pvt. Ltd., 66- A/2, New Rohtak Road, New Delhi-05
	50
	Granted
30.08.10
	08.01.07
Issued
(CTO)  01.08.08 (CTE)
	1.Authorization vaild upto-30.08.2010,CTO issued on 08.01.07 & Applied for CTE on 01.08.08.
2.As per the decision taken on 13.06.08 for installation of (a) SWHS(b) RWHS(c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees 
3.Reply received w.r.t letter issued on 14.08.08 informing quotation for solar water heating system has been obtained and will be completed shortly.For rain water harvesting quotation has been called for. ordinary bulbs have been replaced by CFL.  Sapling have been planted in MCD park. between the two hospitals.  
4.Personal hearing was given  to the unit on 30.10.08. and as decided a letter was issued. it was decided to call on 27.04.09 with full compliance of eariler decisions.Letter Issued
	Call on in next meeting.
	__________
	Inspection

	54
	Jeewan Nursing Home & Hospital, 2-B, Pusa Road, New Delhi-05
	100
	11.07.07
(Renewal)
	O7.07.06 (CTO) 25.08.08
(CTE)
	1.Consent issued on 01.12.08, applied for renwal of authorization on 11.07.07 & for CTE on 25.08.08.
2.As per the general decision taken on 06.05.08, letter issued for installation of (a) SWHS (b) RWHS(c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees.
3 Reply received dt. 01.12.08 stating that insatllation of RWHS will take 2-3 months,
4. Reply received on 19.05.09 giving point wise compliance of 5 points: SWHS yes, CFL-yes, Plantation-yes, ETP-under process
	Ask the unit to file interim report for ETP.
	1.Letter issued on 23.06.09. 
2.No reply received
	Show Cause Notice for refusal of authorization.

	55
	Dr. B.L.Kapur Memorial Hospital, Pusa Road, Delhi  05
	500
	06.11.08
	Issued
15.01.09
(CTO)
Issued
(10.11.08)
(CTE)
	1.CTO issued on 15.01.09 & CTE on 10.11.08, Applied for Authorisation on 06.11.08.
2.Reply received on 26.12.08 regarding installtion of SWHS
3.Adequacy report of the ETP received on 08.03.09 
4.Inspected on 24.06.09 deficiencies observed were segregation to be done properly,sharp waste management needs improvement,STP was found not functional,proper symbols need provided 
	Dr. T.K. Joshi's team to inspect. 
	inspected on 24.06.09 & deficiencies were observed
	Show Cause Notice for refusal of authorization

	56
	Yashraj Bio-Technology Ltd., C-34.Mulund (West), Mumbai-80 ( C. Add. -Plot No -C-232, TTC Industrial Area, MIDC, Navi Mumbai-400705)
	NA
	Applied for renewal of Authorization on 29.05.09( Fee for 3 years received on 22.06.09)
	Not Applicable
	1.In respect of this unit, G.B. Pant Hospital was visited on23-3-207 and the bottles in which the BMW fluid being carried out were seen which were having Biohazard symbol and lebel however Inspection of the vehicle and arrangement used for the transportation of bio-fluid could not  verified as the no one was came to carry the fluid from the transporter during the inspection.
2.Presentation was given by the representative of the unit  before the committee on 01.08.2007 .
3.Letters were issued in the past seeking photographs etc for handlinf of BMW  and later on an affidavit was also sought regarding proper  handling of BMW fluids during the transportation and training etc to the handling staff.
4.Replies to the letters issued were received & unit submitted the asked photographs , an affidavit as asked by the BMW Committee and other information sought. 5.Authorization as decided in the BMW meeting held on 06.05.08 was issued to the unit.& remaining fee for two years was returned to the unit.6.As decided on 29.09.08 a letter was issued. Reply was received ,
letters issued as decided on 30.10.08 & 29.12.08. .
	Call on in next meeting.
	(i)Reply to the letter issued on 17.02.09 received on  27.02.09 & 27.04.09 informing about the  Training Protocol & qualification of the Trainers .
	Authorization ( Renewal ) granted.  Inspection thereafter. 

	57
	Metro Bio-Care services (P) Limited, 55,Railway Road, Samaipur Industrial Area, Delhi -42
	NA
	Applied for Renewal of authorization on 28.11.2008.
	Applied for Renewal of Consent ON 26.11.08
	1.Directions issued by CPCB u/s 5 of EPA on 03.10.07. 2.Inspected on 23-8-2007  6.SCN was issued for providing (i)sludge dewatering device.(ii). Manual mode on PLC should not be used. (iii) Rota meter should be provided at PC &SC of incinerator. 3. Reply Received along with an affidavit regarding directions given by DPCC have been complied. 4.Letter received, regarding compliance with the  directions  by CPCB..5.Unit was inspected  on 27.03.08 and compliance w.r.t directions given was observed. 6. CPCB has released the bank guarantee of unit. 7. Letter/Reply received w.r.t.letter dated 21.10.08 and. w.r.t decision taken on 30.10.08.Letter issued as decided on 28.11.08. The unit was inspected and incinerator was monitored on  20.01.09. As per the monitoring report of DPCC Laboratory, VOC in ash was exceeding the prescribed limit. Letter was issued .Monitoring report for VOC was received , parameter found within the prescribed limit. Reply received from unit regarding rates charged for BMW.  As decided by committee in its meeting held on 02.03.2009, letter was issued on 24.03.2009 to follow the rates as decided by DHS.Operator  attended personal hearing                                                                                                                                                         
	Call on in next meeting.
	(i) Reply w.r.t letter dated 08.05.09 received from DHS vide letter dated 01.06.09 and it has been informed that  there is no provision of extra Bio-Medical Waste in the contract entered with DHS under clause 2 of the agreement with M/s Synergy Waste Management Pvt. Ltd. and informed that  A proposal as mentioned in the letter of DPCC cannot be agreed to.
	Inspection to check PLC. Regarding rates to be charged for Bio-Medical Waste by the Operators of CBWTF s in Delhi,  a letter to be issued to DHS for inclusion of the factors like quantum of BMW generation, cost of bags to be supplied by the Operators etc. 

	
	
	
	
	
	on 27.04.2009. Following decisions were taken in the meeting held on 27.04.09: "  The representatives of the CBWTF came for personal hearing today. They wanted to know as to what rates should be charged for extra BMW generated by Health Care Facilities , if it is beyond 200 gm/bed/day (200 gms/bed/day is the average BMW generation as mentioned in the publication of Directorate of Health Services, GNCTD (DHS) namely “Bio- Medical Waste” in year 2006) since the agreement between DHS and M/s Synergy Waste Management Pvt. Ltd., is silent about any extra charges for extra BMW. Ask DHS in writing to clarify and inform about the same and thereafter inform the CBWTF accordingly. Inform the operator of CBWTF about the sample survey done for hospitals and rates charged by them for BMW. Ask them to confirm whether it is correct, since the operator is emphasizing that they are charging rates as per DHS agreement. The operator handed over the comparative rates chart, compare the rates mentioned by the operator in the chart with the DHS rates and put up in next meeting on 25.05.2009".                                      
	
	
	 

	 
	 
	 
	 
	 
	 
	 
	
 (ii) Reply received w.r.t 
letter issued on 12.05.09 
regarding rates
(iii) Letter dated 12.07.09 received with request 
for renewal of authr. & Consent.
(iv) A letter  dated  24.07.09 
has been received from 
Delhi Medical Association 
regarding non compliance 
w.r.t rates decided by DPCC  
by both the operators.
	 

	59
	Shriram Institute for Industial Research , 19, University Road, Delhi-07.
	----
	28.02.07
	22.08.08
(CTE)
11.11.08
(CTO)
	1.Applied for CTE on 22.08.08, CTO on 11.11.08 & Authorisation on 28.02.07.
2.This is a case of research institute which is engaged in research related with animals and generates BMW 
3.NMR pertaining to DG stacks have been submitted om 08.08.08
4.Reply received on 10.10.08 regarding 5 point RHWS-yes,CFL-yes,Plantation-yes
5.Reply received on 27.02.09 ETP will be completed by may 2009,Mercury based instrutment are phased out. 
No information about the present status of the ETP.
	Call for personal hearing in next meeting.
	Letter issued for personal hearing.
	Unit attended personal hearing on 04.09.09 and informed that ETP has been installed.. The unit wil submit adequacy report for the ETP  within one month. 

	60
	Becton Dickinson India P.Ltd., 2, Community Centre , 3RD Floor, Anand House , Saket w Delhi -17) ( Head Office at 6th Floor Signature Tower-B South City, 
	…..
	Granted
18.03.11
	_____
	1. Authorization vaild upto-18.03.2011
2.It was decided to call on 27.04.09 Issue final reminder for correction of deficiencies. 
3.Letter be pasted and sent to all known addresses.Letter Issued
	No action.
	________
	No action

	61
	M/s FoundationInternational Charitable Trust Society 306, Kohat Enclave, Pitampura, Delhi -34
	…….
	……….
	Not Applied for CTE 
	1.The project was  in the list of 18 projects provided by MoEFvide letter dated 16.04.08. Notice issued on 30.04.08 for applying for consent to establish and to submit environment clearance from MoEF 2. As decided the Unit  was asked  to file following five things :
(i)Consent to Establish
(ii)Environmental Clearance
(iii)Affidavit indicating date of start of construction and completion of construction.
(iv) Approved architectural drawing
(v) Completion Certificate.. 
2.Personal hearing was given  to the unit on 30.10.08. and as decided a letter was issued.
3.Copy of Environmental  Clearance by MOEF dated 04.11.08.
4.Reply received 15.05.09 asking for time to complete the work.
	Unit be asked to apply for Consent to Establish before start of any activity and also apply for environmental clearance.
	 
	Inspection

	62
	Oscar Bio Tech Pvt. Ltd. (Multi Super Specialty Hospital, A- Bl;ock, Shalimar Bagh, Delhi-52) office address D-5, !st floor,Okhla Industrial Area, Phase-1, Delhi-20
	550
	……..
	Applied for CTE 20.12.05. 
	Proposed date of commissioning as per application was 01.12.07.Water consumption total 830 KLD(Domestic 40KLD, sanitation 265KLD, cooling 495KLD, horticulture 20KLD & others 10 KLD). ETP with design capacity of 250KLD is proposed with secondary and tertiary treatment. Treated wastewater will be reused for cooling and horticultural purpose.DG sets- 1000KVA & 750 KVA proposed with acoustic enclosure.letter was issued on 07.03.08 asking EIA clearance.Ask the unit to file item-wise compliance of the EC conditions. Subsequently letters were issued as decided by BMW/CMC Committee. As per the decision taken on 13.06.08 Letter issued. Reply was recived w.r.t to said letter. Damages and bank Gauranttee decided by CMC (Orange) not submitted Case, was taken in the CMC (Orange) on 07.10.08. As decided  the matter was  taken by BMW Committee no. 1 in the meeting on 30.10.08.Letters were issued based on the decisions taken by the CMC(Orange). Unit had filed appeal before the Appeallate Authority ( Financial Commissioner ) and stay was given by the Appeallate Authority. The next date in the
 matter is on 01.10.09.
	Call on in next meeting.
	_________
	Follow up the case.

	63
	Society of Unique Hospital & Research Institute ( Multi Super Specialty Hospital & Research Institute at   Sector-19 Dwarka, Delhi) office address BD-73, Pitam Pura, Delhi-88
	400
	…………
	14.7.2006 
	1.The unit has applied for CTE on 14.07.06 
2.ETP with design capacity of 150KLD is proposed with secondary and tertiary treatment. DG sets- 3 nos of 750 KVA capacity each proposed with acoustic enclosure. 3nos. oil fired boilers (1500Kg/hours. It is mentioned that unit will comply with BMW Rules. 
3.EC given by MoEF vide letter dated 16.05.07.letter was issued on file an affidavit for compliance of EIA clearance conditions. The unit was asked to file item-wise compliance of the EC conditions during the construction and the general conditions. and to commit on affidavit that it will follow the  conditions in the operation phaseand was Ask for following:(i) Affidavit indicating date of start of construction and completion of construction.(ii) Approved architectural drawing(iii) Completion CertificateSubmission of revised application for Consent to Establish dated 30.01.09 submitted. 
4.As decided in the meetng held on 02.03.09 unit wsa asked for full compliance  of five point.Letter Issued 
5.Reply dated 25.05.09 received alongwith an affidavit regarding itemwise compliance of EC conditions.
	Dr. T.K. Joshi's team to inspect. 
	Inspected
	CTE granted with the condition that acoustic enclosure shall be provided within a month.

	64
	St. Stephen's Hospital Tis Hazari, Delhi-54
	595
	13-06-06 (valid up to 
5-07-09)
	CTE granted & Applied for CTR on 24.11.08
	1.  Authorization vaid upto-05.07.09, CTO issued on-24.01.07 & CTE Issued on 13.09.08.
2. As per the general decision taken on 06.05.08, letter issued for installation of (a) SWHS(b) RWHS(c) Replacement of ordinary Bulbs with CFL(d)  ETP (e) Plantation of trees
Reply received on 22.08.08 stating that SWHS-yes,ETP-yes,Cfl-Yes,Plantation-Yes
3.Inspected on 30.03.09 & deficiencies were observed
4.A representation received on 9.5.09 regarding CBWTF not following the rates of DHS.
5.Reply received on 23.05.09 regarding rectificcation of deficiencies.
	Call on in next meeting.
	________
	Inspection. Ask to apply for renewal of authorization under BMW Rules.  


1.Authorization expired on 06-06-07 & applied for renewal on 14-01-08,CTO issued on 26.05.09 & CTE issued on 24.03.09.

2.Reply received on 13.01.09 regarding SWHS is already installed.

3.Reply received on 27.02.09 stating that mercury based instrutments have been phased out 

	
	Call on in next meeting.
	_______
	Authorization ( Renewal ) granted.   

	66
	Sembramky Environmental Management  Pvt. Ltd
Khasra No. 83/22, Nale Wali Gali, Mundka Udyog Nagar, Delhi-41
	CBWTF
	Fresh Case, applied for CTE
	23-Jul-08(CTE)
	This is a fresh case.  Applied for CTE on 23-07-08 for the Establishment of Common Bio-Medical Waste Treatment Facility (CBWTF) at Mundka.
The activity “ Hazardous Waste Processing viz.hospital/medical/industrial waste” is mentioned at sl no. 46 of the list of prohibited / negative list of industries (Annexure III) of MPD 2021.  As per  the note given in the said Annexure III a Public utility service involving any of the activities referred to above shall be permitted subject to environmental laws.4. The applicant has mentioned that plot area for the said facility will be one acre.5. The applicant has mentioned that all the required equipments like incinerator (Double Chamber) with venturi scrubber, autoclaves, shredder etc. shall be installed.  ETP shall be installed and treated effluent shall be reused.6.Letter received from COI. informing that the  area for the site is not a conforming industrial area as on date. However for setting up BMW Treatment Facility in the area, DPCC may decide on its own level depending upon dire need of Delhi as well as, as per provision of MPD-2021 in 
consultation with DDA, if needed
	No action.
	___________
	CTE be granted, as it is a waste treatment facility/ public utility service. Subsequently the file was submitted for the approval of minutes and it was decided that earlier decision of " No Action" be retained.

	67
	Envirocare Waste Management Company, Co., 72-A, Baba Complex, Taimoor Marg, New Delhi-65
	CBWTF
	----------
	---------
	1.This is a case of representation received from the unit for the Establishment of Common Bio-Medical Waste Treatment Facility (CBWTF) in Delhi.
2. The unit is not having any land of its own for the said purpose and requested for providing the land. 
3. As directed by the Chairman, DPCC the case was  placed before the Committee. As decided in the meeting on 30.10.08, a letter was issued to DDA.
Reply recieved from DDA stating that they are not concerned with any kind of solid waste management and MCD / NDMC may be approached on the issue of land for the said purpose. file traced
	Call on in next meeting.
	________
	Inform that DPCC does not have any provision for allotting land for CBWTF since the land matters are dealt by land owning agencies like DDA / MCD.

	68
	Escorts Heart Institute & Research Centre, 
Okhla Road ND-25
	222
	26.05.06
	12.06.09
Issued  
(CTO)
	1.Applied for renewal of Authorization on 12.06.2009, CTO issued on 10.11.08.
2.NMR submitted on 04.09.08 
3.ETP effluent test report submitted on 25.08.08.
4.Reply received on 24.11.08 regarding carryout the necessary  action for Adequecy  Report  for STP Plant from Jamia.
5. Reply received on 17.02.09 informing that mercury based thermometer and BP instrument have been  phased out and this hospital is mercury free.
	Call on in next meeting.
	Applied for renewal of authorization on 12.06.09
	Ask for CTE & also for Adequacy report for ETP.

	69
	Altius Sonia Hospital, 1, Gulshan Park Main Rohtak Road, Nangloi, Delhi- 
	65
	24.10.2008
	Not Applied
	1. Applied for fresh Authorization under BMW rules on 24.10.08         
2. Reply received on 12.5.09  stating that unit is having 45beds hence should be exempted from applying for CTE & CTO.
3.Reply received on 18.05.09 submitted an affidavit for having 45 beds
	Ask the unit to submit copy of registration from DHS.
	1. Letter issued on 23.06.09
2. No Reply. 
	Inspection.

	70
	Dharamshila Cancer Hospital & Research Centre, Vasundhra Enclave, Delhi-96
	200
	03.09.07
	 26.05.08
(CTE)
	1.Applied for Authorisation on 03.09.07 & CTE on 26.05.08. 
2.Earlier it was in the BMW Committee No.3 but during inspection it was found that Hospital is having 200 beds hence case pertains to BMW Committee No. 1. 
3. Reply receiced dt. 05.12.08 regarding the corrrection of bulit up area & total investment. 
4.Letter dated 10.02.09 received stating that as theirs is 150 beded hospital they are not required to install ETP as decision is for 500 bedded & above Hospitals. 
5.Reply received dated 18.05.09 regarding 5 points. reply dtd 22.4.09 received stating that ETP will be installed as soon as the hospital commences the cencus beds status of 100 beds.
6.Reply received on 10.02.09 stating that they are only 150 beded hospital so they donot need to install ETP.
7.Reply received on 25.02.09 regarding the phasing out mercury based instrutment has been started.
	Call for personal hearing in next meeting.
	Letter issued  for personal hearing.
	Unit attended personal hearing on 04.09.09 and informed that RWHS has been installed . The unit wil install ETP & submit adequacy report for the ETP  within three months.


1.Applied for Consent to Establish under the Air & Water Acts, on 27.02.09 for establishment of CBWTF. As per the decision taken by the BMW Committee in the meeting on 02.03.09, an inspection of the site  was carried out  by the Team of Dr. T.K.Joshi, and the team recommended for EIA.  EIA REPORT was submitted . CTE issued on  14.05.09 as decided by the BMW Committee No 1 , in its meeting on  27.04.09. Unit has submitted representation dated 18.5.0-9 regarding change of location  of the  CBWTF  to new location   at  74, Rajasthani Udyog Nagar Industrial Area .

2.Lettr received 19.07.09 asking to issue them CTO & Authorisation.

3.An inspection has been conduced, by a team led by Dr. T. K Joshi on 02.09.09. A copy of Inspection Report is enclosed herewith.

	4. A copy of Complaint is enclosed herewith.
	Ask the unit to submit details of new proposed site for CBWTF.
	(i)Letter Issued  on 23.06.09. (ii)Letter dated 19.08.09 received regarding establishing the CBWTf at old location that is 46, ssi. (iii)A complaint has been received  From Sh Jitendra Sharma, President of Little Scholar Education Society, of Gazipur Delhi 
	Issue letter for rectification of the deficiencies observed by the team during the inspection on  02.09.09. Inspection by the team of Dr. T.K.Joshi.After receiving the  compliance report from the unit inspection be made & if defeciency observed have been removed, issue CTO. 

	 
	 
	 
	 
	 
	 
	 
	against the establishment of the said CBWTF. (iv) Request received from the Operator vide letter dated 07.08.09 regardingCentral Subsidy for establishing the said facility.(v) Applied for CTO  on 13.08.09 for the CBWTF at premises No 46, SSI  Indl. Area, Delhi. 
	 

	 
	 
	 
	 
	 
	 
	 
	along with Technical Adequacy report for ETP & Air Pollution Control Device for Incinerator.
	 

	72
	Indian Hospital;A6-35 Shalimar Bagh, Delhi-88
	82
	_______
	24.06.09
(CTE)
	Unit was inspected on 19.06.09 defeciences observed were
 no segregation of BMW was there, no proper color coding was there, staff was unaware about  BMW rules, no RWHS & SWHS was there.
	_____
	____
	Show Cause Notice  u/s 5 of EPA since not applied for the authorization.

	73
	 Max Health Care, Shalimar Bagh
	 
	 
	Applied for 
CTE
	1.This is a case of Hospital with Built Up Area more than 20000 sq. mts.
2.EC has been granted by SEIAA vide letter dated 28.08.09.
	Wait for SEIAA 
decision.
	EC has been granted by SEIAA vide letter dated 28.08.09.
	CTE granted.

	74
	Sunil blood Bank & transfusion centre 806, Arjun Nagar Kotla mubarakpur Opp. Defence Colon Delhi
	 
	8.12.04
	 
	1. Applied for Authorization under BMW rules on 08.12.04 
2. Previous authorization expire on 27.06.07
3. Not applied for renewal of authorization
4. Letter return back with the remarks of postman that the unit has left the address
	inspection to be expedited.
	inspection was conducted 24.06.09 & unit found shifted.
	Shift the case to BMW Committee No 3.

	75
	Blood bank Oranization 36, Vijay Block Laxmi Nagar Delhi-92
	 
	Not Applied
	 
	1. Reply were received along with an affidavit informing that they cater less than 1000 patients per month, a copy of agreement with SWM
	Ask the unit to correct the deficiencies observed during the inspection
	Letter issued
	Shift the case to BMW Committee No 3.

	76
	Blood bank Oranization Shanti Chamber (opp. Telephone Exchange), 11/6B, Pusa Road, New Delhi-05
	 
	Not Applied
	 
	1. Reply were received along with an affidavit informing that they cater less than 1000 patients per month, a copy of agreement with SWM
	inspection to be expedited.
	Inspection was conducted on 24.06.09 & Blood Bank Having less than 1000 doners per month. Agreement with the Synergy Waste Valid till 15.06.09
	Shift the case to BMW Committee No 3.

	77
	Medicare Products Inc., 4/7, Kirti Nagar, N Delhi-15
	 
	 
	 
	Case was taken up by B,W Committte no-1 as per decision taken by CMC (Orange) in the meeting on 21.01.09
	Call on in next meeting.s
	 
	Shift the case to CMC ( Orange)

	78
	M/s Shanti Nursing Home Ltd. E-1 Panchsheel Park, Naveen Shahdara, Delhi
	 
	Applied 
	 
	M/s Shanti Nursing Home Ltd. E-1, Naveen Shahdara, Delhi was inspected by the trainee BMW as directed by Chairman DPCC, wr.t. complaint received & as decided by the Committee the Committee held on 27.08.08 and as decided in the said meeing the case was put on file. the nursing Home is 20 heded & case pertains to BMW Committee No. 2. As decided on file action is being 
	Ask the unit to correct the deficiencies observed during the Inspection
	Letter issued
	Shift the case to BMW Committee No 2.

	79
	M/s Ayush Therepy Centre,C-62, Ist Floor, Preet ihar, Delhi-92
	 
	Appied on 05.01.09
	 
	regarding Advertisement in the news Paper by Ayush Therapy Centre as decided by the Committee in the meeting on 27.08.08, an Inspection of on eof therapy Centre of Ayush in Preet Vihar Area of Delhi (Ayush therapy Centre, C-62, Ist Floor, Preet Vihar, Delhi-92) was conducted bya Team as directed by Chairman DPCC. the Centre found engaged in activity of message using herbal/ayurvedic oil. about 100 no of people are coming to the centre per month. oil & Grease trap not provided. letter were issued as decided by the Committee and the unit applied for authorization on 05.01.09 Unit was asked to install oil & Grease trap.
	Call on 25.05.09
	 
	Shift the case to CMC ( Orange)

	80
	Dr. Lal Path Lab, E-Block, Sector - 18, Rohini Delhi-85
	 
	 
	 
	As decided in the last meeting on 30.10.08, Trainee BMW inspected the unit on 21.11.08 and following ate the main observation:-
1. it is a building under construction for Dr. Lal Path Lab and as informed the construction started in 2008 for the Pathological Laboratory at the site and sufficient work of construction has already been done. it was informed that the building will be completed in about 1 year time.
2. CTE not applied
3. The lab has the plot barea of 3800 sq. mt. and proposed build up area of 3800 sq. mt.
4. As informed by the representative of the Unit present at the site, ETP is proposed.
5. Rain Water Harvesting System proposed.
6. Solar Water heating System Proposed.
7. CFLs will be used.
	inspection to be expedited.
	Inspection was conducted on 19.06.09 & it were observed:
1. The unit was under construction, complete by 15 September 2009 & inaugrated by Jan 2010.
2. Premission regarding Ground waer could not be shown:
3. No Acoustic arrangement.
	Shift the case to BMW Committee No 3.


	Sl No.
	Name and Address 
	No. of Beds
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting held on  01.06.09


	ATR/status
	Decision taken in the Meeting on 4th, & 8thSept, 2009

	1.
	Lok Nayak Hospital, New Delhi-2
	1600


	12.01.04
	CTO-03.03.08.

CTE- 
Not Applied.
	1. Authorization is valid up to 18-2-2010. Not applied for Consent to Establish under the Air & Water Acts .Letter issued  to  Pr. Secy (Health) for Consent to Establish. Consent to Operate under Air Act is applied on 03.03.08.
2.. As per the general decision taken on 06.05.08, letter issued for installation of:

(a) Solar water heating system (b) Rain water harvesting system 

(c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

3. Hospital was inspected w.r.t News Paper Clipping & also reference was received from Hon’ble Lt. Governors office . Incinerator & Autoclave etc. were also inspected.

· Air Pollution Control Device (APCD) installed with the incinerator was found not operational.

· By pass system found existing for the discharge of the emissions of the incinerator. 

· Acoustic Enclosure / acoustic treatment of the rooms where DG Sets are kept  not provided  & adequate stack height not provided for the DG Sets

· ETP was yet to be commissioned. 

4. Complaint was received against the kabariwalas operating near the Hospital .An inspection was conducted by the PGRC officials & as decided by the CMC (orange), a Show Cause Notice was given to the hospital on 25.07.08. 

5. Reply received w.r.t said SCN stating that BMW is being managed properly and there is no pilferage of the BMW or picking up by the ragpickers . 

6. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy(Health) with copy to Pr.Secy(PWD) from chairman, DPCC was issued.

7. Point wise reply dated 16.10.08, regarding correction of the discrepancies received informing that Air Pollution Control Device is being made functional and also incinerator’s chimney has been repaired. For providing acoustic enclosures to the DG sets reply of PWD engineer enclosed. Informed that ETP installation work is complete (capacity is of 12.50KLD) and Noise monitoring report submitted.

8.. Inspection of the Hospital was conducted on 10.02.09.

· Venturi Scrubber was not in operation. Also, during earlier inspection on 23.06.08 , Venturi Scrubber system was found out of order.

· Deficiencies observed w.r.t BMW Management during inspection on 10.02.2009. 

· Monitoring of Incinerator could not be conducted due to lack of monitoring facility.

·  BMW Management not found as per Rules. Record keeping needs improvement. 

· At the Incinerator of this Hospital incinerable waste of G.B.Pant hospital & MAMC are also incinerated. 

· Proper Temperature recording system required. Should be provided.  Properly Trained /Qualified personnel for operation & Maintenance of Incinerator are required. 
·  Proper segregation of the Bio Medical Waste was not observed. Mixing of the Bio Medical Waste was observed. 

· Training / Awareness programmed for the staff of the Hospital is required seeing the improper segregation and other deficiencies observed w.r.t. Bio Medical Waste Management.

·  ETP provided but found not operating.

·  5 DG sets are without acoustic enclosure. 

· Sharp waste management not found proper.

·  Records  for BMW, needs improvement.

·  As per the report of Dr. Joshi’s team, Since, the Venturi Scrubber (Air Pollution Control Device) installed with the Incinerator is not in use/ not operating, the Hospital may be directed to not to operate the Incinerator without the operation of  Venturi Scrubber and prior permission of DPCC shall be taken in this regard. In the non operation period of the Incinerator, Incinerable Waste from the Hospital may be disposed through Common Bio Medical Waste Treatment Facilities (CBWTF) in Delhi or may be Incinerated at the other Incinerators of the Hospitals of Delhi Govt. 

9.. As per the decision on 02.03.09, D.O. Letters issued on 23.03.09 and 14.05.09 to  MS of Hospital with  a copy to PS to Minister for Health, Delhi and Pr. Secy. (Health) GNCT Delhi, for rectification of the deficiencies observed during the inspection asking unit to submit fresh  monitoring report for incinerator,  file compliance report on the five points mentioned in our earlier letters and submit Adequacy Report for ETP along with application for CTE . 

10. Reply/ fresh monitoring report not received. 

11.A complaint was received against the hospital regarding not managing BMW as per rules. Another Complaint received against the hospital on 28.04.09.

12.A news item was published in the Times of India on 06.04.09 regarding the inspection of this Hospital including other four hospitals of Delhi Government by the Health Minister of Govt. of NCT of Delhi and her observations regarding improper management of BMW particularly Sharp Waste Management. 
	Call for personal hearing in next meeting. 
	Letter for personal hearing issued. 


	M.S of the hospital attended personal hearing on 04.09.09. The unit will apply for CTE and also submit compliance report alongwith   status w.r.t 5 points & other deficiencies communicated to the hospital within 15 days.  

Also include the name of the hospital in the common D.O.Letter to be issued to Pr. Secy ( Health ) &  Pr.Secy ( PWD), GNCT Delhi for the compliance on the 5 points.



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	2.
	Guru Teg Bahadur Hospital, Shahdara , Delhi-95


	938
	22.05.07
	19.12.07 (CTO) &  

18.11.08 (CTE)
	1. Authorization is valid up to 18-2-2010. CTO applied on 19.12.07. CTE applied on 18.11.08.

2. As per the general decision taken on 06.05.08, letter issued on 26.05.08 for installation of:(a) Solar water heating system  (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

3. As decided in the meeting on 18.03.08, letter for deficiencies was issued including seeking application for Consent to Establish under the Air & Water Acts. 

4. A complaint was received against the hospital for not handling the BMW properly. 
5. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy (Health) with copy to Pr. Secy (PWD) from chairman, DPCC was issued and as decided on 27.08.08, a reminder  was issued to Pr. Secy (Health) for getting the Consent to Establish. 

6. w.r.t letters dated 23.09.08,15.07.08 & 02.05.08, HCU vide letter dated 22.10.08 submitted  Test reports for incinerator, Boiler, Noise Report for DG Sets & Regarding 5 Points informed that  matter has been reported & brought into the notice of PWD. 

7. Vide letter dated 04.10.08, HCU has requested MoEF to clarify whether ETP is required considering that Effluent of the Hospital is finally treated in Kondli STP and also apprehended that the ETP will expose the Hospital Staff and Patients to Various microbes etc. Indulgence of MOEF was sought to clarify the whole issue. 

8. Inspection of the Hospital & monitoring of the incinerator was conducted on 16.01.09. Deficiencies observed. 
· Temperatures for Primary & Secondary Chambers are not meeting the prescribed standards. 

9. Letter received from MoEF seeking provision of STP.

10. Reminder letter received on 25.03.09, regarding provision of STP.

11. As decided in the meeting on 29.01.09, D.O. Letters to MS of Hospital issued on 19.02.09 and 14.05.09 with copy to Pr. Secy (Health) GNCT Delhi, for rectification of the deficiencies observed during the inspection asking unit to submit fresh  monitoring report for incinerator,  file compliance report on the five points mentioned in our earlier letters issued.

12. Reply dated 20.03.2009, 25.03.09, 24.04.09 & 01.05.09 received regarding measures taken/ being taken. Monitoring report received for incinerator for monitoring conducted by Guru Gobind Singh Indraprastha University on 11.04.09, Combustion efficiency (98.98%) is not meeting the prescribed standard. Report not submitted for parameter VOC in ash. 


	The unit came for personal hearing today and said that for the compliance of directions on different issues, mater has been taken up with PWD and a meeting in this regard has already been fixed on 11.06.09 in the chamber of Pr. Secy (Health). They stated that for the deficiencies observed in the monitoring of incinerator, the matter has been taken up with the PWD to carry out necessary action as directed by DPCC. Unit was asked to submit the complete information regarding the progress made on different points including deficiencies, after the said meeting on 11.06.09. 
	Letter issued. Reply received on 24.07.09, regarding measures taken/ being taken.
	Reminder letter for compliance of the remaining points & also seek status on 5 points.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	3.
	Deen Dayal Upadhya Hospital, Hari Nagar, New Delhi-64
	500
	23.07.08

	CTO 16.01.08.

CTE- Not applied.
	1. Applied for Authorization on 23.07.08. Not applied for CTE under the Air & Water Acts.
2. SCN u/s 5 of EPA was issued on 6-3-2007. 

3. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Pr Secy  (Health) regarding deficiencies observed .

4. As decided in the meeting on 18.03.08, letter for deficiencies was issued including seeking application for Consent to Establish under Air & Water Acts.

5. As per the general decision taken on 06.05.08, letter issued  on 26.05.08 for installation of:

(a) Solar water heating system       (b) Rain water harvesting system           (c ) Replacement of ordinary Bulbs with CFL 

(d) ETP           (e) Plantation of trees along side of the periphery of the Hospital building.

6. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy (Health) with copy to Pr.Secy (PWD) from chairman, DPCC was issued.

7. Reminder letter was sent to Pr. Secy (Health) for getting the Consent to Establish, as decided on 27.08.08.

8. As decided in meeting held on 28.11.08, letter issued for installation of Solar Water Heating System and Rain Water Harvesting System within a month.

9. Letter dated 22.01.09 received regarding CTE Etc.

10. As per the decision taken on 02.03.09, hospital was inspected and asked to comply with the earlier decisions of the Committee, through a D.O. letter from MS, DPCC to MS of the Hospital.

	Call for personal hearing in next meeting. 
	Letter for personal hearing issued. No Reply.
	Call for personal hearing in the next meeting. Include the name of the hospital in the common D.O.Letter to be issued to Pr. Secy ( Health ) &  Pr.Secy ( PWD), GNCT Delhi for the compliance on the 5 Points  ,

	4.


	Charak Palika Hospital,  Moti Bagh ,  New Delhi-21
	150


	09.06.06 
	CTE-04.02.09

CTO- 06.02.09
	Applied for Authorization on 09.06.06. CTE applied on 04.02.09. CTO applied on 06.02.09.

1. SCN u/s 5 of EPA was issued earlier & reply was received with the remarks that all the deficiencies mentioned in SCN have been rectified.

2. As decided in the meeting on 18.03.08, letter for deficiencies was issued including seeking application for Consent to Establish under Air & Water Acts. 

3. As per the general decision taken on 06.05.08, letter issued on 26.05.08 for installation of:

(a) Solar water heating system (b) Rain water harvesting system © Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

4. Reply dated 19-06-08 w.r.t letter dated 26-05-08 received informing about doing the needful as directed.

5. As per the decision taken in meeting on 13.06.08 a letter from chairman DPCC to Chairman NDMC was issued and a letter dated 23.10.08 received.

6. Reminder to apply for CTE and submit compliance of other decisions of BMW Committee was issued as per the decision taken on 30.10.08. Reminder letter issued as decided on 28.11 08.

7. Inspection of the Hospital  & monitoring of the incinerator  was conducted on 05.02.09. Deficiencies observed: 

· VOC & Temperature range for Primary Chamber are not meeting the prescribed standards. 
· Electrically operated Incinerator. 
8. Deficiencies observed w.r.t BMW Management during inspection on 05.02.2009. 
· Sharp boxes not provided for storing sharps. 
· Proper color coded beans not provided. Proper 
· Temperature recording system required.  
· Properly Trained /Qualified personnel for operation & Maintenance of Incinerator are required which is lacking. 
· ETP provided. Auto clave and shredder found non- functional. Proper segregation of BMW not observed. 
· For DG sets acoustic enclosures not provided. 
· As per the report of Dr. Joshi’s team, the Hospital/ NDMC may be asked to close down/ not to operate the Incinerator and dispose their Incinerable waste through Common Bio Medical Waste Treatment Facilities (CBWTF).

9. As per the decision on 29.12.2008, hospital called for personal hearing on 29.01.2009.

10. As per the decision on 29.01.09, The representative of the unit came for personal hearing. It will file the CTE and CTO within a week; It has partially complied by our conditions and will comply with the remaining conditions by 02.03.2009.

11. As per decision taken on 02.03.09, D.O. Letter from MS,DPCC to MS of Hospital with copy to Chairman, NDMC, for rectification of the deficiencies observed during the inspection and monitoring. Unit to submit fresh monitoring report for incinerator. Unit to file compliance report, on the five points mentioned in our earlier letters issued. 

12. As per decision taken on 02.03.09 and 27.04.09, D. O. Letters Issued on 23.03.09 & 14.05.09 from MS DPCC to MS of the Hospital, seeking full compliance report & fresh monitoring report of Incinerator.
13. Reply received. However, fresh monitoring report for incinerator not received.
	Call for personal hearing in next meeting. 
	Letter for personal hearing issued. No Reply.
	Director (M.S) of the hospital attended personal hearing on 04.09.09. The unit will apply afresh  for Authorization  and also submit compliance report alongwith   status w.r.t 5 points & other deficiencies communicated to the hospital within 15 days.  



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	5.
	Ram Manohar Lohia Hospital, Baba Kharak Singh Marg ND-1
	1000
	29.06.06
	CTO- 20.09.07.

CTE- Not applied.
	1. Authorization is valid up to 18-02-2010. CTO applied on 20.09.07. Not applied for CTE  under the Air & Water
2. Deficiencies observed w.r.t. consent application received e.g.:

· Noise monitoring report of all the DG sets not submitted & it is also not clear that all the DG sets are having acoustic enclosure & as well as adequate stack height. 
· Stack monitoring report of the boilers (2nos.) not submitted. 
· Affidavit submitted is not proper. 
· HCU requested for review of the decision taken for installation of ETP referring the prescribed standard under EPA.. 

3. Noise Monitoring Report for DG sets received from DPCC Laboratory. 

4. As decided in the meeting on 18.03.08 letter for deficiencies was issued including seeking application for Consent to Establish under Air & Water Acts. 

5. Letter received on 22.5.2008 enquiring whether installation of ETP is required or not.

6. As per the general decision taken on 06.05.08, letter issued for installation of:  
(a) Solar water heating system (b) Rain water harvesting system 

(c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

7. As per the decision taken in meeting on 13.06.08 a common letter to Jt. Secy (Health) with copy to D.G.(CPWD) from chairman, DPCC was issued.

8. Letter dated 15.11.08, received from HCU, referring their earlier letters dated 08.08.07 & 16.05.08 & sought clarification whether installation of ETP at this Hospital is required considering the provisions of BMW Rules & also the Effluent finally goes to Okhla STP.

9. Decision taken on 28.11 08: Regarding the exemption of ETP installation, an appropriate reply to be drafted and to be put up administratively. Ask for CTE and confirmation of Rain Water Harvesting System & Solar Water Heating System.
10. Inspection of the Hospital & monitoring of the incinerator was conducted on 19.12.08. VOC & Temperature for Primary & Secondary Chambers are not meeting the prescribed standards. As decided on 29.12.08, letter issued for the deficiencies observed.

11. As per the decision taken on 29.01.09, Reminder issued.

12. Reply dated 19.02.2009 & 09.03.09 received, regarding measures taken/ being taken.

13. As per the decision taken on 02.03.2009, Letter issued for installing the ETP within next 3 months and for submission of compliance w.r.t. the letters issued for deficiencies. 

14. As per the decision taken on 27.04.09, D.O. letter Issued on 14.05.09 from MS, DPCC to MS of the Hospital, seeking full compliance report & also fresh monitoring report for incinerator.
15. Reply dated 09.03.09 and 24.07.09 were received regarding measures taken/ being taken. Fresh monitoring report not received for incinerator.

	Issue Reminder Letter for full Compliance. 
	Reminder letter issued. No Reply.
	Show Cause Notice u/s 21 of the Air Act for CTE .Also seek compliance report on 5 points & other deficiencies.including monitoring report for incinerator.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	6.


	G.B.Pant Hospital, J.L. Nehru Marg, New Delhi-2 


	601
	30.06.06 
	CTE on 29.12.08.

CTO on 26.09.07.


	Applied for Authorization on 30.06.06. CTE applied on 29.12.08. CTO applied on 26.09.07.

1. Complaint was received regarding mismanagement of BMW.

2. Applied for consent under Air Act on 26.09.07, however stack monitoring report for boiler not submitted. Acoustic enclosure/acoustic treatment of the room not provided for the 9 DG Sets out of 12 DG Sets with the hospital. Adequate stack height not provided for all the DG Sets

3. As decided in the meeting on 18.03.08 letter for deficiencies was issued.

4. Letter has been received requesting to issue clearance certificate to operate the incinerator.

5.As per the general decision taken on 06.05.08, letter issued on 26.05.08  for installation of:   
(a) Solar water heating system  (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

6. Point wise reply dated 02-07-08  w.r.t letter dated 26-05-08 received.

7. Based on the complaint received against the kabariwalas operating near the Hospital, an inspection was carried out by PGRC officials and as decided, a Show Cause Notice was given to the hospital on 25.07.08. 

8. Reply received w.r.t SCN stating that BMW is being managed properly and there is no pilferage of the BMW or picking up by the rag pickers. 
10. An inspection of the hospital was conducted on 22.07.08 and it was observed: 

· Separate isolated storage site needs to be provided. 
· Acoustic enclosure/acoustic treatment of the room not provided for the 9 DG Sets out of 12 DG Sets with the hospital. Adequate stack height not provided for all the DG Sets. 
· The hospital has recently installed Microwave. 
· ETP found installed & was in operation (on trial run). 
· Storage site required to be provided for Sludge generated from the ETP & Collection tank for treated effluent should also be provided. 
· Use of treated effluent should be increased which is presently about 10 %.

11. A letter has been issued on 22.08.08 mentioning the deficiencies observed.

12. Letter dated 10.01.09 received regarding disposal of blood bags.

13. As per the decision taken on 02.03.2009, Letter for Adequacy Report of ETP, and for acoustic enclosure for D.G. Set(s), and for other deficiencies, issued.
	Issue Reminder Letter for full Compliance. 
	Reminder letter issued. No Reply.
	Well drafted letter mentioning the deficiencies requirements in the case.

	7.


	Northern Railway Central Hospital, Medical Director, Northern Railway Basant  Lane

 New  Delhi-55
	312
	25-Aug-06 
	19-Nov-07 (CTO)

CTE-not applied.
	 Applied for Authorization on 25.08.06. CTO applied on 19.11.07. Not applied for CTE  under the Air & Water

1. Application received for consent however Stack monitoring report for the Boiler & Noise Monitoring report for DG Sets not submitted. 

2. As decided in the meeting on 18.03.08 letter for deficiencies was issued including seeking application for Consent to Establish under Air & Water Acts.

3. As per the general decision taken on 06.05.08, letter issued on 26.05.08 for installation of:

(a) Solar water heating system

(b) Rain water harvesting system 

(c) Replacement of ordinary Bulbs with CFL 

(d)  ETP 

(e) Plantation of trees along side of the periphery of the Hospital building.

4. Reply dated 11-06-08 w.r.t letters dated 21-04-08and 26-05-08 regarding doing the needful as directed was received.

5. Asked to submit a list of authorized agencies by DPCC in order to process installation of ETP in hospital 

6. A reply of the notice dated 11.06.07 on 15.09.08 informing acoustic treatment of DG set room and issuing of NOC under Air Act received.

7. As decided on 28.11.08 Reminder letter for Solar Water Heating System, Rain Water Harvesting System & ETP and for CTE was issued. 

8. Reply received on 19.02.09 w.r.t letter dated 22.01.09.

9. As per the decision taken on 29.12.08, final reminder for Consent to Establish was issued.

10. As per decision taken on 02.03.2009, Unit was called for personal hearing on 27.04.2009 at 3:30 PM and Letter received from the unit was replied with respect to compliance report on 5 points communicated to the hospital earlier


	Call on in the next meeting. 
	--------------------
	Show Cause Notice us 21 of the Air Act for CTE. Also ask to apply afresh for authorization. 

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	8.
	Guru Nanak Eye Centre, Maharaja Ranjit Singh Marg , New Delhi
	184


	11-Sep-06
	CTE 09.03.09.

CTO  30.11.06
	1. Authorization is valid up to 18-02-2010. CTO applied on 09.03.09. CTE applied on 30.11.06.
2. Noise report shown that Insertion Loss was not as per norms.

3. As decided in the meeting on 18.03.08 letter for deficiencies was issued including seeking application for Consent to Establish under Air & Water Acts.

4. Copy of communication with PWD regarding Noise monitoring report has been submitted.

5.As per the general decision taken on 06.05.08, letter issued on 26.05.08 for installation of: 

(a) Solar water heating system     (b) Rain water harvesting system          (c) Replacement of ordinary Bulbs with CFL          (d)  ETP 

(e) Plantation of trees along side of the periphery of the Hospital building. Reply  received

6. Based on the complaint received against the kabariwalas operating near the Hospital an inspection was conducted by the PGRC officials & as decided, a Show Cause Notice was given to the hospital on 25.07.08. 

7. Reply received w.r.t said SCN stating that BMW is being managed properly and there is no pilferage of the BMW or picking up by the rag pickers.
8. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy(Health) with copy to Pr.Secy(PWD) was issued.

9. As decided on 28.11.08 Reminder letter for CTE, ETP and Rain Water Harvesting System and confirmation of installation of Solar Water Heating System was issued.

10. As per decision taken on 02.03.2009, Unit was called for personal hearing on 27.04.2009 at 3:40 PM.

11. As per the decision taken on 27.04.09, the unit came for personal hearing on 27.04.09. The unit is advised to set up ETP, CFL, Rain Water Heating System & Solar Water Heating System within a period of two months. Letter issued. ETP installed.

	Call on in the next meeting.
	Reply received on 08.06.09 stating that matter has been taken with PWD.
	Include the name of the hospital in the common D.O.Letter to be issued to Pr. Secy ( Health ) &  Pr.Secy ( PWD), GNCT Delhi for the compliance on the 5 Points  Also ask for Environmental Clearance for the upcoming building / project. 

	9.


	E.S.I. Hospital , Basai Darapur,Ring Road , New Delhi-15
	600


	30-Nov-06
	CTE 17.09.08.

CTO 24.12.07.
	1 Authorization valid upto 18.02.10. CTO applied on 24.12.07. CTE applied on 17.09.08..

2..As per the general decision taken on 06.05.08, letter issued on 26.05.08  for installation of:

(a) Solar water heating system              (b) Rain water harvesting system            (c) Replacement of ordinary Bulbs with CFL         (d)  ETP 

(e) Plantation of trees along side of the periphery of the Hospital building.

3. As decided on 30.10.08, letter was issued asking the Hospital to install ETP within 3months.
4. As per the decision taken on 02.03.2009, Letter received from the Hospital was replied and compliance w.r.t. 5 points, was sought from the hospital. DHS letter dated 24.02.09, was forwarded to the hospital regarding rate for BMW disposal through operator.

5. As decided, final reminder issued for full compliance. 

	Dr. Chetna to speak. 
	Dr. Chetna Spoken. No Reply.
	CTE granted. Reminder letter for compliance of the remaining points.

	10.


	All India Institute of Medical Sciences, Ansari Nagar, New Delhi-29
	1596
	28-Dec-07 
	12.09.08 (CTO) and 
12.09.08 (CTE)
	 Applied for Authorization on 28.12.07. CTO applied on 12.09.08. CTE applied on 12.09.08..

1. SCN for refusal of authorization was issued on 21-2-2007.
2. Reply to SCN u/s 5 of EPA received with the remarks that necessary instruction for strict compliance of the statutory provisions have been issued to concerned officer.
3. HCU was inspected on 8-8-2007 during which various deficiencies were observed regarding BMW management

4. As per the general decision taken on 06.05.08, letter issued on 26.05.08 for installation of   (a) Solar water heating system

(b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d) ETP (e) Plantation of trees along side of the periphery of the Hospital building. 

5. As decided on 30.10.08, letter was issued to install ETP within three months. Letter dated 05.01.09 received from the Hospital.
6. Hospital was inspected and incinerator was monitored on 20.12.08 and following deficiencies were observed.
· Particulate Matter, VOC, and Temperature for the Primary & Secondary Chambers not found within the prescribed standards. 
· Deficiencies observed w.r.t. management of Bio-Medical Waste. 

7. As decided by the Committee, letter issued for the deficiencies observed. 

8. As per the decision taken on 29.12.08, DO letter from Chairman, DPCC to Director, AIIMS with a copy to Secretary (Health),Govt. of India and PS to Minister (Health),Govt. of India outlining all the deficiencies observed during the inspection and requiring immediate correction issued. 

9. Letters from Health Deptt.eaHHHhhjfjfjhhhfgjh was received on 09.03.2009 and 25.03.2009.

10. w.r.t to the letter issued after the decision on 02.03.09, reply received from the hospital.

11. As per the decision taken on 02.03.2009, Hospital had filed a reply received. Hospital was asked to correct the deficiencies and send the compliance report.

12. D.O. letters Issued on 14.01.09 & 14.05.09 to MS of the Hospital, seeking full compliance report & also fresh monitoring report for incinerator.
13. Reply dated 19.02.2009, 20.04.09 & 25.04.2009, 25.05.09, 28.05.09 & 04.06.09 received, regarding   measures taken/ being taken.  Monitoring report for incinerator for monitoring conducted by Guru Gobind Singh Indraprastha University on 07.02.09, shows Temp. (893 0 C) in primary chamber is not within the prescribed standards. Report not submitted for parameter VOC in ash. 


	Call Medical Superintendent of the Hospital for personal hearing in the next meeting. No consultant to be deputed for hearing. 
	Letter for personal hearing issued. No Reply.


	M.S of the hospital attended personal hearing on 04.09.09. The unit  will submit the compliance report  alongwith   status w.r.t 5 points & other deficiencies communicated to the hospital within 15 days.  



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	11.
	Safderjung Hospital, Aurobindo Marg New Delhi-29
	1531
	05-Mar-07
	CTR
12-09-08 

CTE 08.08.08
	1. Authorization is valid up to 30-01-2010. CTO applied on 12.09.08. CTE valid upto 17.09.09. 
2.SCN u/s 21/22 of Air Act to submit noise monitoring report of DG sets was issued on 21-06-2007 

3. As decided in the meeting on 18.03.08 letter for deficiencies was issued  including seeking application for Consent to Establish under Air & Water Acts

4.As per the general decision taken on 06.05.08, letter issued ON 26.05.08  for installation of:  (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL  (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE (BMW) had talked to the official (s) of the hospital.
5.  As decided on 27.08.08, letter was issued and unit was asked to file CGWA clearance within 01 month.  Letter was issued on 22.10.08 for ETP and other decisions of BMW Committee. 
6. As decided on 30.10.08, reminder letter was issued.

6. As decided in meeting held on 28.11.08, three months time granted for ETP and to submit compliance of Solar Water Heating System, Rain Water Harvesting within one month.

7. Letter dated 31.12.08 received regarding converter demo plant for the treatment of BMW. 

8. Inspection of the Hospital & monitoring of the incinerator was conducted on 07.01.09. VOC & Temperature range for Primary Chamber are not meeting the prescribed standards.

9. As per the decision taken on 29.01.09, D.O. Letter issued from MS, DPCC to MS of Hospital with copy to Secy (Health) Govt. of India, for rectification of the deficiencies observed during the inspection and monitoring, to submit fresh monitoring report for incinerator, to file compliance report on the five points mentioned in our earlier letters.
10. D.O. letter Issued on 14.05.09 to MS of the Hospital, seeking full compliance report & also fresh monitoring report for incinerator.

11. Reply dated 23.03.09, 17.06.09 and 20.07.09 received and informed that ETP matter has been taken up with the Health Ministry and for monitoring report fee has been paid to the laboratory.
	Call for personal hearing in next meeting. 
	Letter for personal hearing issued. Reply received on 20.07.09 regarding setting up of ETP and payment of fee for fresh monitoring report for incinerator to impaneled lab of DPCC.
	Addl. M.S of the hospital attended personal hearing on 04.09.09. The unit will  submit compliance report alongwith   status w.r.t 5 points & other deficiencies communicated to the hospital within 15 days.  



	12.
	Aruna Asaf Ali Hospital, 5 Rajpur Road, Delhi
	100
	11-Aug-04
	CTO 18.09.07

CTE 26.11.08
	1. Authorization is valid up to 30-01-2010. CTE applied on 26.11.08. CTO applied on 18.09.07.
2. Acoustic enclosure with the DG set provided, however noise monitoring report not submitted. 

3. As decided in the meeting held on 18.03.08 letter for deficiencies and Consent to Establish was issued.
6. As per the general decision taken on 06.05.08, letter issued on 26.05.08  for installation of:

(a) Solar water heating system            (b) Rain water harvesting system               (c) Replacement of ordinary Bulbs with CFL        (d)  ETP                                              (e) Plantation of trees along side   of the periphery of the Hospital building.

7. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy (Health) with copy to Pr.Secy (PWD) from chairman, DPCC was issued.

8. As decided in meeting held on 28.11.08, time granted of three months for ETP installation and one month for confirmation of installation of Solar Water Heating System.

9. Reply dated 13.01.09 received informing that matter regarding installation of ETP is under process.

10. A news item was published in the Times of India on 06.04.09 regarding the inspection of this Hospital including other four hospitals of Delhi Government by the Health Minister of Govt. of NCT of Delhi and her observations regarding improper management of BMW particularly Sharp Waste Management.

11. Inspection of the hospital was carried out on 16.04.08 & deficiencies w.r.t BMW management was observed.

12. As per the decision taken on 02.03.2009, Letter for compliance w.r.t. 5 points, communicated to the hospital earlier issued.

13.D. O. Letter issued to MS of the Hospitals for rectification of the deficiencies observed during the inspection by the team of Dr. T.K. Joshi by 25.05.2009, with copy to Pr. Secy. (Health), Govt. of Delhi and PS to Minister for Health, Govt. of  Delhi. 


	Ask the unit to submit interim report along with compliance on rectification of deficiencies, already communicated.
	Letter issued. Replies received on 01.07.09, 17.06.09 regarding measures taken/ being taken with copy of Noise Monitoring report for DG Set(s).
	Include the name of the hospital in the common D.O.Letter to be issued to Pr. Secy ( Health ) &  Pr.Secy ( PWD), GNCT Delhi for the compliance on the 5 Points  

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	13.


	Sanjay Gandhi Memorial Hospital, Mangolpuri ,Delhi


	100
	22.5.09
	19.03.09 (CTO)

CTE- not applied
	Applied for Authorization on 22.05.09. CTE not applied. CTO applied on 19.03.09.
1. SCN under BMW Rule was issued on 21-2-2007

2. Reply to SCN u/s 5 of EPA received with the remark that corrective measures have been taken.

3. As decided in the meeting on 18.03.08 letter for deficiencies was issued  including seeking application for Consent to Establish under Air & Water Acts

4. As per the general decision taken on 06.05.08, letter issued on 26.05.08 for installation of:

(a) Solar water heating system    (b) Rain water harvesting system     (c) Replacement of ordinary Bulbs with CFL   (d)  ETP    

(e) Plantation of trees along side of the periphery of the Hospital building.

6. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy (Health) with copy to Pr.Secy (PWD) from chairman, DPCC was issued.

7. As per the decision taken on 27.08.08, reminder letter has been sent administratively to new Pr. Secy (Health) for getting the Consent to Establish.
8. As per the decision taken on 28.11.08, letter issued for CTE within one month, installation of ETP within three months and submits an affidavit regarding change in bed number and also applies afresh for renewal of authorization.

9. As per the decision taken on 29.12.08 and 29.01.09, final reminder for Consent to Establish was issued.

10. As per the decision taken on 02.03.2009, unit was called for personal hearing on 27.04.2009.

11. The unit came for personal hearing. He says, he will apply for Consent to Establish within one week. It has already installed solar water heating system and STP for which adequacy report will be submitted. Rain water harvesting system, CFL and plantation will be done within one month. The unit must also file fresh authorization application under BMW Rules, letter issued.


	Issue reminder for CTE and ask for interim report on Compliance of other points.
	Reminder letter issued. Compliance report received on 20.07.09 regarding 5 points stating matter with PWD.


	Reminder letter.

	14.
	Vallabhai Patel  Chest Institute, University of Delhi, PO-Box.No-2101, Delhi-7
	60
	14-Dec-04
	CTO 10.09.07 

CTE 18.07.08
	1. Authorization is valid up to 30-01-2010. CTE Granted. CTO valid upto 09.09.10.
2. As decided on 28.11.08 Reminder letter for compliance of five items as decided earlier was issued.

3. Reply dated 28.01.09 received giving point wise compliance and it was informed that installation of solar water heating system will be done after renovation, Rain water harvesting is not possible as water table is high, Ordinary bulbs have been replaced with CFL, For ETP installation a detailed Project report has been prepared, Mercury based thermometers & B.P. Instruments are not used.  

4. As per the decision taken on 29.12.08, unit called for personal hearing on 29.01.2009.

5. Letter received on 19.03.09, regarding measures taken/ being taken on 5 points communicated earlier and Energy Audit.

6. As per decision taken on 02.03.2009, A letter was sent to clarify about the position of ETP. CGWA should be approached regarding rain water harvesting system and installation of Solar Water Heating System.

7. As decided on 27.04.09, final reminder issued for full compliance.
	Call for personal hearing in next meeting. 
	Letter for personal hearing issued. Reply received on 01.06.09 regarding compliance report of 5 points.
	Unit attended personal hearing on 04.09.09. It was informed that ETP &  SWHS will be installed by September 2009. The unit will  submit compliance report in this regard  alongwith   adequacy report for ETP by October 2009.. 



	15.
	Dr. B.R. Sur Hemopathic College & Hospital, Nanakpura, Moti Bagh, New Delhi-22


	50
	22-Feb-05
	CTO 24.10.07 

CTE 04.08.08

	1. Authorization is valid up to 30-10-2010. CTO valid upto 23.10.10. CTE Granted.
2. As decided in meeting held on 27.08.08, CTE & CTO were issued.
3. As decided on 28.11.08, reminder for compliance of five items as decided earlier, was issued.

4. As per the decision taken on 29.12.08, unit called for personal hearing on 29.01.2009.    

5. As per the decision taken on 29.01.09, The representative of the unit came for personal hearing. The unit will file reply on all the five points by 02.03.2009.

6. Reply received on 03.03.09, regarding measures taken/ being taken on 5 points.


	Ask the unit to file status of compliance for CFL, Rain Water Harvesting System, and Solar Water Heating System along with waste water analysis report. 
	Letter issued. Compliance report received on 14.07.09 stating matter with PWD.
	Reminder letter

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	16.


	Rajan Babu Institute for Pulmonary Medicine & Tuberculosis (RBTB Hospital),  GTB Nagar, Kingsway Camp,Delhi-9 
	1155
	02.Aug-05
	CTO- 

13.11.07    

CTE not applied
	1. Applied for Authorization on 02.08.05. CTO applied on 13.11.07. Not applied for CTE. 
2. SCN under Rules 7 of BMW Rules was issued on 21-2-2007(C/142) and 11-6-2007(C/142). Reply received informed regarding corrective measure taken w.r.t BMW management. 

3. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 & 01.10.07 to Addl. Commissioner, MCD. / Commissioner MCD.

4. Letters/Several representations received requesting permission to operate the Incinerator for trial testing since Hospital has installed APCD after issuance of Directions u/s 5 of EP Act (issued on 17.04.06 (c/112). 

5. Application received for consent to operate however, noise monitoring report for DG Sets not submitted.

6. As decided in the meeting on 18.03.08 letter for deficiencies was issued including seeking application for Consent to Establish under Air & Water Acts7. As per the general decision taken on 06.05.08, letter issued  on 26.05 .08 for installation of:

(a) Solar water heating system (b) Rain water harvesting system(c) Replacement of ordinary Bulbs with CFL(d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

7. An inspection of the Hospital was conducted on 24.07.08 & deficiencies were observed. 
· Hospital is having 2 No 320 KVA DG Sets without Acoustic Enclosure / acoustic treatment of the room.

8. As decided on 27.08.08 notice was issued to HCU to apply for CTE and correct all the deficiencies noted during the inspection. 

9. As per the minutes of the meeting held on 03.11.08, received from  HCU site for ETP is being decided &  possibilities in constructing a common ETP for both this Hospital & MVID Hospital  is to be explored since both the hospitals lies adjacent to each other and both requires ETP.

10. Reply received dated 15.12.08 informed regarding rectification measures taken w.r.t. earlier letters issued. Requested for permission to operate the incinerator. 

11. As per the decision taken on 29.12.08, Unit was allowed to operate the incinerator for 30 days during which monitoring was done.

12. Inspection of the hospital & monitoring of the incinerator was conducted on 06.02.09. Deficiencies observed. 

· VOC & Temperature range for Primary & Secondary Chambers are not meeting the prescribed standards. 

· Having 2 Incinerator, out of which one is standby.  

· This hospital generates 2 to 5 kg/day of incinerable waste however incinerator capacity 125 kg/Hour is quite large considering the waste generation from this hospital. 

· Earlier APCD was not installed and this Hospital of MCD was directed not to operate the incinerator. Thereafter APCD has been installed. 
· Hospital has been permitted to operate incinerator for 30 days vide letter dated 22.01.2009. Earlier the hospital was sending its incinerable waste to the incinerator of MVID Hospital (MCD). 

· Proper Temperature recording system not found should be provided.  Properly Trained /Qualified personnel for operation & Maintenance of Incinerator are required which is lacking. For 2 DG Set(s), acoustic enclosure not provided. 

· ETP is yet to be provided. Platform with the stack for monitoring needs improvement. Autoclavable waste is sent to Hindu Rao Hospital for its treatment and disposal. As per the report of Dr. Joshi’s team, the Hospital / MCD may be asked to close down/ not to operate the Incinerators at this Hospital and Incinerable waste from the Hospital may be Incinerated at the Incinerators of MCD at Hindu Rao Hospital/ Swami Dayanand Hospital or may be incinerated at the Incinerators of two Common Bio Medical Waste Treatment Facilities (CBWTF).

13. As per the decision taken on 02.03.2009, D.O. Letter from MS, DPCC to MS of Hospital for rectification of the deficiencies observed during the inspection and monitoring. Unit to submit fresh monitoring report for incinerator. Unit to file compliance report, with dates, on the five points mentioned in our earlier letters, issued. D.O. Letter was also issued from Chairman, DPCC to Commissioner, MCD. Also, M S, DPCC was talked to M S of the Hospital to outsource the small quantity of the incinerable BMW instead of burning the waste at the incinerator of this hospital.

14. D.O. letter Issued on 14.05.09 to MS of the Hospital, seeking full compliance report. The Hospital has been advised to close down Incinerator as quantity of Bio Medical Waste generated from the Hospital is quite less (2-5 Kg /day) and a D.O. Letter has also been issued to DHA, MCD in this regard.

15. Reply dated 19.05.09,  received regarding measures taken/ being taken for rectification of deficiencies. It is also informed that incinerator is not in operation. Another reply dated 06.07.09 received.


	Issue Reminder Letter for full Compliance. 
	Reminder letter issued. Reply received dated 06.07.09 regarding measures taken/ being taken for rectification of deficiencies observed during the inspection.


	Ask for CTE .Letter for expediting the compliance of other things.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	17.
	E.S.I Hospital, Jhilmil, Delhi-110095


	250
	03.07.07
	CTO 14-Mar-08

CTE- not applied
	1. Authorization is valid up to 7-3-2010. CTO applied on 14.03.08. CTE- not applied.
2. Applied for consent under the Air Act on 14.03.08 along with Noise Monitoring report of both DG sets of 312.5 and 180 KVA.  As per the report the insertion loss meeting the prescribed norms. Stack monitoring report of the boiler not submitted.

3. As decided in the meeting on 18.03.08 letter for deficiencies was issued  including seeking application for Consent to Establish under Air & Water Acts

4. Letter dated 10-06-08 requesting for no objection certificate for installation of x- ray unit at hospital received.

5.As per the general decision taken on 06.05.08, letter issued  on 26.05 for installation of:

(a) Solar water heating system, (b) Rain water harvesting system 

(c) Replacement of ordinary Bulbs with CFL, (d) ETP, and 

(e) Plantation of trees along side of the periphery of the Hospital building. 

6. Letter dated 04.06.08 & 10.06.08 has been received wherein HCU has requested for issuance of NOC of X-Ray Unit.

6. As per the decision taken on 29.12.08, hospital was called for personal hearing.

7. As per the decision taken on 29.01.09, The representative of the unit came for personal hearing. It will file reply on all the five points by 02.03.2009.

8. Letter received on 27.02.09, regarding measures taken/ being taken on 5 points.

9. As per the decision taken on 02.03.2009, reminder letter with copy to medical commissioner, ESI, issued.

10. As decided, letter issued for full compliance.
	Interim report is submitted w.r.t. letter dated 05.05.09.
	Letter issued.

No Reply.
	Reminder for  CTE  & other remaining  things. 

	18.
	G.L. Maternity Hospital (MCD) , Ajmeri gate, Kamla Market, Delhi-6


	97
	24-Apr-07
	CTE & CTO - 17.06.08.
	 Authorization is valid up to 30-5-2010. CTE Granted. CTO applied on 17.06.08.
1. Inspected on 21.08.08 & deficiencies observed: 

· compliance of BMW Rules (storage containers were not containing proper color plastic bags & were without labeling of Bio- hazard symbol. Isolated storage facility not provided for BMW. 

· Incinerable BMW is sent to the incinerator of MVID Hospital which is also of MCD.

· For other plastic infected BMW (Autoclavable waste) proper waste treatment /disposal facility not found. 

· Stack height with the DG Set found inadequate. DG Set is having acoustic enclosure.

2. As decided on 27.08.08, CTE granted. However, notice was issued for correction the deficiencies noted during the inspection. 

5. W.r.t Notice dated 22.10.08, vide letter dated 07.11.08, informed regarding corrective measures taken and also asked a month ‘s time for all the required task like SWHS, RWHS, CFL,Plantation Etc.

6. As decided on 28.11.08 Reminder for compliance was issued.

7.Reply dated 14.01.09 received w.r.t letter dated 22.12.08, informing the action taken by the hospital w.r.t the deficiencies observed earlier & directions given by DPCC

8.  As decided on 29.12.08, Final reminder for compliance issued.

9. Letter received on 27.02.09, regarding measures taken/ being taken on 5 points

10. As per the decision taken on 29.01.09, final reminder issued.

11. Reply received on 25.05.09, regarding compliance report on 5 points.

12. As per decision taken on 02.03.2009, letter for full compliance issued.

13. Letter issued for full compliance. Reply received, asked for exemption for ETP.

	Ask the unit to confirm the status about the ETP. 
	Letter issued. Letter received on 10.07.09 stating exemption for ETP.


	Inspection for beds . 

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	19.
	M.V.I.D Hospital (MCD),  Kingsway Camp, Delhi-9


	227
	09.06.08


	CTO 20.04.07 

CTE 26.06.08 
	Authorization applied on 09.06.08. CTO applied on 20.04.07. CTE Granted.
1. As decided in the meeting on 18.03.08 letter for deficiencies was issued including seeking application for CTE under Air & Water Acts.
2. Reply dated 01-07-08 w.r.t letter dated 25-04-08.regareding submission of test report of waste water generated from hospital was received.

3. As per the general decision taken on 06.05.08, letter issued on 26.05.08  for installation of: (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP  (e) Plantation of trees along side of the periphery of the Hospital building. 

4. Reply received w.r.t letter dated 26.05.08. 

5. Inspection was conducted on 24.07.08 & deficiencies were observed w.r.t the Incinerator & APCD Installed. 

6. Pointwise reply dated 15.10.08, regarding correction of deficiencies observed during inspection on 24.07.08.

7. As decided on 27.08.08 CTE was issued and notice was also issued for correction the deficiencies noted during the inspection. 

8. W.r.t letter dated 22.10.08, vide letter dated  06.11.08, HCU has installed SWHS (one unit at Laboratory)& rest is under progress. For rest of the issues the matter has been taken up with the concerned Deptt. New Elec. Installation is of CFL.Hospital is having thick foliage cover of greenery all around. New trees are being planted.

9. Inspection of the hospital & monitoring of the incinerator was conducted on 06.02.09. Deficiencies observed:

· VOC & Temperature range for Primary Chamber are not meeting the prescribed standards.

· Deficiencies observed w.r.t BMW Management. \

· Proper Temperature recording system required should be provided.  

· Properly Trained /Qualified personnel for operation & Maintenance of Incinerator are required which is lacking. 

· ETP is yet to be installed. 

· For pH control of water in scrubber measures/ mechanism not provided. 

· Bio-Hazard symbol not provided at the Incinerator & Storage site.

· Plat form, railing & ladder needs improvement for monitoring purpose. 

· Record keeping for BMW needs improvement. 

· As per the report of Dr. Joshi’s team, the Hospital / MCD may be asked to close down/ not to operate the Incinerators at  MVID Hospital and Incinerable waste from the Hospitals and from Kasturba Hospital and G.L.Maternity Hospital may be Incinerated at the Incinerators of MCD at Hindu Rao Hospital/ Swami Dayanand Hospital or may be incinerated at the Incinerators of two Common Bio Medical Waste Treatment Facilities (CBWTF).

10. As per the decision taken on 02.03.2009, D.O. Letter from MS, DPCC to MS of Hospital for rectification of the deficiencies observed during the inspection and monitoring. Unit to file compliance report, with dates, on the five points mentioned in our earlier letters, issued. D.O. Letter was also issued from Chairman, DPCC to Commissioner, MCD. Also, M S, DPCC was talked to M S of the Hospital to outsource the small quantity of the incinerable BMW instead of burning the waste at the incinerator of this hospital.

11. D.O. letter Issued on 14.05.09 from MS DPCC to MS of the Hospital, seeking full compliance report. The Hospital has been advised to close down Incinerator as quantity of Bio Medical Waste generated from the Hospital is quite less (1-2 Kg /day) and a D.O.Letter has also been issued to DHA, MCD in this regard.

12. Reply dated 13.04.09, 05.05.09, 18.05.09 and 27.05.09 received regarding measures taken for rectification of deficiencies. Monitoring report for incinerator for monitoring conducted by Guru Gobind Singh Indraprastha University on 28.03.09 shows parameters within the prescribed limit received.

13. As decided on 01.06.09, letter issued on 26.06.09 for full compliance.


	Issue Reminder Letter for full Compliance. 
	Reminder letter issued. No Reply.


	Letter seeking status w.r.t. 5 points & other things.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	20.


	Lal Bahadur Shastri Hospital, Khichripur
	100


	8-Aug-06
	CTE 20.01.09

CTO  28.12.07 


	1. Authorization is valid up to 30-5-2010.  CTO applied on 28.12.09 (pending). CTE applied on 20.01.09 (pending).
2. HCU submitted a letter on 18-7-2007 wherein they have requested to know about the justification of balance fee in respect to authorization issued on 20-6-2007

3. As decided in the meeting on 18.03.08 letter for deficiencies was issued  on 25.04.08  including seeking application for Consent to Establish under Air & Water Acts

4.As per the general decision taken on 06.05.08, letter issued on 26.05.08  for installation of:

(a) Solar water heating system        (b) Rain water harvesting system             (c) Replacement of ordinary Bulbs with CFL            (d)  ETP 

(e) Plantation of trees along side of the periphery of the Hospital building.

5. Replies received vide letter dated 07.08.08 and NMR for DG Sets, Stack Monitoring report for incinerator ( VOC parameter not monitored) &  Waste Water monitoring report submitted ( Bio-assay parameter not meeting the standards).
6. As decided on 27.08.08, Reminder letter is sent administratively to new Pr. Secy (Health) for getting the Consent to Establish. Letter was issued. 

7. Letter dated 22.10.08, received referring earlier letter dated dated 07.08.08 but CTE Not submitted. 

8. Inspection of the hospital & monitoring of the incinerator was conducted on 05.02.09. Deficiencies observed. 

· Particulate Matter, VOC & Temperature range for Primary Chamber are not meeting the prescribed standards. 

· Deficiencies observed w.r.t BMW Management. 

· Proper Temperature recording system required should be provided.  

· Properly Trained /Qualified personnel for operation & Maintenance of Incinerator are required which is lacking.

· ETP is yet to be provided. Storage site for BMW needs improvement and bio hazard symbol not found on the containers. 

· Records of BMW maintained however needs further improvement for proper record keeping. .

9. As decided on 29.12.08, letter for Consent to Establish for the proposed new building and to submit interim report by 29.01.2009 issued.

10. As per the decision taken on 29.01.09, reminder issued.

11. Reply dated 09.04.09, 25.04.09 and 21.05.09 received regarding measures taken/ being taken/ matter referred to concerned Deptt./ PWD for necessary action.

12. D.O. Letter issued on 23.03.09 and 14.05.09 to MS of Hospital with copy to Pr. Secy. (Health) GNCT Delhi, for rectification of the deficiencies observed during the inspection and monitoring. Unit was also asked to submit fresh monitoring report for incinerator. Unit to file compliance report, on the five points mentioned in our earlier letters.
13. Reply dated 27.06.09 received and informed that approached to empanelled laboratory for monitoring. Another letter received on 13.07.09 and 05.08.09.

	Ask the unit to file full compliance. 
	Letter issued. Replies received on 13.07.09 and 05.08.09 regarding submitted fee for fresh monitoring report for incinerator to impaneled lab of DPCC.


	CTE granted. Include the name of the hospital in the common D.O.Letter to be issued to Pr. Secy ( Health ) &  Pr.Secy ( PWD), GNCT Delhi for the compliance on the 5 Points . Issue letter to the hospital seeking  compliance report including monitoring report w.r.t the earlier letters issued. 

	21.
	A&UTibbia College Hospital, Karol Bagh, New Delhi-5
	150
	22-Sep-06
	CTE 18.11.08.

 CTO 28.09.06 


	1. Authorization is valid up to 30-5-2010.  CTO applied on 28.09.06. CTE applied on 18.11.08.
2. HCU was inspected on 23-8-2007 and the BMW management found as per rule.

3. The stack height with the DG set is yet to be increased.

4. Meeting taken by Pr. Secy. (Health) on 25.09.07, HCU was directed ( in the meeting) to comply with norms/standards prescribed for DG Sets and submit compliance report along with the Noise Monitoring report to DPCC. However noise monitoring report not received.

5..As per the general decision taken on 06.05.08, letter issued for installation of:

(a) Solar water heating system 

(b) Rain water harvesting system 

(c) Replacement of ordinary Bulbs with CFL 

(d)  ETP 

(e) Plantation of trees along side of the periphery of the Hospital building. 

6. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy. (Health) with copy to Pr. Secy. (PWD) from chairman, DPCC was issued.

7. Inspection of the unit was conducted as decided on 28.11.08.

8. As decided on 29.12.08, letter for correction of deficiencies issued.

9. As decided on 02.03.2009, A D.O. letter from Chairman, DPCC to Pr. Secretary Health and Pr. Secretary, PWD, issued.


	Call for personal hearing in next meeting. 
	Letter for personal hearing issued.


	Unit attended personal hearing on 04.09.09. The unit will  submit compliance report alongwith   status w.r.t 5 points & other deficiencies communicated to the hospital within 15 days. 
Also include the name of the hospital in the common D.O.Letter to be issued to Pr. Secy ( Health ) &  Pr.Secy ( PWD), GNCT Delhi for the compliance on the 5 points.



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	22.
	Dr. Baba Saheb Ambedkar Hospital Sector-6, Rohini
, New Delhi-85 


	500
	 02.08.07


	CTO 13.08.07.

CTE- 07.01.09

	 Applied for Authorization on 02.08.07.  CTO applied on 13.08.07. CTE applied on 07.01.09.
1. SCN under EPA was issued on 23-3-2007 & 11-6-2007.

2. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Pr Secy  (Health).

3. Meeting taken by Pr. Secy. (Health) on 25.09.07, HCU was directed (in the meeting) to inform DPCC about the rectification measures. 

4. As decided in the meeting on 18.03.08 letter for deficiencies was issued  on 21.04.08  including seeking application for Consent to Establish under Air & Water Acts

5. Reply dated 02.06.08 w.r.t. letter dated 21.4.2008 received regarding  rectification of deficiencies observed  during inspection  

6. As per the general decision taken on 06.05.08, letter issued  on 26.05.08 for installation of:

(a) Solar water heating system              (b) Rain water harvesting system                 (c) Replacement of ordinary Bulbs with CFL           (d) ETP 

(e) Plantation of trees along side of the periphery of the Hospital building.

7 Inspection of the hospital was conducted on 20.08.08 & deficiencies were observed . 

· Near the BMW Storage solid waste found spilled on ground & the condition was pathetic. 

· Proper segregation of BMW not observed. 

· Bio – hazard Symbol not provided over the Containers & on the storage site. 

· Proper records keeping for BMW not observed.8. 

8. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy(Health) with copy to Pr.Secy(PWD)  was issued. 

9. As decided on 27.08.08 notice was issued for corrections of deficiencies noted by inspection team and also the HCU was asked to apply for CTE. 

10. A news item was published in the Times of India on 06.04.09 regarding the inspection of this Hospital including other four hospitals of Delhi Government by the Health Minister of Govt. of NCT of Delhi and her observations regarding improper management of BMW particularly Sharp Waste Management.

11. Inspection of the hospital was carried out on 18.04.08 & deficiencies w.r.t BMW management were observed.

12. As per the decision taken on 29.01.09, reminder issued.

13. As per the decision taken on 02.03.2009, unit was called for personal hearing on 27.04.2009 and following decisions were taken.
14. The unit came for personal hearing today. The solar water heating system is getting installed. Rain water harvesting system, ETP and Solar Water Heating System be installed within 2--3 months. CFLs will be changed within one month. Issue D. O. Letter to MS of the Hospitals for rectification of the deficiencies observed during the inspection by the team of Dr. T.K. Joshi by 25.05.2009, with copy to Pr. Secy. (Health), Govt. of Delhi and PS to Minister for Health,  Govt. Delhi, issued.
	Call on in next meeting. 
	--------------------
	 Include the name of the hospital in the common D.O.Letter to be issued to Pr. Secy ( Health ) &  Pr.Secy ( PWD), GNCT Delhi for the compliance on the 5 Points. Reminder letter seeking compliance from the hospital w.r.t. deficiencies & 5 points.   

	23.
	Lala Ram Swaroop Institute of Tuberculosis and Respiratory Diseases,  Sri Aurobindo Marg New Delhi-30
	515
	17-Jul-06
	CTO 06-Aug-07
CTE 27.10.08
	1. Authorization is valid up to 7-3-2010, (with condition that HCU shall close down the incinerator). CTO applied on 06.08.07. CTE applied on 27.10.08.
2. HCU has also requested to operate the incinerator as APCD has been installed.

3. Letter was issued for the trial run of the incinerator seeking stack monitoring report within 30 days and the hospital to install the ETP.

4. The hospital has submitted stack analysis report but the parameter of Volatile Organic Compound was not analyzed for the ash generated from the incinerator. No information regarding ETP was submitted. No waste water analysis report was submitted.

5. Reply received w.r.t. letter dated 02.05.2008. Analysis report of incinerator ash submitted however not within the limit.

6. As per the general decision taken on 06.05.08, letter issued for installation of:

(a) Solar water heating system  (b) Rain water harvesting system  (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

7. Inspection of the hospital  & monitoring of the incinerator  was conducted on 09.02.09. Deficiencies observed. 

· VOC & Temperature range for Primary Chamber are not meeting the prescribed standards.

· Deficiencies observed w.r.t BMW Management. Sharp boxes are yet to be provided for sharp waste. 

· Proper Temperature recording system not found should be provided.  

· Properly Trained /Qualified personnel for operation & Maintenance of Incinerator are required.  

· ETP is yet to be provided.

8. Reply received on 05.02.09 w.r.t. letter dated 22.01.09 regarding measures taken/ being taken and letter received on 16.02.09 enclosing preliminary report on ETP.

9. As decided on 29.12.08, final reminder for compliance issued,

10. As per the decision taken on, D.O. Letters issued on 23.03.09, 14.05.09 and 13.07.09 to MS of Hospital with copy to Secretary Health GOI, for rectification of the deficiencies observed during the inspection and monitoring. Unit was asked to submit fresh monitoring report for incinerator. Also Unit to file compliance report, on the five points mentioned in our earlier letters.
11. Reply dated 15.04.09, 26.05.09 & 23.07.09 received regarding measures taken/ being taken for rectification of deficiencies. Monitoring report for incinerator conducted by GGSIPU on 22.04.09. Temperature of Primary Chamber (865 C) is not meeting with the prescribed standards.
	Suitable reply be sent by the BMWM Cell. 
	Letter issued. Reply received on 23.07.09 regarding measures taken/ being taken and submitted fresh monitoring report for incinerator.


	Issue letter seeking status of compliance w.r.t the deficiencies communicated & also for 5 points. 

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	24.
	Kasturba Hospital, Near Jama Masjid, New Delhi-2
	450
	26.08.09
	CTO- 17.01.05 
CTE 
24.11.08.


	 Authorization applied on 26.08.09.  CTO applied on 17.01.05. CTE applied on 24.11.08.
1. As decided in the meeting on 18.03.08 letter for deficiencies was issued  on 21.04.08 including seeking application for Consent to Establish under Air & Water Acts 

2. As per the general decision taken on 06.05.08, letter issued for installation of:

(a) Solar water heating system  (b) Rain water harvesting system   (c) Replacement of ordinary Bulbs with CFL    (d)  ETP 

(e) Plantation of trees along side of the periphery of the Hospital building.

3. Letter received on 14.07.08 w.r.t letter dated 26.05.08, informing that needful is being done.

6. As decided on 28.11.08, inspection of the unit was done.

7. As decided on 29.12.08, letter for correction for deficiencies issued.

8. Reply received on 17.02.09 w.r.t. letter dated 28.01.09.

9. As per the decision taken on 29.01.09, reminder issued.

10. As per decision taken on 02.03.2009, A letter was sent for deficiencies, as communicated earlier based on the decision on 06.05.2008.


	Call for personal hearing in next meeting. 
	Letter for personal hearing issued.


	Addl. M.S of the hospital attended personal hearing on 04.09.09. The unit will apply afresh for CTO and also submit compliance report alongwith   status w.r.t 5 points & other deficiencies communicated to the hospital within 15 days.  



	25.
	Sardar Valabh Bhai Patel Hospital, East Patel Nagar, New Delhi-8
	50
	10.06.09
	CTE 28.08.08.

CTO 18.12.07.


	 Authorization is valid up to 30-5-2010.  CTO applied on 18.12.07. CTE applied on 28.08.08.
1. As per direction HCU was inspected on 19-3-2007(C/31) but BMW Management not found as per rule.

2. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy(Health) with copy to Pr.Secy(PWD) from chairman, DPCC was issued.

3. As decided on 27.08.08 reminder letter was issued.

4. As decided on 30.10.08, letter issued to submit compliance of deficiencies w.r.t documents etc regarding consent application and to submit waste water details and CGWA clearance.

5. As decided on 29.12.08, hospital was called for personal hearing on 29.01.2009.

6. Letter received on 04.03.09.

7. As per the decision taken on 29.01.09, the representative of the unit came for personal hearing today. It assured that it will file a reply within a week.

8. As per the decision taken on 02.03.2009, Final reminder issued.

9. Letter was issued as decided and NMR for DG set records.
	Ask the unit to correct the deficiencies observed during the inspection. 
	Letter issued. Noise monitoring report for DG Set submitted from Delhi Power Services & Co. and Reply received on 06.07.09 regarding measures taken/ being taken for rectification of deficiencies.
	Well drafted reminder letter.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	26.
	Nehru Homeopathic Medical College, Defense Colony, New Delhi-24


	100
	1-Dec-06
	CTO 05.12.06 

CTE. 13.10.08
	1. Authorization is valid up to 07.03.2010. Consent to Operate is valid up to 07.03.2010. CTE Granted.
2. Noise Monitoring Report for 125 KVA DG Set submitted.

3. As decided in the meeting on 18.03.08 letter for deficiencies was issued including seeking application for Consent to Establish under Air & Water Acts5. 

4. As per the general decision taken on 06.05.08, letter issued  on 26.05.08 for installation of:

(a) Solar water heating system (b) Rain water harvesting system(c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

5. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy (Health) with copy to Pr.Secy (PWD) from chairman, DPCC was issued.

6. As decided on 28.11.08 Reminder for Compliance of five points was issued.

7. Replies received on 16.03.09 regarding measures taken/ being taken on 5 points compliance.

8. Decision taken on 29.01.09, the representative of the unit came for personal hearing today. The unit will submit reply on all the five points by 02.03.2009. 

9. As per the decision taken on 02.03.2009, Final reminder for compliance issued.
	Issue reminder for full Compliance 
	Reminder letter issued. No Reply.


	Include the name of the hospital in the common D.O.Letter to be issued to Pr. Secy ( Health ) &  Pr.Secy ( PWD), GNCT Delhi for the compliance on the 5 Points  

	27.
	Satyawadi Raja  Harish Chander hospital, Plot No.30,Sector-7A, Narela, Delhi-40


	200
	13-Jun-07 
	 Not Applied
	1. Applied for authorization on 13-6-7.  Not applied for CTO and CTE.
2. SCU under BMW Rules was issued on 11-6-2007.

3. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Pr Secy (Health).

4. Meeting taken by Pr. Secy. (Health) on 25.09.07, it was decided that MS of the Hospital should submit Consent application within 15 days. 

5.. As decided in the meeting on 18.03.08 letter for deficiencies was issued  including seeking application for Consent to Establish under Air & Water Acts

6. As per the general decision taken on 06.05.08, letter issued on 26.05.08 for installation of 

(a) Solar water heating system  (b) Rain water harvesting system        (c) Replacement of ordinary Bulbs with CFL      (d)  ETP 

(e) Plantation of trees along side of the periphery of the Hospital building.

7. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy (Health) with copy to Pr.Secy (PWD) was issued.

9. Reply received on 06.02.09 regarding measures taken/ being taken and letter received dated 06.02.09 regarding Submission of Orange form.

8. As decided on 29.12.08, final reminder for CTE and interim report issued.

9. As per the decision taken on 29.01.09, final reminder issued.

10. As per the decision taken on 02.03.09, A common D.O. letter from Chairman, DPCC to Secretary Health and Secretary, PWD, was sent.

	Ask the unit to file interim report. 
	Letter issued. No Reply.


	Include the name of the hospital in the common D.O.Letter to be issued to Pr. Secy ( Health ) &  Pr.Secy ( PWD), GNCT Delhi for the compliance on the 5 Points  . Also call for personal hearing in the next meeting.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	28.
	Jag Pravesh Chand Hospital (Shastri Park Hospital),Govt. of NCT of Delhi, Shastri Park,Delhi-53
	200
	 25-Oct-06
	CTO- 20.11.07.

CTE- not applied.
	1. Authorization is valid up to 7-3-2010.  CTO applied on 20.11.07. CTE- not applied.
2. As decided in the meeting on 18.03.08 letter for deficiencies was issued  including seeking application for Consent to Establish under Air & Water Acts 

3. As per the general decision taken on 06.05.08, letter issued  on 26.05.08 for installation of:

(a) Solar water heating system (b) Rain water harvesting system   (c) Replacement of ordinary Bulbs with CFL (d)  ETP 

(e) Plantation of trees along side of the periphery of the Hospital building

4. EE (BMW) had talked to the official (s) of the hospital.
5. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy (Health) with copy to Pr.Secy (PWD) from chairman, DPCC was issued. Letter dated 24.10.08 received from the hospital.

6. As decided on 27.08.08, reminder letter was issued.

7. Letter Dated 10.11.08, received informing that HCU is making arrangements to process the proposal for (i) RWHS (ii) CFL (iii) & for this PWD has been requested. SWHS is not being installed since the HCU has already installed Boiler.

8. As decided on 29.12.08, letter for interim report issued.

9. As per decision taken on 02.03.09, Unit was called for personal hearing on 27.04.09 and taken on 01.06.09.

	The unit came for personal hearing today. They confirmed that they have already installed Solar Water Hearting System and will apply for Consent to Establish within 7 days. Other works like CFL, Rain Water Harvesting System is being done by PWD for which matter is under process and they will carry out the remaining compliance as early as possible. 
	Letter issued. No Reply.


	Ask for CTE.. Include the name of the hospital in the common D.O.Letter to be issued to Pr. Secy ( Health ) &  Pr.Secy ( PWD), GNCT Delhi for the compliance on the 5 Points  

	29.
	Northern Railway Divisional Hospital, S.P. Mukherjee Marg, Delhi-6
	50
	 20-Aug-04
	CTO- 21-Nov-07

CTE- 21.07.08 
	1. Authorization is valid up to 7-3-2010(C/56). CTE Granted. CTO valid upto18.11.10.
2. Deficiencies observed during inspection are:-

· Log book of BMW not maintained.

· Agreement with CBMWT expired.

·  currently waste found stored in storage area is there for quite some time.

· Sharp waste management not proper.

3. As decided on 29.09.08, letter was issued for correction of deficiencies observed on 17.09.08. 

4. Reply received vide letter dated 10.11.08 & informed that corrective measures taken.


	No action. 
	------------
	No action.

	30.
	Ayurvedic Hospital, MCD, Haiderpur, Delhi-52
	100
	 14.11.07
	CTE- 27.10.08

CTO- 27.10.08
	Applied for Authorization on 14.11.07. CTE granted. CTO applied on 27.10.08.
1.Vide letter dated 18.12.07 informed regarding having DG Set of 75 KVA which is not working since 2005 and in future it will function under the Air Act. 

2 As per the general decision taken on 06.05.08, letter issued on 26.05.08  for installation of:

(a) Solar water heating system     (b) Rain water harvesting system         (c) Replacement of ordinary Bulbs with CFL        (d)  ETP 

(e) Plantation of trees along side of the periphery of the Hospital building.

3. Note received from RMS stating that necessary proceedings have been initiated and Engineering department has been apprised about the directions of DPCC. Claims that there is no BMW generation in the hospital being a Ayurvedic Hospital. 

4. As decided on 29.12.08, letter for interim report issued.

5. As decided on 28.11.08 and 29.01.09, Reminders for Compliance of five points as decided earlier was issued.

6. Letters received on 08.04.09, regarding installation of Acoustic Enclosure and Possession of Building.

7. Hospital was called for personal having 27.04.09 and as decided letter was issued on 03.07.09 for Rain Water harvesting System and Solar Water Heating System.
8. Reply received on 20.07.09 and informed that the compliance is under process.
	Ask the unit to file compliance for Rain Water Harvesting System and Solar Water Heating System. 
	Letter issued. No Reply.


	Ask for status w.r.t 5 points.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	31.
	Babu Jagjeevan Ram M

memorial Hospital, Jahangirpuri, Delhi-33
	100
	 29-Jun-06
	CTO- 27.09.07
CTE- 06.08.08
	1. Authorization is valid up to 7-3-2010(C/112). CTO applied on 27.09.07. CTE granted.
2. Stack Monitoring report for DG Set submitted, shows emissions within limit.    Noise monitoring report for DG set (125 KVA) not submitted.

3. As per the general decision taken on 06.05.08, letter issued on 26.05.08  for installation of:

(a) Solar water heating system     (b) Rain water harvesting system          (c) Replacement of ordinary Bulbs with CFL         (d)  ETP 

(e) Plantation of trees along side of the periphery of the Hospital building.

4. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy (Health) with copy to Pr.Secy(PWD) from chairman, DPCC was issued.

5. Letter for CGWA clearance was issued as decided on 30.10.08.

6. As decided on 29.12.08, final reminder for compliance of all earlier directions issued.

7. A news item was published in the Times of India on 06.04.09 regarding the inspection of this Hospital including other four hospitals of Delhi Government by the Health Minister of Govt. of NCT of Delhi and her observations regarding improper management of BMW particularly Sharp Waste Management.

8. Inspection of the hospital was carried out on 18.04.08 & deficiencies w.r.t BMW management was observed and letter was issued. 
9. decision on 27.04.09: The nit came for personal hearing. SWHS, RWHS and conversion to CFLs to be done by 25.02.09. ETP to be installed within three months. Also ask the unit to file permission from DJB for ground water drawl.
10. DO letter issued on 26.05.09 from MS to the hospital for rectification of deficiencies by 25.05.09 with a copy to P. Secy. (Health), GNCTD and PS to Minister for Health.
	Call on in next meeting. 
	Reply received on 16.06.09 regarding measures taken/ being taken.
	Include the name of the hospital in the common D.O.Letter to be issued to Pr. Secy ( Health ) &  Pr.Secy ( PWD), GNCT Delhi for the compliance on the 5 Points.  

	32.


	Majeedia Hospital, Jamia Hamdard, IHMMR Campus, Hamdard Nagar, New Delhi-110 062


	136
	 23-Feb-07
	CTO-08.10.07

CTE- 16.12.08
	1. Authorization under BMW Rules is valid up to 7-3-2010. CTO applied on 08.10.07. CTE applied on 16.12.08.
2. As per the general decision taken on 06.05.08, letter issued on 26.05.08  for installation of:

(a) Solar water heating system        (b) Rain water harvesting system           (c) Replacement of ordinary Bulbs with CFL              (d)  ETP                                                (e) Plantation of trees along side of the periphery of the Hospital building.  

3. Vide letter dated 23.10.08, informed that 

· SWHS – under process.    

· RWHS – Already Installed .Awarded by Govt of Delhi.
· CFL – Already Executed.

· ETP – under process. 

· Plantation- Already under taken.

4. As decided on 29.12.08, the hospital informed that they are expanding their hospital by another 200 beds for creating medical college during the personal hearing.

5. Letter received on 05.02.09 informed regarding built-up area.

6. Inspection of the hospital was carried out by the team of Dr. T. K. Joshi.

7. As per the decision taken on 27.04.09, letter for rectification of deficiencies observed during the inspection issued.
	Issue reminder letter. 
	Reminder letter issued. Reply received on 30.07.09 regarding measures taken/ being taken.


	Letter seeking status w.r.t 5 points.

	33.
	Jai Prakash Narayan ApexTrauma Centre, Ansari Nagar, Raj Nagar, New Delhi-29


	200
	 7-Sep-06
	CTO- 27.09.07
CTE- 24.08.05 
	Applied for authorization on 07.09.06.  Applied for CTO on 27.09.07. CTE applied on 24.08.05 
1. HCU was inspected on 19-3-2007(C/50) and BMW Management found as per rule, but ETP was not in operation.

2. HCU had not submitted waste water test report 

3. Applied for Consent to Operate on 27.09.07. Noise monitoring report for DG set received from DPCC lab.

4..As decided in the meeting on 18.03.08 letter for deficiencies was issued  including seeking application for Consent to Establish under Air & Water Acts

5. Reply received.

6. As per the general decision taken on 06.05.08, letter issued  on 26.05.08 for installation of:

(a) Solar water heating system 

(b) Rain water harvesting system 

(c) Replacement of ordinary Bulbs with CFL 

(d)  ETP 

(e) Plantation of trees along side of the periphery of the Hospital building.

7. As per the decision taken in meeting on 13.06.08 a common letter to Jt. Secy(Health) with copy to D.G.(CPWD) from chairman, DPCC was issued.

8. As decided on 29.12.08, letter for interim report issued.

9. As per the decision taken on 29.01.09, reminder issued.
10. As per the decision taken on 02.03.09, reminder letter for compliance was issued.
	Call for personal hearing in next meeting. 
	Letter for personal hearing issued.


	Unit attended personal hearing on 04.09.09. The unit will apply afresh for Authorization and also submit compliance report alongwith   status w.r.t 5 points & other deficiencies communicated to the hospital within 15 days.  



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	34.
	Hedgewar  Arogya Sansthan, Opposite CPCB, Karkardooma, east Arjun Nagar, Delhi-32
	200
	 14-3-07
	CTE- 20.08.08.

CTO- 19.12.07


	1. Authorization is valid up to 30-5-2010. CTE Granted. CTO applied on 19.12.07.
2. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Pr Secy (Health).

3. Application for consent to operate received along with affidavit. The application reveals having two boilers (HSD fired) and two DG sets of 62.5 KVA,( without acoustic enclosure).Stack monitoring report  not  submitted. 

4. As per the general decision taken on 06.05.08, letter issued for installation of:

(a) Solar water heating system       (b) Rain water harvesting system           (c) Replacement of ordinary Bulbs with CFL           (d)  ETP 

(e) Plantation of trees along side of the periphery of the Hospital building.

5..As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy(Health) with copy to Pr.Secy(PWD)  was issued.

6. As per the decision taken on 27.08.08 CTE was issued subject to the condition that effluent status, noise monitoring report and CGWA clearance will be filed within 01 month. 

7. Reply received on 23.03.09, regarding the measures taken/ being taken on 5 points.

8. HCU was called for personal hearing on 27.04.09 and accordingly letter was issued.

	Ask the unit to file interim report about progress of work. 
	Letter issued. No Reply.


	Ask for the compliance status w.r.t. 5 points.Include the name of the hospital in the common D.O.Letter to be issued to Pr. Secy ( Health ) &  Pr.Secy ( PWD), GNCT Delhi for the compliance on the 5 Points  

	35.
	Hindu Rao Hospital Delhi – 110 007l.


	980
	5-Apr-06 
	CTE- 12.05.09 
CTO-12.05.09 
	Applied for Authorization on 05.04.06. CTE applied on 12.05.09. CTO applied on 12.05.09.
1. HCU requested to extend the time limit for installation of ETP. 

2. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Addl. Commissioner (Health), MCD5. As decided on 1-8-2007, D.O. letter was issued on 17.08.07 & 01.10.07 to Addl. Commissioner, MCD / Commissioner MCD., seeking consent application under Air Act. 

3. Letter dated 08.10.07 received and informed that matter regarding ETP is under process and will be finalized at the earliest.

4. As decided in the meeting on 18.03.08 letter for deficiencies was issued on 21.04.08.
5. As per the general decision taken on 06.05.08, letter issued  on 26.05.08 for installation of:

(a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d) ETP (e) Plantation of trees along side of the periphery of the Hospital building.
6. Inspection of the Hospital & monitoring of the incinerator was conducted on 06.01.09 . Deficiencies observed. VOC & Temperature range for Primary & Secondary Chambers are not meeting the prescribed standards.

7. Decision taken on 29.01.09, Representative of unit came for personal hearing today.  D. O. Letter from MS, DPCC to MS of Hospital, for rectification of the deficiencies observed during the inspection and monitoring. Unit to submit fresh monitoring report for incinerator. Unit to file compliance report, with dates, on the five points mentioned in our earlier letters. D. O. Letter also to be issued from Chairman, DPCC to Commissioner, MCD issued.

8. Reply received regarding measures taken/ being taken for rectification of deficiencies on 28.04.09.

9. D. O. letter was issued on 19.02.09 from MS, DPCC to the Hospital, 26.02.09 from Chairman DPCC to Commissioner, MCD, on 14.05.09 and 26.05.09 from MS DPCC to MS of the Hospital for compliance and monitoring report of the incinerator.

10. Reply dated 22.04.09, 20.07.09 received regarding measures taken/ being taken for the rectification of deficiencies. Monitoring report for incinerator conducted by GGSIPU on 12.0.09 received and showing the parameters within the prescribed limits. 

	Ask the unit to file full compliance including fresh monitoring report for incinerator. 
	Letter issued. Reply received regarding measures taken/ being taken along with fresh monitoring report for incinerator dated 20.05.09. 


	Issue letter for the compliance w.r.t 5 points & other deficiencies communicated to the hospital.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	36.
	Rao Tula Ram Memorial Hospital, Jafferpur, Delhi
	100


	7-Nov-06
	Not Applied
	1. Authorization is valid up to 7-3-2010. Not applied for CTE and CTO.
2. SCN u/s 21/22 of Air Act was issued on  01-5-2007 and on 11-06-2007.
3. Reply was received with the remark that APCD has been installed with incinerator and stack report is also submitted and the installation of ETP is under process with PWD.   

4. Reply received to SCN u/s 21/22 with the remark that they have applied for consent under air act but the same  has not been received.

5.  Meeting taken by Pr. Secy. (Health) on 25.09.07, it was decided that MS of the Hospital should submit Consent application within 15 days. Not Applied for Consent though submitted required fee for DG set monitoring.

6. The hospital was inspected by a three member team headed by Dr. T.K.Joshi, on 27.02.08 
· the records for incinerator revealed that incinerator was not operated during the period 19.11.07 to 03.12.07 and for the period 22.01.08 to 12.02.08 and the reasons could not be explained for the non-operation of the incinerator. 
· It was also revealed from the records maintained that temperature in the secondary chamber of the incinerator is for below the prescribed temperature. 

7. As decided in the meeting on 18.03.08 letter for deficiencies was issued on  19.05.08  including seeking application for Consent to Establish under Air & Water Acts

8. As per the general decision taken on 06.05.08, letter issued  on 26.05.08 for installation of :

(a) Solar water heating system  (b) Rain water harvesting system     (c) Replacement of ordinary Bulbs with CFL       (d)  ETP 

(e) Plantation of trees along side of the periphery of the Hospital building.

9. As per letter to DHS by the HCU, it reveals that though installation of STP was taken up in the last year. PWD has submitted the Plan & estimate but due to lack of funds it could not be materialized. Presently Septic Tanks are used for disposal of Soil Waste and maintained by PWD.

10. As decided on 29.12.08,  final reminder for CTE issued.

11. Inspection of the Hospital was conducted on 05.01.09. Deficiencies observed. 
· Incinerator is not in operation since 13.09.08. 
· Body of Venturi Scrubber found broken. 
· Incinerable Bio-Medical Waste is being treated /disposed through Operator of Common Bio-Medical Waste Treatment Facility.

12. As per the decision taken on 29.01.09, the hospital was asked, not to operate incinerator in view of broken scrubber and the facts that outsourcing of the Incinerable Bio-Medical Waste is being done successfully through Operator of Common Bio-Medical Waste Treatment Facility. Unit to file compliance report, on  the five points mentioned in our earlier letters

13. As per the decision taken on 02.03.09, Reminder letter seeking compliance report for the deficiencies communicated to the hospital issued. The name of the hospital was included in the common DO letter from Chairman, DPCC to Pr. Secy. (health) and Pr. Secy. (PWD).

14. Another DO letter was issued on 14.05.09 for compliance report.

15. Reply dated 11.05.09 received, regarding measures taken/ being taken.
.


	Call for personal hearing in next meeting. 
	Letter for personal hearing issued. Letter received on 05.08.09 regarding lifting of BMW of RTRM Hospital.


	Call for personal hearing in the next meeting.
Also include the name of the hospital in the common D.O.Letter to be issued to Pr. Secy ( Health ) &  Pr.Secy ( PWD), GNCT Delhi for the compliance on the 5 points.



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	37.
	Chacha Nehru Bal Chikatsalya, Geeta Colony, Delhi-110 031
	216
	1-May-07
	CTO- 02.04.08
CTE- 01.09.08
	1. Authorization under BMW rules valid up to 21.03.10 subject to the condition that ETP will be installed within 3 months. CTO is valid up to 01.04.11. CTE Granted
2. As per the general decision taken on 06.05.08, letter issued on 26.05.08  for installation of:

(a) Solar water heating system      (b) Rain water harvesting system            (c) Replacement of ordinary Bulbs with CFL 

(d)  ETP        (e) Plantation of trees along side of the periphery of the Hospital building.

3. As decided on 28.11.08, Reminder for Compliance of five points was issued.

4. Letter received on 02.02.09, referring earlier letters.

5. As decided on 29.12.08, CTO issued and letter for interim report issued.

6. As per the decision taken on 29.01.09, reminder issued.

7. As per the decision taken on 02.03.09, Letter for full compliance issued.

8. Reply received on 05.03.09, regarding the measures taken/ being taken on 5 points.

9. Reply received on 29.04.09.


	Ask the unit to file interim report. 
	Letter issued. Compliance report received on 13.07.09 stating matter with PWD.


	Ask for adequacy report for ETP.

	38.
	Guru Gobind Singh Govt. Hospital, Raghubir Nagar, New Delhi-110 027
	100
	13-Mar-07
	CTO- 19.12.07.

CTE (issued)


	Authorization applied on 13.03.07. CTO applied on 19.12.07. CTE Granted.

1. As decided in the meeting on 18.03.08 letter for deficiencies was issued on  21.04.08  including seeking application for Consent to Establish under Air & Water Acts 

2. Reply received w.r.t. letter dated 21.4.2008. 

3. As per the general decision taken on 06.05.08, letter issued  on  26.05.08 for installation of:

(a) Solar water heating system       (b) Rain water harvesting system               (c) Replacement of ordinary Bulbs with CFL 

(d)  ETP         (e) Plantation of trees along side of the periphery of the Hospital building.

4. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy.(Health) with copy to Pr. Secy.(PWD) from chairman, DPCC was issued.

5. A copy of the Letter sent to Ex. Engg. PWD received asking PWD to expedite the installation of ETP and also to take CGWA clearance.

6. As decided on 27.08.08 CTE was issued and Unit was asked to expedite the installation of ETP and ground water clearance from CGWA within 01 month. 

7. As decided on 28.11.08 Reminder for Compliance of five points was issued.

8. w.r.t letter dated 23.12.08, HCU has informed that 

· SWHS – installed 
· RWHS – Requested to PWD
· CFL - completed 
· ETP – Sanction issued. 
· Trees already planted.

9. As decided on 29.12.08, letter for interim report issued.

10. As per the decision taken on 02.03.09, The name of the hospital was included in the common DO letter from Chairman, DPCC to Pr. Secy. (health) and Pr. Secy. (PWD).

11. Letter received dated 04.05.2009.


	Call for personal hearing in next meeting. 
	Letter for personal hearing issued.


	M.S of the hospital attended personal hearing on 04.09.09. The unit will  submit compliance report alongwith   status w.r.t 5 points & other deficiencies communicated to the hospital within 15 days.  

Also include the name of the hospital in the common D.O.Letter to be issued to Pr. Secy ( Health ) &  Pr.Secy ( PWD), GNCT Delhi for the compliance on the 5 points.



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	39.
	Lady Hardinge Medical College and Associated Hospital, Shahid Bhagat Singh marg, New Delhi


	1227
	9-Mar-07
	CTE- 26.11.08.

CTO- applied
	1. Applied for authorization on 9-3-2007. CTE applied on 26.11.08. CTO applied.   
2. Letter issued on 28.12.07 asking Stack Monitoring report of Boilers as well as incinerator & for providing acoustic treatment/ enclosure for the 2 DG Sets of 160 KVA each , noise monitoring  report for the DG Sets & also for installation of ETP. Reply to the said letter received.

3.  As decided in the meeting on 18.03.08, letter for deficiencies was issued on 25.04.08.
4. Reply received w.r.t. letter dated 25.4.2008.

5.As per the general decision taken on 06.05.08, letter issued on  26.05.08 for  installation of:

(a) Solar water heating system    (b) Rain water harvesting system       (c) Replacement of ordinary Bulbs with CFL 

(d)  ETP      (e) Plantation of trees along side of the periphery of the Hospital building.

6. As per the decision taken in meeting on 13.06.08 a common letter to Jt. Secy(Health) with copy to D.G.(CPWD) from chairman, DPCC was issued.

7.Reply dated 08.10.08 received regarding compliance of letter dated 26.05.08 informing: 
· Solar water heating systems were installed in the new building & 3 more are being installed.

· There are 17 Rain Water Harvesting pits in the institutional Area & 12 in residential area.

· Replacement of the ordinary bulbs with CFL is being carried out in phased manner.

· For ETP installation mentioned that 2 ETPs have to be installed for which necessary funds are not available & likely to be sanctioned in next financial year. Till then working only on the installation of 1 ETP and project estimate is enclosed, but no such enclosure found along with letter.

· There are ample of trees present. 
· Informed that Stack monitoring repots & Noise monitoring reports will be submitted as soon as they get it from NPC.
· Informed that Energy Auditing has been carried out in 2007 & accordingly all the energy saving measures are being taken.

8. Inspection of the Hospital & monitoring of the incinerator  was conducted on 19.12.08 . Deficiencies observed. 
· Particulate Matter, VOC, Temperature range for Primary Chamber are not meeting the prescribed standards. 
9. Letter issued for the deficiencies observed as decided by the Committee.

10. As per the decision taken on 29.01.09, reminder issued on 24.02.09. Another DO letter issued on 14.05.09 for full compliance report and monitoring report of incinerator.
11. Reply dated 02.07.09 received regarding measures taken/ being taken. Fresh monitoring report not submitted.


	Call for personal hearing in next meeting. 
	Letter for personal hearing issued.


	Director  of the hospital attended personal hearing on 04.09.09. The unit will apply afresh  for CTO and also submit compliance report alongwith   status w.r.t 5 points & other deficiencies communicated to the hospital within 15 days.  



	40.
	Central Jail

 Hospital, Tihar
	150
	Applied on 24.06.09.
	Not Applied
	1. Applied for Authorization on 24.06.09. CTE and CTO not applied. 
2. Meeting taken by Pr. Secy. (Health) on 25.09.07, it was decided that MS of the Hospital should submit Consent application within 15 days. However Consent Application under Air Act not received so far. 

4. As decided in the meeting on 18.03.08 letter for deficiencies was issued on  25.04.08  including seeking application for Consent to Establish under Air & Water Acts 

5. Reply received informing that the matter has been referred to PWD in respect to letters received from DPCC. List of Lab was sought which was  faxed to the hospital.

6. As per the general decision taken on 06.05.08, letter issued  on 26.05.08 for installation of :

(a) Solar water heating system      (b) Rain water harvesting system        (c) Replacement of ordinary Bulbs with CFL 

(d)  ETP      (e) Plantation of trees along side of the periphery of the Hospital building.

7. Reply dated 27-05-08.w.r.t letter dated 25-04-08 & letters received on 08.07.08  w.r.t letter dated 26.05.08.mentioning that to communicate with Prison Head Quarters for the necessary action.

8. Reply Received Copy of the letter sent to Superintendent Engineer, PWD forwarded. 

9. As decided on 27.08.08 reminder letter was issued. 

10. A letter dated 11.11.08, received from Exe Engineer (E) stating that for operation of DG Sets Consent is not required. The letter is for both the Jails Centre Jail Tihar & Jail at Rohini.


	Inspection to be expedited. 
	Inspected, deficiencies observed. Applied for renewal of Authorization on 24.06.09.
	Letter for rectification of the deficiencies observed during the inspection. Also call for  personal hearing in the next meeting.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	41.
	ESI Hospital, Shree Maa Anandmayi Marg, Okhla phase-1, New Delhi- 110020
	150
	22-Oct-07
	Not Applied
	1. Applied for renewal of Authorization under BMW Rules on 22.10.07. CTE and CTO not applied.
2. D.O. letter issued to Jt. Secy. (Labour) GOI with copy to DG ESI. Reply received from Jt. Secy. (labour) GOI.

3. .As decided in the meeting on 18.03.08 letter for deficiencies was issued  including seeking application for Consent to Establish under Air & Water Acts 

4. As per the general decision taken on 06.05.08, letter issued on 26.05.08  for installation of:

(a) Solar water heating system  (b) Rain water harvesting system        (c) Replacement of ordinary Bulbs with CFL 

(d)  ETP         (e) Plantation of trees along side of the periphery of the Hospital building.

5. Letter dt 23.01.09 received informing that they are having their BMWM contract with Synergy.

6. Replies received dated 29.01.09 and 02.02.09 w.r.t letters dated 13.01.09 and 22.01.09.

7. As per the decision taken on 29.01.09, final reminder issued.

8. As per the decision taken on 02.03.09, Unit was called for personal hearing on 27.04.09 and issue of non lifting of BMW was taken up with the operator (M/s Synergy Waste Management Pvt. Ltd.) and Letter of DHS dated 24.02.09 was forwarded to the unit.

9. Decision on 27.04.09: Unit came for personal hearing. He promised to apply for CTE by tomorrow. SWHS installed. RWHS and CFLs will be installed by 25.05.09. ETP is not required since effluent of the Hospital is going into the CETP, Okhla which is 60-70 yards from the hospital. Letter issued.

	Dr. Chetna to speak. 
	Dr. Chetna Spoken. No Reply.
	Reminder for CTE & CTO.

	42.
	ESI Hospital, Sector-15. Rohini
	100
	05-Oct-07
	CTO- 18.07.08
CTE- 24.10.08
	1. Applied for renewal of authorization on 05.10.07. Applied for CTO on 18.07.08. CTE granted
2 As decided in the meeting on 18.03.08 letter for deficiencies was issued  including seeking application for Consent to Establish under Air & Water Acts 

3. As per the general decision taken on 06.05.08, letter issued ON 26.05.08  for installation of:

(a) Solar water heating system      (b) Rain water harvesting system        (c) Replacement of ordinary Bulbs with CFL 

(d)  ETP        (e) Plantation of trees along side of the periphery of the Hospital building.

4. Letter dated 12-06-08 and 16-06-08.w.r.t letter dated 26-05-08.receiverd , asking for time upto 31-10-08, for  necessary installation. 

5. Vide letter dated 24.10.08, informed that 

· SWHS – proposals received and are being processed.

· RWHS – Estimates received & are being vetted.
· CFL – will be completed soon.
· ETP – Estimate received. Time asked upto 31.03.10. 
· Frontal & side periphery has already trees planted at back side. Matter is being followed.

6. As decided on 30.10.08, letter was issued for properly filling up the CTE form and to submit compliance of earlier decisions of BMW Committee.

7. As decided on 28.11.08 Reminder for Compliance of five points as decided earlier, was issued.


8. As decided on 29.12.08, CTE subjected to compliance of all the five conditions issued.

9. As per the decision taken on 02.03.09, letter for full compliance issued.

	The unit came for personal hearing today. it was observed that the person is from the ESI hospital and he is taking up the mater with headquarters and nothing concrete has been found. Send a letter to unit to depute a responsible person from headquarter for giving proper commitments regarding the progress of work.  Call for personal hearing in next meeting. 
	Letter issued. Letter received on 25.05.09 regarding outsourcing of BMW.


	M.S of the hospital attended personal hearing on 04.09.09. D.O letter from M.S DPCC to DG,ESI highlighting the issues & for compliance  w.r.t 5 points.  



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	43.
	Institute of Human Behaviour & Allied Sciences, Near GTB Hospital, Dilshad Garden
	190
	5-Aug-05
	CTO- 17.07.08
CTE- 04.08.08
	1. Authorization applied on 05.08.05. CTE issued with condition that ETP will be installed expeditiously and noise monitoring report and CGWA clearance to be filed within 01 month. Applied for renewal of Consent to Operate on 15.01.08.
2. Acoustic Enclosure provided for DG Set of 2x 625 KVA & for other DG Set, (180 KVA DG Set) it is informed that it is not in operation (acoustic enclosure not provided). Noise Monitoring Report for DG Set not submitted.

3. As decided in the meeting on 18.03.08 letter for deficiencies was issued  including seeking application for Consent to Establish under Air & Water Acts

4. As per the general decision taken on 06.05.08, letter issued ON 26.05.08  for installation of: 
(a) Solar water heating system   (b) Rain water harvesting system    (c) Replacement of ordinary Bulbs with CFL      (d)  ETP
(e) Plantation of trees along side of the periphery of the Hospital building.

5. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy. (Health) with copy to Pr. Secy. (PWD) from chairman, DPCC was issued.

6. Communication along with effluent test report from DPCC lab and a copy of letter addressed to HOD, Deptt. of Microbiology of IHBAS received. Parameter of Bio Assay   not done.

7. w.r.t letter dated 22.10.08, vide letter dated  07.11.08, informed that for CGWA clearance matter is under process and Noise Monitoring report submitted for DG Set of 625 KVA.

8. As per the decision taken on 02.03.09, letter for full compliance issued.

9. Replies received on 28.04.09 and 22.05.09 regarding compliance report of 5 points.


	Ask the unit to file adequacy report from empanelled consultant of DPCC. 
	Letter issued. Reply received on 13.07.09.


	Ask to apply afresh for authorization and also to submit adequacy report for ETP.

	44..


	Palika Maternity Hospital, Lodhi Colony , New Delhi-3
	50
	09-Aug-05


	CTE- 27.11.08

CTO- not applied.

	1. Authorization is valid up to 30-01-2010. CTE applied on 27.11.08. CTO not applied.
2. SCN u/s 21/22 of Air Act was issued on 11-6-2007(C/137) but HCU did not apply under Air Act.

3. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Chairperson, NDMC..

4. Letter issued seeking consent application under Air Act , HCU s has informed in its reply that there is no Boiler and DG Set in the Hospital and also informed that installed incinerator is not functional ( closed) 

6. As decided in the meeting on 18.03.08 letter for deficiencies was issued  including seeking application for Consent to Establish under Air & Water Acts

As per the decision taken in meeting on 13.06.08 a letter from Chairman, DPCC to Chairman, NDMC was issued.

8. As decided on 27.08.08 reminder letter was issued. 

9. Inspection of the Hospital & monitoring of the incinerator was conducted on 11.02.09. Deficiencies observed.  VOC & Temperature range for Secondary Chamber are not meeting the prescribed standards. Electrically operated Incinerator. The incinerator was earlier not operational and restated in last week of December 2008. Deficiencies observed during the inspection on 11.02.2009. 
· Sharp Boxes for sharps needs to be provided. 
· Records for BMW maintained however needs improvement. 
· Proper Temperature recording system required should be provided. Properly Trained /Qualified personnel for operation & Maintenance of Incinerator are required which is lacking. 1 DG Set of 100 KVA without acoustic enclosure found kept which is reportedly has not been commissioned/ operated so far. 
· As per the report of Dr. Joshi’s team, the Hospital/ NDMC may be asked to close down/ not to operate the Incinerator and dispose their Incinerable waste through Common Bio Medical Waste Treatment Facilities (CBWTF).

12. As per the decision taken on 02.03.09, D.O. Letter from MS DPCC to MS of Hospital with copy to Chairman, NDMC, for rectification of the deficiencies observed during the inspection and monitoring, Unit to submit fresh monitoring report for incinerator issued.

13. Reply received and informed that incinerator is not operational these days and presently the BMW through disposing operator of CBMWTF.


	Call for personal hearing in next meeting. 
	Letter for personal hearing issued.


	M.S of the hospital attended personal hearing on 04.09.09. It was informed that incinerator is not being operated, for D.G set acoustic provided. Noise Monitoring Report to be submitted.
CTE Granted. The unit will apply for CTO & submit compliance report w.r.t deficiencies communicated to the hospital, within 15 days.  Unit be directed to close down incinerator & outsource for disposal of BMW.


	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	45
	International Centre for Genetic Engineering & Bio Tech, ICGEB  Campus, P.O. Box  10504, Aruna Asaf Ali Marg, Delhi -67.
	Nil
	21- Mar- 05

and on 11.06.08 (for renewal)
	CTE- 11.07.08

CTO- 11.07.08
	1. Applied on 11.06.08 for renewal of authorization under BMW Rules. Applied for CTE and CTO on 11.07.08. 

2. CTE was issued with conditions that CGWA clearance to be filed within 01 month and Noise monitoring Report for DG Sets . STP already installed.8.W.r.t letter dated 22.10.08, Copy of permission letter Dated 06.09.02, from CGWA Tube Well submitted.8. Noise monitoring report for two DG Sts of 625 KVA submitted.

3. Test report of STP from GGSIPU received. Adequacy report for STP not submitted.

4. This is a case of Research Centre of Govt. of India, which is engaged in research activities related with Genetic Engineering & have applied for authorization under BMW Rules. Provisional Authorization granted earlier was valid up to 05.11.2002. Application for renewal was received on 21.03.05. 
5. The Institute has installed an incinerator for the disposal of BMW and submitted stack monitoring report dated 19.05.05. Showing parameters within the prescribed limits.
6. As decided in the meeting on 18.03.08, letter for deficiencies was issued.

7. Inspection of the unit & monitoring of the incinerator was conducted on 09.02.09. Deficiencies observed.  VOC & Temperature range for Primary and Secondary Chambers are not meeting the prescribed standards. Deficiencies observed w.r.t BMW Management. Color coded Bags/ Containers not provided. Shredder not provided (for Autoclavable Waste). Proper recycling system for water for scrubber not observed. Records were not maintained for Autoclavable Waste. Isolated Storage Site not provided for Autoclavable BMW. Less quantum of Incinerable Bio-Medical Waste mainly from Animal House which (animals are used for research) is kept in Deep Freezer. Incinerator is operated once in a week. Proper Temperature recording system required, should be provided. Properly Trained /Qualified personnel for operation & Maintenance of Incinerator are required which is lacking. As per the report on Dr. Joshi’s team, the unit may be asked to close down/ not to operate the Incinerator and dispose the Incinerable waste through the operator of Common Bio Medical Waste Treatment Facilities (CBWTF).

8. As decided on 29.12.08, letter for adequacy report of STP issued.

9. As per the decision taken on 02.03.09, D.O. Letter dated 23.03.09 & 14.05.09 from MS DPCC to Director of the institute for rectification of the deficiencies observed during the inspection and monitoring, Unit to submit fresh monitoring report for incinerator and also submit Adequacy report for STP issued. 

10. Reply dated 03.07.09 received. Monitoring report for incinerator conducted by GGSIPU on 03.07.09 received, VOC in ash (0.02 %) is not meeting the prescribed standards. 


	Call for personal hearing in next meeting.
	Letter for personal hearing issued. Reply received on 03.07.09 regarding measures taken/ being taken. 


	Unit attended personal hearing on 04.09.09. The unit will  submit compliance report w.r.t deficiencies communicated to the hospital alongwith Adequacy Report for STP, within 15 days.  



	46
	Bhagwan Mahavir Hospital  , H – 4/5, Pitampura, Delhi -34.
	200
	19- Mar-07
	CTO- 20.09.07
CTE- 07.10.08
	1. Applied for Authorization on 19.03.07. Applied for CTO on 20.09.07. Applied for CTE on 07.10.08
2. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 24.04.08 including seeking CTE.
3. Reply received w.r.t. letter dated 24.4.2008.

4. As per the general decision taken on 06.05.08, letter issued  ON 26.05.08       for installation of:

      (a) Solar water heating system           (b) Rain water harvesting system             (c) Replacement of ordinary Bulbs with CFL        (d)  ETP  
      (e) Plantation of trees along side of the periphery of the Hospital building.

4. Reply dated 10.06.08 received w.r.t. letter dated 24.04.2008 regarding submission of reports w.r.t 2 DG sets and waste water generated in the hospital was received.

5. Reply  dated 23-06-08.w.r.t latter dated .26-.05-8 was received regarding doing the needful as directed
6. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy(Health) with copy to Pr.Secy(PWD) from chairman, DPCC was issued.
7. As decided on 27.08.08, reminder letter was issued.
8. Reply received on 09.02.09 regarding measures taken/ being taken.
9. As decided on 29.12.08, final reminder for submitting for compliance.
10. Reply received regarding measures taken/ being taken.
11. As per the decision taken on 29.01.09, final reminder issued.
12. As per the decision taken on 02.03.09, Letter for full compliance, also mention to contact CGWA regarding Rain Water Harvesting System etc issued.


	Call for personal hearing in next meeting.
	Letter for personal hearing issued.


	Unit attended personal hearing on 04.09.09. CTE Granted.

The unit will  submit compliance report alongwith   status w.r.t 5 points & other deficiencies communicated to the hospital within 15 days.  

Unit to be inspected.

Also include the name of the hospital in the common D.O.Letter to be issued to Pr. Secy ( Health ) &  Pr.Secy ( PWD), GNCT Delhi for the compliance on the 5 points.



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	47
	Swami    Dayanand Hospital, Shahdara , Delhi-32
	230


	01-May-05
	CTE- 24.06.08.

CTO- 19.07.05
	1. Authorization is valid up to 7-3-2010. Applied for CTE on 24.06.08. CTO valid upto 30.05.10.
2. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 02.05.08. Reply received vide letter dated 09.06.08 regarding submission of reports for DG Sets & waste water test report.



3. As per the general decision taken on 06.05.08, letter issued  on 26.05.08 for installation of  

(a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d) ETP 

(e) Plantation of trees along side of the periphery of the Hospital building.

4. Reply dated 10-06-08, w.r .t letter dated 26-05-08, received informing about doing the needful as directed.

5.  Decision taken on 27.08.08, While CTE application has been received, it cannot be processed since wastewater generation and its treatment details are not submitted and also submit CGWA clearance. MS to inform MS accordingly.

6. Inspection of the Hospital was conducted on 15.01.09 & monitoring of the incinerator was conducted on 16.01.09. Deficiencies observed that, Temperature range for Primary Chamber is not meeting the prescribed standards.

7. As per the decision taken on 29.01.09, D. O. Letter from MS, DPCC to MS of Hospital, for rectification of the deficiencies observed during the inspection and monitoring. Unit to submit fresh monitoring report for incinerator. Unit to file compliance report, with dates, on the five points mentioned in our earlier letters. D.O. Letter also to be issued from Chairman, DPCC to Commissioner, MCD, issued.

8. Reply dated 02.03.09 & 13.05.09 received, regarding measures take0n/ being taken

9. Monitoring report for incinerator for monitoring conducted by Guru Gobind Singh Indraprastha University on 28.03.09 shows parameters within the prescribed limit. 

10. Another DO letter issued from MS, DPCC to the Hospital on 14.05.09 for compliance report.
11. Reply dated 25.05.09 received informing collapsing of chimney due to high velocity squall on 22.05.09 and also about other measures taken.

12. Accordingly, letter was issued on 03.07.09 to the unit for not operating the incinerator till restoration of chimney and confirmation and compliance report.
13. Reply dated 14.07.09 received informing that incinerator shall not be operated till restoration of chimney and confirmation report. Also informed about the other measures taken.


	A letter be sent to the unit that incinerator should not be operated till restoration of chimney and confirmation followed by inspection by Dr. T.K. Joshi’s team. Also ask the unit to provide a copy of compliance on five points as stated to be submitted on 02.03.2009.
	Letter issued.

To be inspected.
	Inspection.
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	48


	MCD Chest Clinic and Hospital, Nehru Nagar, New Delhi- 65
	55
	28-Dec-04
	Not Applied
	1. Authorization is valid till 30-10-2010. CTE and CTO not applied.
2. SCN u/s 21/22 of Air Act was issued on 11-06-2007(C/82) since HCU had not applied under Air Act.

3. HCU submitted the reply on 26-7-2007(C/102) wherein it is mentioned that the DG set is out of order and not being used by them.

4. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 02.05.08 including seeking application for CTE.

5. Reply received w.r.t. letter dated 02.05.08. Required documents not submitted instead asked whether it is necessary to obtain consent under Air / Water Acts.

6. Another letter dated 09.08.08 received. It is informed that PWD has been requested to provide information so that needful can be done as directed by DPCC. It is also informed that neither Incinerator nor DG Set is working since 2002. 

Letter received. 

7. As decided on 27.08.08 reminder letter was issued. 

8. As decided on 01.06.09, letter issued and reply dated 16.06.09 was received. 


	Ask the unit to file interim report along with CTE application. 
	Letter issued. Reply received on 16.06.09 regarding measures taken/ being taken for Consent to Establish, Solar Water Heating System and Conversion of CFLs.


	Issue letter clarifying the things and also ask for CTE & CTO 



	49
	Maharishi Balmiki Hospital, Pooth khurd , New Delhi-39
	100
	30-Jan-04
	CTO 26.03.07 
CTE

07.07.08
	1. Authorization is valid up to 30-01-2010.  CTE granted. CTO valid upto 03.10.10.
2. As decided on 27.08.08 CTE was issued with conditions that CGWA clearance and proper affidavit will be filed within 01 month. 

3. As decided in the meeting on 18.03.08, letter for deficiencies was issued.

4. As per the general decision taken on 06.05.08, letter issued on 26.05.08 for installation of 

(a) Solar water heating system      (b) Rain water harvesting system         (c) Replacement of ordinary Bulbs with CFL          (d)  ETP 

(e) Plantation of trees along side of the periphery of the Hospital building.

5. Copy of communication to EE (PWD) by the HCU submitted w.r.t the letters issued by DPCC vide letter dated 11.06.08.6. Another letter received from the Hospital on 10.07.08 stating the matter has been referred to PWD.

6. As per the decision taken in meeting on 13.06.08 a common letter to Pr. Secy (Health) with copy to Pr.Secy(PWD) from chairman, DPCC was issued.

7. Reply dt. 28.11.08 received regarding five point compliance stating 

· SWHS under process.

· RWHS not required 

· CFL replacement is done in phase manners. 

· ETP is already installed 

8. As decided on 29.12.08, letter for interim report issued.

9. As per the decision taken on 02.03.09, the hospital was asked to file adequacy report for ETP, For Rain Water Harvesting System, and hospital to contact CGWA.

10. Reply received on 29.04.09 regarding compliance report of 5 points.


	Ask the unit to file adequacy report of ETP and permission from DJB for ground water extraction as per new orders. Unit to submit  CGWA opinion on Rain Water Harvesting System and ground water drawl.  
	Letter issued.

No Reply.
	Issue letter with clarification for adequacy report.
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	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	50
	Dr. Shyama Prasad Mukherjee Chest Hospital, Patpar ganj, Delhi-91
	52
	17-Aug-06
	CTE- 04.12.08.

CTO- 04.12.08
	1. Authorization was valid up to 7-3-2010. Applied for CTE and CTO on 04.12.08.
2. HCU reply to the SCN under Air Act with the undertaking that no DG set is in operation(C/58).  3. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 26.05.08.  

3. Reply dated 12-06-08.w.r.t letter dated 26-05-08 received. Another letter received on 10.07.08.

4. Letter was received.

5. As decided on 27.08.08 reminder letter was issued.


	Ask the unit to correct the deficiencies observed during the inspection. 
	Letter issued. Compliance report received on 09.07.09 regarding measures taken for rectification of deficiencies observed during the inspection.


	CTE & CTO granted.

	51
	National Institute of Immunology, Aruna Asaf Ali Marg, New Delhi-67
	Nil
	3-Jun-04


	CTE- 27.11.08

CTO- 13.02.09 


	1. Authorization is valid upto 30.04.09. Applied for CTE on 27.11.08. Applied for CTO on 13.02.09. 

2. Letter dated 15.10.08 received asking for time to submit the form as testing of noise level of D.G. set and stack monitoring is in process. 

3. As decided on 27.08.08, reminder letter was issued.

4. Vide letter dated 07.10.08, request made for extra time for submission of test reports for DG Set. 

5. Inspection of the unit & monitoring of the incinerator was conducted on 11.02.09. Deficiencies observed.  Particulate Matter, VOC & Temperature range for Primary and Secondary Chambers are not meeting the prescribed standards. Deficiencies observed w.r.t BMW Management.  

· Incinerator is operated twice in a week. 

· Leakages observed from ID Fan portion. 

· Shredder not provided (for Autoclavable Waste). 

· Sharp Boxes not provided. Proper colored bags not found in use. 

· Records for incinerable Waste maintained however not properly maintained. 

· Generates less quantum of Incinerable Bio-Medical Waste, mainly from Animal House, Dead Animal bodies, used in research, is kept in Deep Freezer.  

· Proper Temperature recording system required should be provided.  Properly Trained /Qualified personnel for operation & Maintenance of Incinerator are required which is lacking. 

· Proper record for BMW and Incinerable Waste need to be maintained. 

· Lack of awareness about BMW management, Staff requires Training/ Awareness. For DG Sets (1500 KVA, 1000 KVA and 20 KVA) acoustic enclosure not provided. 

As per the report of Dr. Joshi’s team, the unit may be asked to close down/ not to operate the Incinerator and dispose the Incinerable waste through the operator of Common Bio Medical Waste Treatment Facilities (CBWTF).

6. Decision taken on 29.01.09, the representative of the unit came for personal hearing today.  The unit will apply for Consent to Operate and send a copy of noise monitoring report of the D.G. Set.

7. Reply dated 09.04.2009, received regarding measures taken/ being taken.

8. As per the decision taken on 02.03.09, 27.04.09 and 01.06.09, D.O. Letter issued on 23.03.09 & 14.05.09 from MS DPCC to Director of the institute for rectification of the deficiencies observed during the inspection and monitoring, to submit fresh monitoring report for incinerator. Reminder issued on 26.06.09.
9. Reply dated 03.07.09 received, informing that outsource of BMW disposal through M/s Metro Bio-care Services Pvt. Ltd. 
	Issue reminder letter for full compliance.
	Reminder letter issued. Reply received regarding outsourcing of BMW to M/s Metro Bio-Care Services Pvt. Ltd.


	Ask to apply afresh for authorization under BMW Rules and also seek compliance w.r.t  deficiencies communicated to the unit. Unit to provide acoustic enclosure and submit noise monitoring report for  DG Sets .

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	52
	Moti  Nagar Hospital 

(Acharya Bhikshu Hospital), Govt. of Delhi, Moti Nagar, Delhi-15
	81
	25-Oct-07


	CTE- 02.06.09.

CTO- 02.06.09.
	1. Authorization applied on 25.10.07. Applied for CTE and CTO on 02.06.09.
2. letter received on 05.02.09.

3. As decided on 29.12.08, letter for interim report issued.

4. As per the decision taken on 29.01.09, reminder issued.

5. As per the decision taken on 02.03.09, the clarification was sent regarding application of CTE, as purchase of form is not the Consent to Establish. If applied, copy of the application should be provided along with the receipt of the application.


	Call for personal hearing in next meeting. 
	Letter for personal hearing issued.


	M.S of the hospital attended personal hearing on 04.09.09. 

The unit will  inform the present status w.r.t disposal of bio medical waste within 15 days.


	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	53.
	Rajiv Gandhi Super Speciality Hospital

Near GTB Hospital, Tahirpur, Delhi-93
	650
	Not applied
	CTE

06.07.09.

CTO

Not applied
	1. Authorization not applied. Applied for CTE on 06.07.09. Not applied for CTO.
2. As decided trainee BMW inspected on 21.11.08 & following observed 

· Building of Hospital found under Construction.   

· It was informed that the construction started in year 2000.     

· HCE is having a Plot Area of 52595 sq. mt. and proposed Build-up area of 60490 sq. mt.                                                                            

· Proposed Capital investment of Rs.99.71 Crores.                                                                                                      

· 4 DG set(s) of 1000 KVA each with acoustic enclosures having Stack Height of approx 8 mts observed.  

· Rain Water Harvesting System found under construction.   

· STP (Sewage Treatment Plant) found under construction.      

3. Letter of CTE was issued as decided on 28.11.08.        

4. Letter received on 30.01.09.                               


	The unit came for personal hearing today. They confirmed that they will be applying for CTE within 1 month however they have been asked to do within 15 days. Further they told that 98 % construction is already over and remaining 2 % will be done in PPP mode. Installation of Solar Water Heating System, CFLs,  medical gas line will be done by PPP partner. However, STP and Rain Water Harvesting system is already complete. He was asked to submit the details of his statements within 15 days along with details of Plantations carried out on the periphery of the hospital. He also told that they have not received any letter from DPCC. Accordingly copy of letters required to be complied were handed over to the hospital’s representatives. He was also asked to provide the total covered area in the hospital. 


	Letter issued. No Reply.


	CTE  granted. Ask the unit to submit adequacy report for ETP. Inspect the unit thereafter.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Authorization Application Date
	Date of application for consent
	Brief facts
	Decision Taken in the Meeting on  01.06.09


	ATR/status
	Decision taken in the Meeting on 04.09.09

	54
	Institute of Liver & Biliary Sciences, D-1, Vasant Kunj, New Delhi-70
	188
	Not Applied.
	CTE- 16.10.08

CTO- 29.06.09
	1. Not applied for Authorization. Applied for Consent to Establish under Air & Water Act on 16.10.08. Applied for CTO on 29.06.09.
2. Stated in the application that EC not required as the total built up area of the project is less than 20,000 Sq. meters.

3. CTE issued as decided on 28.11.08.

4. As per the decision taken on 02.03.09, hospital was inspected by the team of Dr. T.K. Joshi.
	Call on in next meeting. 
	------------
	Letter seeking application for authorization under BMW Rules, Adequacy report for ETP,  approved building plan for the second phase of the project along with the details of the total built  up area in both the phases of the project.

	55
	NDMC Veterinary Hospital, Moti Bagh, New Delhi. 
	NIL
	19.03.07
	Not applied 
	1. Applied for authorization on 19.03.07. Not applied for CTE and CTO. 

2. Inspected on 17.08.09, following deficiencies were observed:

· Temperature in Primary and Secondary Chambers of incinerator not found within the prescribed standard.

· Proper Temperature recording System (Graphic Recorder or some computerized control system), needs to be provided.
· No segregation of waste found. There is common bin for all type of wastes.

· BMW management not found as per BMW rules.

· Colour coding not followed.

· Bio-hazard symbols not provided on storage bins.

· Isolated storage site for BMW not provided.

· Records maintained for incinerable BMW. Sharp waste management provided.
	Dr. T.K. Joshi’s team to inspect and report. 
	Inspected.
	Letter for CTE, CTO & for correction of the deficiencies observed during the inspection. Unit to also submit monitoring report for the incinerator from any of the empanelled laboratories of DPCC.

	56
	Shri Dada Dev Matri Avum Shisu Chikitsalya,Dabri, New Delhi-110045
	64


	Applied on 12.03.09
	Not applied 
	1. Applied for Authorization on 12.03.09. Not applied for CTE and CTO.
2. Hospital was inspected by the team of Dr. T.K. Joshi as decided by BMW Committee No. 1 in its meeting held on 02.03.09. Deficiencies observed.
	Ask the unit to correct the deficiencies observed during the inspection. Also ask the unit to apply for CTE and comply with the five points.  
	Letter issued. Reply received on 05.08.09 regarding measures taken/ being taken
	Seek  CTE & CTO & also status of compliance..

	57
	Janak puri Super Specialty Hospital (Govt. of NCT of Delhi), C-2/B, Janakpuri, New Delhi-58. 
	300
	Applied on 28.07.09
	Not Applied.
	1. Applied for Fresh Authorization under BMW Rules on 28.07.09. As informed, OPD services are operational.

2. Authorization fee submitted Rs. 3000/-. Fee not submitted for 300 beds.
	--------------
	---------
	Ask the unit to apply for  CTE & CTO. 

	58. 
	National Institute of Communicable Diseases,   22, Sham Nath Marg , Delhi-54
	NIL
	Applied on 14.06.04
	Not Applied.
	1. Applied for Authorization on 14.06.04.  Not applied for CTE and CTO.

2. Inspected on 06.05.04, Deficiencies observed

· No ECS with incinerator.

3. As decided on 06.05.04, letter for deficiencies issued on 20.05.04.

4. Flue gas analysis report received on 05.06.04.

5. SCN issued on 17.12.04 for closure of the incinerator.

6. As decided on 17.07.09 in the meeting of BMW Committee No.3, Case has been shifted to BMW Committee No. 1.

7. Incinerator not in operation, BMW disposal through operator of CBMWTF.
	-----------
	--------
	Issue well drafted letter seeking application for  CTE, , CTO & Authorization

.


	S. No-
	Name and Address
	Date of application
	Brief Facts
	Decision Taken on 01.06.09
	ATR/Status
	 

	
	
	Auth.
	Consent
	
	
	
	 

	1
	International Panaacea Limited A-31/B-1, Mohan Co- Opeartive Indst. Est. Mathura Road, New Delhi-44 
	Not Applied
	22.05.06 (CTR)
	1. The unit is engaged in  formulation of Bio Tech Product.
	Inspection to be expedited.
	Inspection was conducted on 18.06.09 and deficiencies were observed.               
	

	2
	Shalaks Pharmaceuticals Pvt. Ltd. 12, DLF, Moti Nagar, Main Najafgarh, New Delhi-15
	19.09.2008
	 
	1.Unit has submitted details of Waste water,  stack height, quantity of BMW generation.
	Inspection to be expedited.
	Inspection was conducted on 18.06.09 and following defeciencies were observed:                       1) Staff of the unit were not aware of BMW management.                                                 2) it was infomed that unit is having batch type of ETP but at the time of inspection, tank was empty.
	

	3
	I.G. Homeo Remedies Pvt. Ltd. 316, FIE Parparganj Industrial Area Delhi-92
	 7.10.08
	 
	1. Submitted details of Waste water,  stack height quantity of BMW generation .        .2.Inspection was conducted on 28.05.09 & following defeciencies were observed:                                          1) ETP was found non operational.                                  2) No record for BMW generation                                    3) No segreagation of  waste was observed
	No action w.r.t. BMW Rules as nature of waste generated by the unit is not covered in any of ten category prescribed under Schedule-I of BMW Rules 1998. 
	No action
	

	4
	M/s Alde Medi Impex Ltd. K-33, Udyog Nagar, Rohtak Road, New Delhi
	Not Applied
	 
	1. Letter returned back with the remarks of postman that the uit has left the address. 
	Inspection to be expedited.
	Inspection was conducted on 19.06.09 &            Unit found Non-operational. It was informed that unit was shifted to Haridwar & M/s SFS Garments found engaged in the premises.
	

	5
	Ambey Laboratories -D-10 DSIDC Industrial Complex Rohtak Road, Delhi-41
	 05.11.08
	 
	 
	Inspection to be expedited.
	Inspection was conducted on 19.06.09 & following were observed  1) Unit found Non-operational however the condition reveal that manufacturing process is being done regularly.                     2) No arrangement for the dispersion of Air Emissions.                                                      3) No ETP was found. Phenyls & washing found lying over the floor.                                 4) The staff were not aware about BMW Rules.
	

	6
	Arora Pharamaceuticals (P) Ltd.,  C-35/13  Lawrnce Road Ind. Area  Delhi-35
	30.01.09
	03.11.08(CTE)
	 
	Inspection to be expedited.
	Inspection was conducted on 25.06.09 & observed  that no industrial activity was going on due construction.
	

	7
	Care and Cure Pharamaceuticals Pvt. Ltd 164, Naharpur Village, Delhi-85
	Not Applied
	 
	1. Called for personal hearing on 02.03.09. Inspection was conducted.The unit was found closed.
	No action as the unit found closed and shigted as per the enquiry from the nearby Property Delaer.
	No action.
	

	8
	M/s Chemo Remedies A-50, G.T. Karnal Road, Idustrial Area, Delhi-110033
	Not Applied
	 
	1) as decided on 29.09.08 this unit was aded in the list of Pvt cases / units. Inspection was conducted w.r.t. M/s Chempo Biological of the same premises and it was found that name of the unit is M/s Chemo Remedies.
	The name of the unit as noted during Inspection is M/s Chemo Remedies. Ask the unit to correct trhe deficiencies observed durng the Inspection
	Lettter issued
	

	9
	Chemo Drugs, A-50, G.T. Karnal Road, Idustrial Area, Delhi-110033
	Not Applied
	 
	1) As decided on 29.08.08, this unit was added in the list of Pvt cases/units..
	Ask the unit to correct the deficiencies observed during the Inspection
	Lettter issued
	

	10
	Cooper Pharmna, B-59, Wazirppur Industrial Area, Delhi-110052
	Applied
	 
	1) As decided on 29.09.08, this unit was added in the list of Pvt cases/units. File of consent shifted from CMC (Orange) to CMC (BMW) .                                  
	Inspection to be expedited.
	Inspection was conducted on 25.06.09 following defeciencies were observed.       1) ETP installed but not functional.           2) No information regarding consent / Authorization                                          3) No agreement with the CBWTF Operators.                                             4) It was informed that unit will be shifed to Dehradun by 15th july, 09, 
	

	11
	Dr. Wadhwa Chemicals Works, F-14/58, Model Town, Delhi
	Not Applied
	 
	1) As decided on 29.09.08 , this unit was aded in the list of Pvt cases/units. Letter return back with the remarks of postman that the unit is closed from long time. Inspection was conducted and the unit was found closed.
	No action as the funit found closed and shifted as per the enquiry from the nearby General Store.
	No action
	

	12
	Dr. Wadhwa Pharmaceuticals , G- 40/2, Lawrene Road ,  New Delhi-35
	04.03.09
	 
	As decided on 29.09.08, this unit was added in the list of Pvt cases/units. 
	Inspection to be expedited.
	Inspection was conducted on 15.06.09 & following defeciencies were observed.    
	

	13
	Gopesh Pharam, H-1455, DSIDC, Narela Indl, Park, Narels, Delhi 110040
	24.09.08. 
	 
	1. As decided on 29.09.08, this unit was aded in the list of Pvt cases /units.                                             2) Reply dated 04.02.09 received regarding rectification of deficiencies noted by SIT. Reply dated 20.02.09 received. Unit came for personal hearing on 02.03.09 and submitted details of waste water, stack height, quantity of BMW genereation. As decided reminder was issued to submit the compliance with affidavit, photographs and documentary proof. 
	Issue final reminder for full compliance call on 25.05.09  
	Final reminder issued
	

	14
	La Grande Pvt. Ltd. G-40/2, Lawrance Road, Delhi-110035
	02.03.09
	 
	As decided on 29.09.08, this unit was added in the list of Pvt cases/units. 
	Inspection to be expedited.
	Inspection was counducted on 15.06.09 & following  defeciencies  were observed:-
1. ETP was Non-operational
2. No channelization in coating section of medicines.
	

	15
	Nav Bharat Impex, C-24, Lawrence Road, Industrial Area,Delhi-35
	Not Applied
	 
	1. As decided on 29.09.08, this unit was aded in the list of Pvt cases/units. 
2. Reply received in response to SCN stating that no BMW is generated in the manufctruing  process of Menthol Crystal and Peepermint Oil in which they are engaged. 
3. Submitted the details of waste water, acoustic enclosure & stack height & BMW quantity.
	Inspection to be expedited.
	Inspection was conducted on 15.06.09 & following defeciencies were observed:
1. The unit is presently sale of its wastes to invoice cum Challan is provided)
2) Stack height was inadequate.
3) Two DG set (s), acoustic found inadequate.
4) Emissions observed inside the crystallization chamber of methanol.
	

	16
	Nice Pharamaceuticals, G-40/1, Lawrence Road, Idustrial Area,delhi-35
	Not Applied
	 
	As decided on 29.09.08, this unit was added in the list of Pvt cases/units. 
	Inspection to be expedited.
	Inspection was conducted on 15.06.09 & following defeciencies were observed: 
1.) ETP was not installed.
2) No agreement with CBWTF operators.
	

	17
	NiceRemedies, A- 61/2,  G.T.K. Road, Industrial Area, Delhi-110033
	09.01.09
	 
	1. As decided on 29.09.08, this unit was added in the list of Pvt cases /units. 
	No action w.r.t. BMW Rules as nature of waste generated by the unit is not covered in any of ten category prescribed under Schedule-I of BMW Rules 1998. 
	No action.
	

	18
	Standford Laboratories Pvt. Ltd. K-30, Udyog Nagar Industrila Area, Phase-I Delhi- 110041
	Not Applied
	 
	As decided on 29.09.08, this unit was added in the list of Pvt cases / Units. Letter return back with the remarks of postman that the unit has left the address.
	Inspection to be expedited.
	Inspection was conducted on 19.06.09 & following were observed:
1) Unit found closed, it is informed that unit is shifted, from the last 14 year & presently Shri Ram Udyog are operating at the premises & found engaged in manufacturing of Valves.
	


Inspection was conducted on 25.06.09 &  following defeciencies were observed: 

1) Phenyl  was found lying in front of the gate.

2) Unprotected Environment for the workers. 

3) Good Manufacturing Practices were not being followed. 

4) As informed Agreement with the Synergy for BMW but record  could not be shown. 

	5) No information regarding Authorization.
	

	20
	Sisla Laboratories J-2050, DSIDC, Indl, Area, Narela Delhi-110040
	Not Applied
	 
	As decided on 29.09.08, this unit was added in the list of pvt cases/units.
	Inspection to be expedited.
	Inspection was conducted on 29.07.08 &  following defeciencies were observed:
1) ETP installed but not functional 
2) DG set without acoustic enclosure however the same was not in operational condition.
	

	21
	Bio-Laboratories, I-2118, DSIDC Narela Indl, Area, Delhi-40
	11.11.08
	 
	As decided on 29.09.08, this unit was added in list of Pvt cases/ units. Reply dated 30.01.09 received wrt reminder notice issued on 24.12.08 stating that they have applied for authorization under BMW Rules.
	Inspection to be expedited.
	Insepction was conducted on 15.06.09 & following defeciencies were observed       1)Although ETP was in operational condition but no treatment was going on 
2) Equalization tank effulents foud in septic conditions.
3) Sludge drying beds outles not connected to equalization tank.
	

	22
	M/s Chemo Biological A-50, G.T. Karnal Road, Industrial Area, Delhi-33
	Not Applied
	 
	As decided on 29.09.08, this unit was added in the list of Pvt cases/units. Reply dated 08.01.09 received stating that they stopped manufacturing activities since 02.11.07. copy of cancellation of Drugs manufacturing. As decided during on 02.03.09. 
	Ask the unit to apply for authorization underBMW Rules.
	Letter issued.
	

	23
	Wang Laboratories International, Office No-2-IInd Floor, Plot No-7 Local Shopping Centre, Karampura, New Delhi C/o M/s Tose International Pvt. Ltd H-1429, 1441, DSIDC Indl, Area Narela, Delhi-40
	Not Applied
	 
	As decided on 29.09.08, this unit was added in the list of Pvt cases/units.
	Re-inspected by Dr. T.K. Joshi's team as the premises was found locked.
	Inspection was conducted on 10.080.09 & premises was found locked. As informed by neighbour (Computer repairing shop owner) the office cum godown of Wang laboratories is opened only once or twice in a month.
	

	24
	Atlanta Pharaceuticals Off. No. I, IInd Floor, Plot No-7, Local Shopping Centre , Karampura, New Delhi-110015. C/o M/s Tose International Pvt Ltd H-1429, 1441 DSIDC Indl Area, Narela, Delhi-40
	Not Applied
	 
	As decided on 29.09.08, this unit was added in the list of Pvt cases /units.
	Re-inspected by Dr. T.K. Joshi's team as the premises was found locked.
	Inspection was conducted on 10.080.09 & premises were found locked. As informed by neighbour (Computer repairing shop owner) the office cum godown of Atlanta Pharmaceuticals is opned only once or twice in a month.
	

	25
	Dr.Wellman's Homeopathic Laboratories Ltd. AM-4 Dilkhush Indl Estate, G.T. Karnal Road Delhi-33
	Not Applied
	03.12.08 (CTE & CTO)
	1. As decided on 29.09.08, this unit was added in the list of pvt cases/units .
	Unit was engaged in the activity of mfg of homeopathy medicines. No action w.r.t. BMW Rules as the waste generated by the unit is not category prescribed under Schedule -I of BMW Rules, 1998.
	Inspection was conducted on 28.05.09 &  it was found that nature of the waste generated in the premises not covered under BMW Rules.
	

	26
	Dr.Wellman's Homeopathic Laboratories Ltd. A-108, Wazirpur Indl. Area, Delhi-52
	Not Applied
	 
	As decided on 29.09.08, this unit was added in the list of Pvt cases/units.
	Inspection to be expedited.
	Inspection was conducted on 19.06.09 &  following defeciencies were observed: 
1) No ETP was found installed.
2) 25 KVA DG set found.
	

	27
	JVS Pharma Co. A-108, Wazirpur Indl.Area Delhi-52
	Not Applied
	 
	1. As decided on 29.09.08, this unit was added in the list of Pvt cases/units.
	Inspection to be expedited.
	Inspection was conducted on 19.06.09 & following defeciencies were observed:
1) ETP was not installed.
2) Height of the stack neet to be increased.
	


1. As decided on 29.09.08, this unit was added in the list of Pvt cases /units.

2. Reply dated 30.01.09 received wrt letter dated 22.12.08 regarding rectification of deficiencies noted by SIT.


Inspection was conducted on 25.06.09 & following defeciencies were observed:

1.) ETP not regulary operated.

	2) No isolated storage provided for waste storage.
	

	29
	Alpine Industries, A-67, Naraina Industrial Area, phase-I, N Delhi-15
	Not Applied
	 
	As decided on 29.09.08, this unit was added in the list of Pvt cases/unit.
	Inspection to be expedited.
	Inspection was conducted on 16.06.09 & Unit found closed. It was informed that the premises is used for residential purpose from the past 13-14 years.
	

	30
	Arbro Pharmaceuticals Limited, 6/14, Kirti Nagar Industrial Area, N Delhi-15
	11.08.08
	 
	1. As decided on 29.09.08, this unit was added in the list of Pvt cases/unit
2) Submitted the CGWA clearance dated 24.02.09, 
3)Submitted details of waste water, stack height, quantity of BMW generation vide letter dtd 04.05.09
	Inspection to be expedited.
	Inspection was conducted on 25.06.09 & following defeciencies were observed: 1) ETP not operated regularly. 
2) Inadequate Stack Height.
	

	31
	Bio Laboratories, 3026/7 Ranjit Nagar, Delhi-08
	11.11.08 
	 
	1. As decided on 29.09.08, this unit was added in the list of Pvt cases/units. 
	Inspection to be expedited.
	Inspection was conducted on 16.06.09 & it was found that premises is used for residential purpose
	

	32
	Grand Chemicals Works. C-212/2, Mayapuri Industrial Area, N Delhi-64
	 01.01.09
	 
	1. As decided on 29.09.08, this unit was added in the list of pvt cases /units.
2. Reply dated 22.11.08 received regarding BMW authorization, submitting the copy of agreement with synergy.
	Inspection to be expedited.
	Inspection was conducted on 26.06.09 & following defeciencies were observed:
1. No ETP was installed.
2. Unit engaged in manufacture of Phenyl  
	

	33
	Indus Pharma Pvt. Ltd. 5/2, Kirti Nagar, Industrial Area, N Delhi-15
	03.02.09
	03.02.09 (CTE)
	1. As decided on 29.09.08, this unit was added in the list of Pvt cases/units. 
2. Submitted details of waste water, stack height, quantity of BMW generation vide letter dtd 08.05.09
	Inspection to be expedited.
	Inspection was conducted on 25.06.09 & following defeciencies were observed:
1. ETP was not operated regularly.
2. No records found regarding Bio-Medical Waste Management.
3. No sharp waste Management.
	

	34
	J.K. Remedies 8/41, Kirti Nagar Industrial Area, N Delhi-15
	17.09.08
	 
	1. As decided on 29.09.08, this unit was added in the list of pvt cases/units.
2. Submitted the CGWA clearance dated 24.02.09.
3. Submitted details of waste water, stack height, quantity of BMW generation vide letter dated 04.05.09.
	Inspection to be expedited.
	Inspection was Conducted on 25.06.09 & following defeciencies were observed:
1.) ETP not operated regularly.
2.) Inadequate Sharp Waste Management.
3.) Unit does not have accoustic enclosure & having inadequate stack height.
	

	35
	New Loyds Surgico, B-15, DSIDC Complex, Industrial Area, Kirti Nagar, N Delhi--15
	Not Applied
	 
	As decided on 29.09.08, this unit was added in the list of Pvt.cases/units.
	Inspection to be expedited.
	Inspection was conducted on 25.06.09 & it was observed that BMW is not generated in the premises
	

	36
	Tribhawan Injectables, 8/39, Kirti Nagar Industrial Area, N Delhi-15
	01.09.08
	 
	1. As decided on 29.09.08, this unit was added in the list of Pvt.cases/units.
2. Noise Monitoring Report submitted.
3. Submitted details of waste water, stack height, quantity of BMW generation vide letter dated 04.05.09..
	Inspection to be expedited.
	Inspection was conducted on 25.06.09 & following defeciencies were observede
1.) ETP was not in operational Condition.
2.) Inadequate Sharp Waste Management.
3.) Records of BMW (Bio-medical Waste) was not Maintained.
	

	37
	Wang Pharmaceuticals & Chemicals, 35-A Goyala Khurd, Near Najafgarh,  Delhi
	Not Applied
	 
	1. As decided on 29.09.08, this unit was added in the list of Pvt cases / units. 
2. Reply dated 22.10.08 received  stating that they are not generating any BMW.
3. Submitted details of waste water, stack height, quantity of BMW generation vide letter dated 01.05.09.
	Inspection to be expedited.
	Inspection was conducted on 26.06.09 & following defeciencies were observed: 
1.) Unit has not applied for Authorization & Consent.
2.) Inadequate Stack Height observed.
3.) Unit claims that it does not generate BMW & recycle in the process.
	

	38
	Hahnemann Pharmaceuticals (P) Ltd. A-7, Narain Industrial Area, Phase-I, New Delhi-28
	Not Applied
	21.10.08 (CTE)
	1. As decided on 29.09.08, this unit was added in the list of Pvt cases / units.
2. Reply dated 21.10.08 received stating that this unit is manufacturing cosmetics, perfumery & homeopathic medicines, and does not generate any BMW. 
3. Exempted for authorization under BMW Rules.
	Inspection to be expedited.
	Inpection was conducted on 10.08.09 & the unit was found closed. Only Admn. Office was open & it is informed by M.D, that Inspection was already carried out by the officials of DPCC.
	

	39
	Narm Pharmaceuticals 9611, Mayapuri Industrial Area, N Delhi-64
	Not Applied
	 
	1. As decided on 29.09.08, this unit  was added in the list of Pvt cases/units.
2. Letter returned back with remarks of postman that the unit has left the address. 
	Inspection to be expedited.
	Inspection was conducted on 25.06.09& No activity was found & unit was shifted to Bihar.
	

	40
	Asclepius Pharmaceuticals Pvt. Ltd. F-34/7, Okhla Area, Phase-II, N Delhi-20
	Not Applied
	 
	1. As decided on 29.09.08, this unit was added in the list of Pvt cases /units. 
2. Submitted details of waste water, stack height, quantity of BMW generation vide letter dated 22.04.09.
	Inspection to be expedited.
	Inspection was conducted on 19.06.09 & Working area found loked. No activity observed during Inspection.
	

	41
	J. Mitra & Co. Ltd. A-180, Okhla Industrial Area, N Delhi-20
	24.06.08
	 
	1. As decided on 29.09.08, this unit was added in the list of Pvt cases/units. 
2. Reply dtd 11.05.09 received regarding correction of deficiencies. Submitted details of waste water, stack heignt, quantity of BMW generation vide letter dtd 24.04.09.
	Inspection to be expedited.
	Inspection was conducted on 24.06.09 & following defeciencies were observed:
1.) ETP not installed.
2.) Discharging Effluent in sewers.
3.) No lablelling on containers as per BMW.
	


1. As decided on 29.09.08, this unit was added in the list of Pvt cases/unit.  

	2.Letter returned back with the comments of postman that not such unit exists.
	Inspection to be expedited.
	Inspection was conducted on 16.06.09 & observed that the factory is being shifted to Noida. A Printing Press was runing in the said premises at the time of inspection.
	

	43
	MANB Health Care, Y-12 Okhla, Industrial Area Phase-II, N Delhi-20
	Not Applied
	 
	1. As decided on 29.09.08, this unit was added in the list of Pvt cases / units. 
	Inspection to be expedited.
	Inspection was conducted on 19.06.09 and it was observed that the unit has been shifted to nearby premises and at this site production will be started by july, 2009.
Not applied for authorization under BMW Rules.
	

	44
	New Life Pharmaceuticals, A-240 Okhla Industrial Area, -I N Delhi-20
	28.11.08
	 
	 1. As decided on 29.09.08, this unit was added in the list of Pvt cases/unit. 
	Inspection to be expedited.
	Inspection was conducted on 24.06.09 & following  defecincies were observed 
1. Unit is having Expired Agreement which was valid till 30.11.09 with Synergy Waste.
2.) Seprate isolated storage area is not provided for proper waste disposal.
	

	45
	Pine Pharma Pvt. Limited, 91/2, Okhla Industrial Area-I, New Delhi-20
	Not Applied
	 
	1. As decided on 29.09.08, this unit was added in the list of Pvt cases / units. 
	Inspection to be expedited.
	Inspection was conducted on 24.06.09 &  following defeciencies were observed
1.) ETP was not installed
2.) No Acoustic enclosures.
3.)Inadequate Stack height,
	

	46
	Radicura Pharmaceuticals Pvt. Ltd. B-117, Okhla Industrial Area-I, N Delhi-20
	19.03.08
	 
	1. As decided on 29.09.08, this unit was added in the list of Pvt cases / units. Reply dated 07.01.09 received informing that CTE had already granted by Central Board. 
	Inspection to be expedited.
	Inspection was conducted on 10.06.09 & following defeciencies were observed.
1.) No Colour Coding was oserved.
2.) Records of BMW were not found.
	

	47
	Ranbaxy Fine Chemicals Ltd.  (Diagnostic Divisions), A-3 Okhla New Delhi-20
	Not Applied
	 
	 
	 
	Inspection was conducted on 10.06.09 & following defeciencies were observed.
1.) Contract with any CBWTF operator has not been found.
2.) Containers for waste disposal were not provided anywhere .
3.)ETP installed but not functional.
	

	48
	Stericat Gustring Pvt. Ltd. E-25/B-I Mohan Co-Op. Indl Area, Mathura Road, New Delhi-44
	Not Applied
	 
	1. Replied w.r.t. SCN issued and stated that they have stopped all manufacturing activities. Reply dtd 27.04.09 received stating that factory were closed & no work is going on at present.
	Inspection to be expedited.
	Inspection was conducted on 18.06.09 & No Industrial activity observed & unit shifted to Manesar.
	

	49
	Surgi Media D-9/1, Ph-I Okhla Indl. Area, N Delhi-20
	Not Applied
	 
	1. As decided on 29.09.08, this unit was added in the list of Pvt cases/units.
	Inspection to be expedited.
	Inspection was conducted on 10.06.09 & Unit has not been generating BMW.
	


1. As decided on 29.09.08, this unit was added in the list of Pvt cases / units.

2. Reply dataed 05.02.09 w.r.t. letter dated 28.1.09 r eceived regarding rectification of correction of deficiencies. Submitted details of waste water, stack height, qauantity of BMW generation vide letter dtd 27.04.09

	3. Reply dtd 4.05.09 received regarding correction of deficiencies alongwith photographs.
	Call on next meeting.
	 
	

	51
	Uttam Air Products Pvt. Ltd. F-90/5, Okhla Industrial Area, N Delhi-20
	Not Applied
	 
	1. As decided on 29.09.08,  this unit was added in the list of Pvt cases / units. 
2. Reply dated 03.01.09 received stating that they are manufacturing of Medical Oxygen for which raw material is only atomspheric air. They are certifying that there is no generation of BMW. 
3. Submitted details of waste water, stack height, quantity of BMW generation vide letter dtd 06.05.09.
	Inspection to be expedited.
	Inspection was conducted on 24.06.09 & following defeciencies were observed:L
1) Inadequate Stack height.
2.) Unit does not generate BMW (Bio-medical Waste)
	

	52
	R.P.L. (India) pharmaceuitcals (P) Ltd. D-8/6, Okhla Industrial Area Phase-I, New Delhi-20
	25.03.08
	 
	1. Reply dated 04.02.09 received w.r.t letter dated 28.01.09 regarding rectification of correction of deficiencies. 
	Inspection to be expedited.
	Inspection was conducted on 10.06.09 & following defeciencies were observed
1.) No record of BMW & HMW found.
2.) No Seprate isolated storage area of Bio-Medical Waste.
3.) No ETP was installed.
	

	53
	H. C. Sen & Company 5A/1, Darya Ganj, Ansari Road, N Delhi-06
	Not Applied
	 
	As decided on 29.09.08, this unit was was added in the list of pvt cases/units.  As decided during meetin on 02.03.09 Inspection could not be conducted.
	Re-inspected by Dr. T.K. Joshi's team as the premises was found locked.
	Inspection was conducted on 05.05.09 & the unit officials refused to carry out Inspection due unvailbility of concerned person.
	

	54
	Medochem Laboratories Pvt. Ltd. 624/4A, Vishwas Nagar, Shahdara Delhi-32
	Not Applied
	 
	1. As decided on 29.09.08, this unit was added in the list of Pvt cases/units.
	No action w.r.t. BMW rules as nature of  waste generated by the unit is not covered in any of the ten category prescribed under Schedule-I of BMW Rules 1998.
	Inspection was conducted on 04.05.09 & following defeciencies were observed:
1.) No agreement with any CBWTF operator observed.
2.) The discharged expired medicine are either burned or disposal through drains after dillution.
3.) No ETP was installed.
4) No records of BMW.
	


1. As decided on 29.09.08, this unit was added in the list of Pvt cases/units. 


Inspection was conducted on 19.06.09 & following defencies were observed.

1.) Non Complaince with respect to BMW & HMW Rules 

	2) Inadequate Stack Height.
	

	56
	U.K. Pharama 4/2611, Bihari Colony Delhi-32
	Not Applied
	 
	1. As decided on 29.09.08 , this unit was added in the list of Pvt cases/units.
	No action w.r.t. BMW Rules as nature of waste generated by the unit is not covered in any of ten category prescribed under Schedule-I of BMW Rules 1998. 
	Inspection was conducted on 19.06.09 & following defeciencies were observed
1.) Non-Complaince with respect to BMW & HMW Rules, 
2.) As informed no manufacturing process is done due to cancellation of license & production will starts at Loni after Six Months
	

	57
	Frontier Chemical Works A-6/3, Jhilmil Indl,. Area, Delhi
	Not Applied
	 
	1. As decided on 29.09.08, this unit was added in the list of Pvt cases/units. 
	No action as the unit was found closed during the Inspection
	Inspection was conducted on 28.05.09 &  unit was found closed another unit named as M/s S. S. Gas was found operational at the same address.
	

	58
	Logotech India Pvt. Ltd. 403, Patparganj Indl Area, Patparganj N Delhi
	Not Applied
	 
	1. As decided on 29.09.08, this unit was added in the list Pvt cases/units. 
2. Reply dt. 22.11.08 received regarding BMW authorization & submitted the copy of agreement  with synergy.
	Ask the unit to correct the deficiencies observed during the Inspection
	Letter issued
	

	59
	Aspen Laboratories Pvt. Ltd. B-82, G.T. Karnal Road, Indl. Area, Delhi-33
	Applied for renewal 
	 
	During the inspection of M/s Jagat Diagnostic Pvt. Ltd. B-82, G.T.K. Road Industrial Area, Delhi-33 on 20.08.08, In the same premises another unit M/s Aspen Laboratories Pvt. Ltd. was also found operating which Imports drug/Testing kits used for HIV etc. and generates Bio-medical Waste & having agreement with one of the Common Operators for BMW Treatment & disposal. Deficiencies observed w.r.t. complaince of BMW Rules. Applied for  authorization under the BMW Rules to DPCC. M/s Aspen Laboratories Pvt. Ltd. which was found operating in the same premises and agreement Bio-Medical waste for applying for CTE & for correction of the deficiencies observed during the inspection on 20.08.08. Reply received stating that they have been granted CTE & CTR. Reply received dt. 1.12.08 stating that correction of deficiencies have been done reply dated 13.01.09 received submitting correction of deficiencies observed during  inspection, Reply dated 25.02.09 received regarding the rectification of deficiencies. letter dated 25.05.09 received regarding request for renewal of A 
	No action
	No Action
	

	60
	Polychem formulation 6/1 WHS Kirti Nagar N Delhi-15
	Not Applied
	 
	Letter returned back with the remarks of postman that unit has left the address. 
	inspection to be expedited.
	Inspection was conducted on 25.06.09 & Unit does not exist & shifted to some other location. Presently premises used as furniture showroom.
	

	61
	Vital Drug Pvt. Ltd. B-56 Khasra No-665, Nawada Uttam Nagar, N Delhi-59
	Not Applied
	 
	Letter returned back with the remarks of postman that unit has left the address. 
	inspection to be expedited.
	Inspection was conducted on 26.06.09 & followin defeciencies were observed Unit was found closed.
	

	62
	Kapoor Medical Gases, Plot no-281, Mundka Village Rohtak Road, Delhi-41
	Not Applied
	 
	1. Name of this unit was obtained from drug control deptt.
2. Reply has been received stating that they are not engaged in any manufacturing activity. They are doing bottling of medical gas cylinder and hence no waste is generated of any kind. 
	inspection to be expedited.
	Inspection was conducted on 19.06.09 & following defeciencies were observed Exact location of the unit could not be located. Local enquiry reveals that one such unit used to exist but were closed down since last one year.
	


1. Reply received informing that they are licenced to manufacture adhesive plaster strips under drugs asnd cosmetic act and during its production and testing no BMW generated and hence BMW rules are not applicable. 

	2. Submitted details of waste water, stack height, quantity of BMW generation vide letter dtd 04.05.09
	No action as no industrial activity was observed during inspection
	No Action
	

	64
	Sharp Menthol India Ltd. C-15 SMA Cooperative Indl Estate Delhi-33
	Not Applied
	 
	1. Reply received stating that they are manufacturing 100% natural menthol and not generating any BMW hence BMW rules are not applicable. 
	inspection to be expedited.
	Inspection was conducted on 28.06.09 & following defeciencies were observed
1.) ETP yet to be installed
2.) Approx I tonn of residual waste was Lying in the gallary.
3.) Stack height was below the up roof level.
	

	65
	I.J.Pharmaceuticals Pvt. Ltd.I-2091, Indl. Area, Narela Delhi-40
	Not Applied
	 
	1. Submitted the details of waste water, acoustic enclosure & stack height & BMW quantity.
	inspection to be expedited.
	Inspection was conducted on 29.07.09 it is observed that unit is no-operatioinal at time of inspection unit stated that all ingredients produce area consumed in the process
	

	66
	TOSC International Pvt Ltd. (Pharmaceuticals division), H-1429, 1441, DSIDC Indl Area Narela Delhi-40
	Not Applied
	 
	1.Reply received informing that it is a very small unit manufacturing a few medicienes of ORAL liquid preparation and hence no BMW generated in the factory.                     2. submitted the details of waste water, acoustic  enclosure & stack height & BMW quantity.
	Call on in next meeting.s
	 
	

	67
	Sharp Menthol India Ltd. C-3 SMA cooprative Indl. Estate Delhi-33
	Not Applied
	 
	1. Reply received staing that they are manufacturing 100% natural menthol and not generating any BMW hence BMW rules are not applicable. 
	inspection to be expedited.
	Inspection was conducted on 28.06.09 following defeiencies were observed
1.) ETP yet to be installed.
2.) Approx I tonn of residual waste was lying in the gallary
3.) stack height was below the up roof level.,
	

	68
	Ralson Remedies Pvt. Ltd. J-38, Udyog Nagar Rohtak Road Delhi-41
	Not Applied
	 
	1. Reply received stating that they are not using any hazardous chemicals they use only natural herbs, alcohols and hence no BMW is generated and asking for guidance regarding BMW. 
2. Submitted the details of waste water acoustic enclosure & stack height & BMW quantity.
	inspection to be expedited.
	Inspection was conducted 19.06.09 & following defeciencies were observed
1.) No ETP was found installed.
2.) Stack height the height of main building.
	


Inspection was conducted on 16.06.09 & followoing defeciencies were observed

1.) No ETP was found

2.) No information regarding agreement with CBWTF operator & application with respect to Consent / Authorization

	3.) No Acoustic arrangement & Inadequate stack height.
	

	70
	Mayur Air Products (P) Ltd. B-49, Okhla  Indl Area, Ph-I ND-20
	Not Applied
	 
	1. Reply received stating that they are manufacturing only Medical Oxygen/Industrial Oxygen & there is no BMW generated in the process as it is done from atmosphere air. 
2. Submitted details of Waste water,  stack height & quantity of BMW generation vide letter dtd 13.05.09
	inspection to be expedited.
	Inspection was conducted on 10.06.09 & following defeciencies were observed
1.) CTE were expired dated 16.04.09.
2.) No BMW( Bio-Medical) was generating in the process.
	

	71
	Vaibhav Oxygen A-38, B-I Extn,  Mohan co-operative Indl. Estate Badarpur N Delhi-44
	Not Applied
	 
	1. Reply received stating that it is a oxygen gas filling unit and does not produces any waste execpt oxygen . 
2. Submitted details  of waste water, stack height, quantity of BMW generation vde letter dtd 23.04.09.
	inspection to be expedited.
	Inspection was conducted on 18.06.09 following defeciencies.
1. unit having Acoustic enclosure.
2. Inadequate Stack height
3. BMW not generated
	

	72
	Bindlysh Biotec Ltd, A-45 Jhilmil Indl Area Delhi-95
	Not Applied
	 
	1. Reply received stating that the unit is not producing or testing any biological and as such unit do not generate any BMW.
2. It is oxygen gas filling unit and does not require any waste treatment facility and BMW rules are not applicable.
Reply dated 22.01.09 received 
	Ask the unit to correct the deficiencies observed during the inspection
	Letter issued
	

	73
	Bio Nova Pharmaceuticals Pvt. Ltd., C- 66/1 Okhla Indl. Area, Phase-I, N Delhi-20
	Not Applied
	 
	1. Reply received dated 09.04.08, stating that they will apply for authorization.. 
	inspection to be expedited.
	Inspection was conducted on 10.06.09 no such unit found at given location.
	

	74
	Aggarwal Pharmaceuticals, B-2644 DSIDC Narela Indl Area, Delhi-40
	22.01.09
	 
	Reply dated 10.03.08 received stating that they will apply for authorization within three months.
	Ask the unit to correct the deficiencies observed during the inspection
	Letter issued
	

	75
	Unipex Pharmaceuticals Pvt Ltd. D-1651 DSIDC Narela Indl. Area, Delhi-40
	Not Applied
	 
	Inspection was conducted.
	Ask the unit to correct the deficiencies observed during the inspection
	Letter issued
	


1. Reply dated 15.04.08 received stating that they will apply for authorization within three months. 

	2. Submitted the details of waste water, acoustic enclosure & stack height & BMW quantity.                                                                                                                                                                     3. Inspection was conducted.
	Ask the unit to correct the deficiencies observed during the inspection
	Letter issued
	

	77
	Wellbeck Pharmaceutical Pvt Ltd F-24 Phase Okhla Indl Area ND
	Not Applied
	 
	1. Reply dated 10.03.08 received stating that they will apply for authorization within three month.                                             2. Letter returned back with the comments of postman that no such unit exists on this address.
	 Inspection to be expedited
	Inspection was conducted on 10.06.09 & premises was found empty as the company were shifted from there.
	

	78
	Remedies Pharmaceutical India Ltd, 34, Phase-II Badli Industrial Area, Delhi-42
	 
	 
	 
	inspection to be expedited.
	Inspection was conduted.
	

	79
	Ranbaxy Labroatories Ltd. (EVT) E-47/9, Okhla Indl Area Phase-II, New Delhi-20
	 
	 
	Reply  dated 03.02.08 received  stating that they will apply for authorization within time limit
2.Reply dated 02.06.08 submitted that they are not generating any BMW and hence not required to apply for authorization under BMW rules. Case was taken up by BMW Committee No-1, as per decision taken by CMC (orange) in its meeting.  
	inspection to be expedited.
	Inspection was conducted on 18.06.09 & following defeciencies were observed
1. Contract with any CBWTF operator has not been found.
2. Container for waste disposal were not provided anywhere.
3. ETP installed but not functional.
	

	80
	Analytical Services Ltd E-47/9, Okhla Indl Area, Phase-II, New Delhi
	 
	 
	Case was taken up by BMW Committee No-1, as per decision taken by CMC (orange) in its meeting. 
	inspection to be expedited.
	Inspection was conducted on 18.06.09 & following defeciencies were observed 
1. No isolated storage for Bio-medicalWaste
2. bio-hazard Symbol on containers  not provided.
	


1. Unit is engaged in R & D of Vaccines. CTO applied on 22.02.06.

2. Inspected by the officials of PGRC on 27.04.07 & was placed before CMC (Orange) in its meeting on 09.10.07

3. unit is having a DG set of 380 KVA and also have a oil fired Boile. It was decided that the unit shall apply for CTE and submit a Bank Guarantee of Rs. 50,000. unit applied for CTE on 227.11.07 and submitted bank Gurantee of Rs. 50,000 valid upto 21.11.08

4. unit submitted test report for the waste water genereted from the unit showing that the parameters are within the limit.

5. Stack monitoring report for the Oil fired Bolier was not submitted 

6. Activities / processes of the unit are covered under HW (M&H) rules. Inspection was done on 31.03.08 & deficiencies were observed

	7. letters issued Replies stating that installation work for ETP initiated & submitted NMR. it was decided to call on 27.04.09 with full compalince of eariler decision. Letter issued
	Call on in next meeting.
	 
	


1. this is a case of manufacturing of Vaccines CTO applied on 20.01.06. the unot has submitted two set of application form for consent (renewal) dated 12.07.06 & 20.01.06 and contradictory statemtents were made in the applications.

2. The unot was inspected by the officials of PGRC on 25.09.07 & was placed before CMC (Orange) in its meeting held on 09.10.07.

3. The team inspected the unit on 06.11.07 & it isas observed that unit had not applied for authorization under BMW Rules though having agrreeement with M/s Syndergy Waste Managment Pvt. Ltd., 

4. Applied for the Authorization on 13.11.07.5. as per Hazardous Waste (M & H) Rules, 1989, as are covered under the said rules.

5. Inspection done on 31.03.08 & defiencies were observed.

6. Letters were issued as decided by the Committee and reply received.

	7. Reply dated 10.02.09 received stating that installation work for ETP initiated and submitted BMR it was decicded to call on 27.04.09 with full complaince of earlier decision letter issued.
	Call on in next meeting.
	 
	


1. Unit is engaged in mfg. of pharmaceuticals. 

2. It was inspecte be PGRC (Orange) in meeting on 09.10.07.

3. Unit is having 2 DG Set of  380 KVA & 725 KVA with acoustic enclosure and LPG Bhatti.

4. unit Submitted test report for the waste water generated.

5. Inspection done on 06.11.07 it was found that unit had not applied for the authorization under BMW Rules. valid agreement.

6. Activities / processes of the unit are covered under the HW Rules. The unit was inspected by the team on 03.03.08 Waste water is generated for which no ETP / Equalization tank provided.

7. Other Unit M/s Pancea Bio- Pharmaceuticals Research at First Floor a R & D Laboratory is also operating which has not applied for authorization under BMW rules.

8. Letter for deficiencies were issued & reply recieved. Reply received informing installation of ETP and will be operate in first week of March, 2009 NMR and information regarding apply for approval of cleareance of CGWA.

	9. It was decided to call on 27.04.09, with full complaince of earlier decision. Letter issued
	 
	 
	


ANNEXURE 4

Decisions taken by the BMW Committee No.1 ,in the Meeting Held 04.09.2009, w.r.t. Agenda No.5- Regarding proposals received from Dr. T.K.Joshi on (i)  Study on the Lead (ii)Study on the  Effect of  Mercury Waste
 (i) Action Taken Report w.r.t Study on the Lead
      Earlier in meeting on 08.02.08, It was decided that a study has to be done of the      quantum of lead used in Delhi and is likely adverse impact on the citizen of Delhi. Such      study will reveal the appropriate strategy for handling and containing the   effect of lead on      the health of the city.  Based on study further necessary action   will be taken. Information      sought by Dr.T.K.Joshi was sent.

   
(ii) Action Taken Report w.r.t Study on the Effect of Mercury Waste 

      In the meeting on 08.02.08 , it was decided that a formal study on  the effect of Mercury       Waste on  the citizens of Delhi will be done since as informed by Dr.T.K.Joshi,  no such      study in Delhi has been carried out earlier. Dr. T.K. Joshi will submit a proposal. The      proposal will also look at the appropriate technologies for disposal of Mercury waste in the          city.Information sought by Dr  T.K.Joshi  was  sent .

      Decision Taken in the Meeting of BMW Committee No. 1, on 06.05.08 

Dr. T.K. Joshi to submit the proposals for both the studies (i) Study on the lead & (ii)  Study onthe Effect of Mercury Waste , within the month of May, 2008.

     Action Taken : Letters issued to Dr. T.K. Joshi for the proposal for both the studies (i)       Study on the lead &  (ii) Study on the Effect of Mercury Waste.                               

     Separate  proposals for  both the studies, received from Dr. T.K.Joshi , were placed         before the Committee 

     Decision Taken in the Meeting of BMW Committee No. 1, on 13.06.08

     Both the proposals  received from Dr. T.K.Joshi  may be examined by Dr. Chetna Harjai,      Scientist , Deptt.of  Environment and put up  by 14.07.2008.

    Action  Taken  w.r.t decision taken  on 13.06.08
     Copy of both the Proposals were given to Dr. Chetna Harjai in the meeting on 13.06.08.      Her  comments are awaited. 

    Decision Taken in the Meeting of BMW Committee No. 1, on 14.07.08

    Put up on file for administrative decision. 
    
    Action  Taken  w.r.t decision taken  on 14.07.08
    Concerned  files  after getting the proposals for both the studies were  submitted  however     not returned back then. 

    Decision Taken in the Meeting of BMW Committee No. 1, on 27.08.08

    Both files to be procured & submitted administratively within a week.

    
  Action  Taken  w.r.t decision taken  on  27.08.08 :

  Regarding (i) above as decided earlier by the Committee the proposal on Lead was    examined   by Dr. Chetna of Deptt.of Env. & Submitted to Chairman, DPCC. It is learnt from   Ms Kamna   that the said matter/ file was marked to her & as directed by Chairman she has    to speak to   Chairman, DPCC on the said matter. 

  Regarding (ii) Above, Proposal received from Dr. T.K.Joshi for Study on the   effect of    Mercury waste, Finance Deptt. of Govt. of NCT Delhi has given its concurrence . 

 
Decisions Taken in the Meeting of BMW Committee No. 1, on 29.09.08 : 
      

 (i) Since Finance Deptt. of  Govt. of NCT Delhi has given its concurrence on the Proposal        received from Dr. T.K.Joshi for Study on the   effect of  Mercury waste, further action is        to be taken by Dr.T.K.Joshi. 

 (ii) Regarding the proposal received from Dr.T.K.Joshi  on the study on Lead the matter to        be decided administratively on  file. 

 Action  Taken  w.r.t decision taken  on  29.09.08 :

Regarding (i) above, a letter has been received from Dr.T.K.Joshi requesting for the release of payment to start the work.

Regarding (ii) above as decided on file by Chairman, DPCC, a letter has been issued to Dr..T.K.Joshi seeking his response on the points raised by the Deptt of Environment, GNCT Delhi on the proposal received from Dr.T.K.Joshi.

Decision Taken by BMW Committee No. 1 in the Meeting Held on 30.10.2008:
Action will be taken administratively.

 Action  Taken  w.r.t decision taken  on  30.10.08 :

Regarding (i) above, as decided the matter has been put on file for administrative decision for the release of payment to start the work for Study on the   effect of    Mercury waste.

Regarding (ii) above as decided on file by Chairman, DPCC, a letter was  issued to Dr..T.K.Joshi seeking his response on the points raised by the Deptt of Environment, GNCT Delhi on the proposal received from Dr.T.K.Joshi on the study on lead. Response waited.

Decision Taken by BMW Committee No. 1 in the Meeting Held on 28.11.2008:
               File be submitted administratively.

 Action  Taken  w.r.t decision taken  on  28.11.08 :

               File submitted administratively.

Decision Taken by BMW Committee No. 1 in the Meeting Held on 29.12.2008:
File to be submitted administratively.  

Action  Taken  w.r.t decision taken  on  29.12.08 :

File submitted administratively. 


 
Decision Taken by BMW Committee No. 1 in the Meeting Held on  29.1.2009:

File to be submitted administratively.  

 Action  Taken  w.r.t decision taken  on  29.01.09 :

File submitted administratively. 

Decision Taken by BMW Committee No. 1 in the Meeting Held on 02.03.2009

 File to be submitted administratively.
 Action  Taken  w.r.t decision taken  on  02.03.09 :

File submitted administratively. 

Decision Taken by BMW Committee No. 1 in the meeting held on 27.04.2009

             File to be submitted administratively.
               Action  Taken  w.r.t decision taken  on  27.04.09 :

File was submitted administratively. Work awarded for “ Exploratory study of Mercury exposure in  Delhi”  and  Rs 7.25 Lakh has been released to  COEH in this regard.

Regarding proposal for study on Lead, Terms of Reference has been prepared and has been sent to Dr.T.K.Joshi of COEH.
             Decision Taken by BMW Committee No. 1 in the meeting held on 01.06.2009



Regarding study on Lead, wait for the response of COEH.
              Action  Taken  w.r.t decision taken  on  01.06.2009 :

Point wise reply  dated   18.07.09   has been received from Dr. T.K.Joshi,  requesting  additional amount of Rs. 22 Lakh towards purchase of lead monitoring equipments  .                                              

             Decision Taken by BMW Committee No. 1 in the meeting held on 04.09.2009



Dr. T.K.Joshi will consult  DPCC lab regarding lead monitoring equipment and  put up               administratively after getting the response from Dr.T.K.Joshi.
           (Dharmentra )          (Dr. A. K. Ambasht)            ( Dr.T.K.Joshi)             ( Dr. Chander Prakash ) 

         Chairman,DPCC              M.S.,DPCC                  COEH, MAMC                        SEE (BMW ) 

             (Dr. Chetna Harjai)                    ( D.K.Singh )           (D.K.Srivastava )         ( M.I.Siddiqui)        Scientist, Env.Deptt, GNCTD               EE ( BMW)              AEE ( BMW)                 AEE ( BMW) 

Annexure 5

Decisions taken by the BMW Committee No.1, in the Meeting Held 04.09.09, w.r.t. Agenda No. 6:  Minutes of the Meeting of Advisory Committee on BMW Held on 31.10.2008

A meeting of the Advisory Committee on Bio Medical Waste Management held on 31st October 2008 at 3.00 PM at the chamber of Principal Secretary (Health & Family Welfare) at 9th Level, Delhi Secretariat New Delhi-02. Minutes of the  said meeting have been received and copy is enclosed 

Following decisions were taken wherein DPCC has to take action besides action by other Agencies:

1. DPCC will conduct regular inspections and the report will be placed before the Committee.

2. Delhi Medical Association will be involved in the training programmes of Nodal Officer of Govt. and Private Hospitals. ( Action  DHS,COEH,DPCC and DMA)

3. The information in the form of Frequently Asked Questions on biomedical waste management will be displayed on website (Action DMA, DHS, DPCC).

4. DPCC has taken a decision to get ETPs installed in 79 hospitals having more the 100 beds ( Action  DPCC, concerned Hospitals).

5. Emission testing of all 17 inclinators presently functional (including two CBWTFs) will be conducted by DPCC and the report will be presented in the next meeting.

6. Sensitization of Delhi Police for Bio Medical Waste (Management and Handling ) Rules, 1998, will be done by DPCC

The next meeting of the said Advisory Committee will be held in January 2009.

The said matter was put in file and as decided by the Member Secretary, DPCC, the matter is placed before the Committee for its perusal.

Decision taken by the BMW Committee No1 in the Meeting Held on 28.11.2008          

File be submitted administratively.

Action Taken  w.r.t decision taken in the  meeting  on 28.11.08:

                                      File submitted administratively.
Decisions Taken by BMW Committee No. 1 in the Meeting Held on  29.12.2008:                        File to be  submitted administratively.
Action Taken  w.r.t decision taken in the  meeting  on 29.12.08:
                                          File submitted administratively.
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Decisions Taken by BMW Committee No. 1 in the Meeting Held on  29.1.2009:

                                          File to be  submitted administratively.

Action Taken  w.r.t decision taken in the  meeting  on 29.01.09:
                                        File submitted administratively.

Decisions Taken by BMW Committee No. 1 in the Meeting Held on  02.03.2009:

Regarding above mentioned decisions  taken by the advisory Committee 

w.r.t    Point No 1, 2, 3 & 6  -- No   action at present .      

           Point No  4  --  Likely date of completion of the ETP in the hospitals will be                                    submitted in next meeting on 27.04.09.


Point No. 5  --   Incinerators monitored.

Action Taken  w.r.t decision taken in the  meeting  on 02.03.09.

                                      Concerned file submitted.

Decisions Taken by BMW Committee No. 1 in the Meeting Held on  27.04.2009:

                                      Call on 25.05.2009.

Action Taken  w.r.t decision taken in the  meeting  on 27.04.09.

                                      Concerned file submitted and as approved letter issued to Commissioner of Police for BMW Rules. 

Decisions Taken by BMW Committee No. 1 in the Meeting Held on  01.06.2009:
                                      Call on in next meeting.

 Action Taken  w.r.t decision taken in the  meeting  on  01.06.09.

         A meeting of the  Advisory Committee was  held on 26.08.2009  however minutes are          awaited.

Decisions Taken by BMW Committee No. 1 in the Meeting Held on  04.09.2009:
Wait  for the minutes of the meeting of the Advisory Committee held on 26.08.2009.
                 

     (Dharmentra )      (Dr. A. K. Ambasht)           ( Dr.T.K.Joshi)             ( Dr. Chander Prakash ) 

   Chairman,DPCC         M.S.,DPCC                  COEH, MAMC                    SEE (BMW ) 

       (Dr. Chetna Harjai)               ( D.K.Singh )      (D.K.Srivastava )         ( M.I.Siddiqui)       

Scientist, Env.Deptt, GNCTD     EE ( BMW)            AEE ( BMW)               AEE ( BMW) 

Annexure 6

Decisions taken by the BMW Committee No.1, in the Meeting Held on 04th & 8th September 2009, w.r.t.  Agenda No. 7 : Monitoring of  Incinerators for Bio Medical Waste, in Delhi

W.R.T. the High Court Case W.P.(C) No. 6377 of 2004, in the matter of “Court on its Own Motion Vs Delhi Pollution Control Committee.” Regarding Hospital Incinerators in Delhi, Chairman ,DPCC had directed that  team of Dr.T.K.Joshi (for the inspection related to Health Care Establishments and Bio-Medical Waste) will carry out the monitoring of the Hospitals and Two Common Bio- Medical Waste Treatment Facilities (CBWTF) in Delhi to know the present status of the Rules, 1998, as amended to the date, within a month and submit the report to the Member Secretary, DPCC.

       Decisions Taken by BMW Committee No. 1 in the Meeting Held on  29.12.2008:
                     Inspections to be expedited.

Action Taken Report w.r.t Decision taken on 29.12.2008
Inspection of 10 units having incinerators were conducted . Monitoring were conducted in case of 9 units since  incinerator of one unit ( Rao Tula Ram Hospital , Jafferpur, Delhi ) was not operational for last five months. Letters issued in case of 4 units as decided by the Committee in the meeting on 29.12.08. Hon’ble High Court has directed to complete the inspection /monitoring work of these incinerators within 4 weeks and  submit the report within 6 weeks . Next date of hearing in the matter is on 25.02.08. The work of inspection/monitoring is going on. 

The Committee was apprised about the observations made by the Team of Dr.T.K.Joshi and also about the monitoring results for the incinerators monitored by DPCC Laboratory.
      
      Decisions Taken by BMW Committee No. 1 in the Meeting Held on 29.1.2009:

      Decisions taken in respect of the inspected /monitored units are given at Annexure 1 & 2.  In rest       of the cases inspections to be expedited.

Action Taken Report w.r.t Decision taken on 29.01.2009:

DO Letters/ Letters issued as decided in meeting on 29.01.09.

Two more Incinerators at (i.) Palika Maternity Hospital, Lodhi Colony New Delhi (has started operation of Incinerator in December 08. Earlier Incinerator was not operational) and at National Institute of Immunology, Aruna Asaf Ali Marg New Delhi (informed during the hearing on 29.01.09 that the Institute has operational Incinerator) were added in the list of 17 Incinerators. Therefore inspection of remaining 9  units having Incinerators was carried out by team of Dr.T. K. Joshi and Monitoring of Incinerators were also carried out by DPCC Laboratory during the inspection. Incinerator at Lok Nayak Hospital could not be carried out due to lack of Monitoring facility. Earlier Monitoring of Incinerator at Rao Tula Ram Memorial Hospital, Jaffer pur, could not be carried out since Incinerator found not operational (not operational for more than five

Contd. 2….

--2—

months). Thus 19 units (15 Hospitals, 2 Research Institutes and 2 CBWTF) were inspected and Monitoring was carried out in case of 17 units. Venturi Scrubber (Air Pollution Control Device) at Lok Nayak Hospital was not found in operation though Incinerator was in operation. During earlier inspection on 23.06.08, Venturi Scrubber was not found  operational/ found out of order.

Report of the team of Dr. T.K.Joshi on the Monitoring of Incinerators for Bio Medical Waste, in Delhi, along with summarized statement on Monitoring of Incinerators (for Bio Medical Waste) in Delhi, conducted by Laboratory of DPCC, in December 2008 to February 2009 was placed before the Committee. 

DPCC has issued DO letters/ letters in case of 10 Units, please refer S.No. 1, 3, 4, 5, 10, 11, 13, 14, 16 and 17 of the list enclosed with the report, for rectification of deficiencies, as decided by the Committee in its meeting held on 29.12.08 and 29.01.09. Reminder letters were issued in case of 3 Hospitals (Ram Manohar Lohia Hospital, Lady Hardinge Hospital, AIIMS) as decided on 29.01.09. 

Ram Manohar Lohia Hospital and M/s Synergy Waste Management Pvt. Ltd. Have responded to the letters issued. In rest of the 8 cases (out of 10 cases in which letters have been issued) response is awaited.

In rest of the 9 cases S. No. 2, 6, 7, 8, 9, 12, 15, 18 and 19 of the list enclosed with the report, decisions are to be taken by the Committee.

As per the report of Dr. T. K. Joshi.

1.The Hospitals (i) Maharishi Valmiki Infectious Diseases Hospital (MVID Hospital),    Kingsway Camp, Delhi(of MCD) (ii) Rajan Babu Institute for Pulmonary Medicine &    Tuberculosis (RBTB Hospital), Kingsway Camp Delhi (of MCD) (iii) Charak Palika    Hospital, Moti Bagh New Delhi (of NDMC) (iv) Palika Matermity Hospital Lodhi    Colony New Delhi (of NDMC) (v) International Centre for Genetic Engineering & Bio    Technology, Aruna Asaf Ali Marg, Delhi(vi) National Institute of Immunology, Aruna    Asaf Ali Marg, New Delhi  (vii) Rao Tula Ram Memorial Hospital, Jaffer Pur Delhi ,    may be asked to close down/ not to operate the Incinerators.


Letter already issued in case of Rao Tula Ram Memorial Hospital for not to Operate     the Hospital as decided on 29.01.09.

2. For temperature, each Incinerator should have Graphic or Computer Recording Devices    for automatically recording of dates, time of operation/ day along with temperatures in    primary and secondary chambers. 

   Programmable Logic Control (PLC) based control system is preferred for Incinerator    operation and for continuously monitoring and automatically recording the dates, time of 
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   day, batch sequential number and operating parameters such as temperatures in both the    chambers.

3. Properly Trained/ Qualified personnel for the operation and maintenance of the      individual Incinerators are required which is lacking at present.

4. Proper record keeping for the Bio Medical Waste found lacking at most of the Units            inspected by the team.

5. Since, the Venture Scrubber (Air Pollution Control Device) installed with the Incinerator     of Lok Nayak Hospital, is not in use/ not operating, the Hospital may be directed to not     to operate the Incinerator without the operation of Venturi Scrubber and prior permission     of Delhi Pollution Control Committee shall be taken in this regard. In the non operation    period of the Incinerator, Incinerable Waste from the Hospital may be disposed through    Common Bio Medical Waste Treatment Facilities (CBWTF) in Delhi or may be    Incinerated at the other Incinerators of the Hospitals of Delhi Govt. 

6. As per the Analysis Report for the monitoring conducted by the Laboratory of DPCC for     the Incinerators; 

(i)  Particulate Matter  concentration in the Stack Emissions is not meeting the prescribed standard of 150 mg/ Nm3 in case of following: (a) AIIMS (b) Guru Tegh Bahadur Hospital (c) Lady Hardinge Medical College & Associated Hospital (d) Lal Bahadur Shastri Hospital (e) Swami Dayanand Hospital (f) National Institute of Immunology 

(ii) Combustion Efficiency is not within the prescribed standards in case of Guru Tegh Bahadur Hospital

(iii) Volatile Organic Compounds in Ash (in %) not found within the prescribed standards in all the 17 Incinerators monitored by DPCC.

(iv) Temperature in Primary Chamber not found within the prescribed standards  (within the prescribed range) in 14  Nos. of cases ( S.No. 1, 2, 3, 4, 5, 6, 7, 9, 10, 12, 13, , 14, 18, 19) 

(v) Temperature in Secondary Chamber not found within the prescribed standards (within the prescribed range) in 8 Nos. of cases (S.No. 1, 3, 4, 10, 12, 15,18, 19) 

7. In the absence of any secured landfill in Delhi, the ash generated from the Incinerators is     being disposed / dumped on the  existing  Municipal Landfills in Delhi.  

8. Deficiencies observed are mentioned in the inspection reports of the team and the same     may be communicated to the Hospital/ unit for rectification of the deficiencies.

9. Each Hospital should have a dedicated Cell for the proper management of Bio Medical     Waste and a Nodal Officer for the same to co ordinate the various activities related with    the cell and also for imparting proper training / for creating awareness among the staff of    the Hospitals.
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10. Stack emission monitoring from the empanelled Laboratories of DPCC should be      conducted quarterly by the Hospitals / CBWTF having Incinerators and monitoring         reports should be submitted to DPCC.

      Report of the Team of Dr. T.K.Joshi , may be perused for other observations made by      the team for taking the decisions. 

Affidavit has been filed by DPCC. Hon’ble High Court on 25.02.09during the hearing in the matter has directed to file the status after the action in remaining cases. Next date of hearing in the said case is on 24.03.2009.

Decisions Taken by BMW Committee No. 1 in the Meeting Held on 02.03.2009:
The Committee was apprised about the observations made by the Team of Dr. T.K. Joshi, and also about the monitoring results for the incinerators monitored by DPCC Laboratory.

Affidavit has been filed in the Hon’ble High Court of Delhi that action is proposed as per BMW Rules against remaining 9 cases for the deficiencies. Committee deliberated and it was decided that deficiencies observed during the inspection/ monitoring and mentioned in the report of Dr. T. K. Joshi to be communicated to the units for the rectification of the deficiencies. 

For MCD Hospitals at (i) Maharishi Valmiki Infectious Diseases Hospital (MVID Hospital) (ii) Rajan Babu Institute for Pulmonary Medicine & Tuberculosis (RBTB Hospital), Member Secretary, DPCC to talk to Medical Superintendent of the Hospitals to outsource the small quantity of the incinerable Bio-Medical Waste instead of burning the waste at their incinerators. 

Decisions taken in respect of the inspected/ monitored units are given at Annexure 1 & 2.
Action Taken Report w.r.t Decision taken on 02.03.2009:

Letters issued in individuals cases of hospitals having Incinerators, as decided by the Committee. Hon’ble High Court, in its last order dated 24.03.09, has directed to file further status report on or before the next date of hearing i.e. on 21.05.09.
Decisions Taken by BMW Committee No. 1 in the Meeting Held on 27.04.2009

Decisions taken in respect of the inspected/ monitored units are given at Annexure 1 & 2.
Action Taken Report w.r.t Decision taken on 27.04.2009:

D.O. letters issued in individuals cases of hospitals / Research Institutes having Incinerators, as decided by the Committee. Affidavit submitted along with updated status of 19 incinerators in the  Hon’ble High Court. Next date of hearing in the matter is on 06.08.09.
Decisions Taken by BMW Committee No. 1 in the Meeting Held on  01.06.2009:
                                      Call on in next meeting.

Action Taken Report w.r.t Decision taken on  01.06.2009:

D.O. letters /Letters issued in individuals cases of hospitals / Research Institutes having Incinerators, as decided by the Committee.   As decided by the Committee , one more incinerator at NDMC  Veterinary Hospital, Moti Bagh, New Delhi  was inspected on 17.08.09 , by a team lead by Dr. T.K Joshi  and incinerator was found operating . Temperature for Primary & Secondary Chambers of the incinerator were not  meeting the prescribed standards. Other deficiencies w.r.t management of Bio-Medical Waste  were also observed in the hospital. Status of 20 incinerators including this hospital was placed before the committee. 

Case last came up in the High Court on 17.08.09 and as informed by the legal cell the court has asked for the complete status before the next date of hearing i.e. on 28.10.09. The said court order was also placed before the committee.
Decisions Taken by BMW Committee No. 1 in the Meeting Held on 04th & 8th September 2009,:

Decisions taken in respect of the inspected/ monitored units  are given at Annexure 1 & 2.
        In case of units which have submitted monitoring report of the incinerators from Guru               Gobind Singh Indraprastha University, CPCB to be requested for the monitoring of the         Incinerators.

           (Dharmentra )       (Dr. A. K. Ambasht)       ( Dr.T.K.Joshi)             ( Dr. Chander Prakash ) 

         Chairman,DPCC         M.S.,DPCC              COEH, MAMC                        SEE (BMW ) 

             (Dr. Chetna Harjai)                ( D.K.Singh )     (D.K.Srivastava )         ( M.I.Siddiqui)        Scientist, Env.Deptt, GNCTD            EE ( BMW)        AEE ( BMW)                   AEE ( BMW) 

Annexure 7
Decisions taken by the BMW Committee No.1, in the Meeting Held on 04.09.09, w.r.t. 

Agenda 8: Regarding Common Bio-Medical Waste Treatment Facility at Ghazipur.

                     The Case of M/s SMS Envoclean Pvt. Limited, was earlier placed before the Committee as decided in file. Earlier the application for Consent to Establish received from the unit was refused vide letter dated 25.06.07, as decided by BMW Committee in its meeting held on 22.06.07. The said decision was taken after the inspection of the site by the team of officials from CPCB, DPCC and DHS and also considering the comments received from CPCB regarding the site proposed for the said facility at Ghazipur. 

             A letter was issued to Member Secretary, CPCB on 23.01.09 after the meeting of Chief Secretary, Delhi on 26.12.08. Chief Secretary of GNCT of Delhi in the said meeting desired that CPCB may be approached to allow setting up of CBWTF at Ghazipur as there is a need for CBWTF for East Delhi.

             In response to the said letter, CPCB has sent letter dated 11.02.09. In the said letter CPCB has referred Rule 7 of BMW Rules regarding DPCC is the prescribed Authority for enforcement of provisions of BMW Rules. For specific views of CPCB on the subject, information e.g. Feasibility Report, Base Line Data, Location Map recommendations of DPCC, Expenditure and other details have been sought.

              The matter was discussed in the meeting of BMW Committee No1 on 02.03.2009, and it was decided that Member Secretary, DPCC will write a letter to CPCB referring the earlier letters of CPCB on the subject.

               A letter as decided by the Committee was issued on 24.04.2009 to Member Secretary, CPCB. In response to the said letter, CPCB has submitted a reply dated 19.5.2009 wherein they have stated that while selecting a site for CBWTF, guidelines of CPCB as well as baseline data of proposed site w.r.t. ambient air quality and ground water quality for relevant parameters be taken into account. CPCB has also stated that the proposed site at Ghazipur (approx. 0.25 Acres) is about 300 meters away from residential flat and a mosque (sensitive area) is located at a distance of 80 meters from the site. CPCB has also stated that the proposed site is located on a part of Ghazipur Municipal landfill. CPCB has stated that views of CPCB on the proposed CBWTF at Ghazipur, Delhi be considered.


A letter has been received from the Office of Chief Minister, Delhi on 15.05.2009 wherein RWA has submitted a representation regarding setting up of CBWTF at Ghazipur. In the representation forwarded by Chief Ministers Office, there is also a mention of Kitchen Waste Treatment Plant at Ghazipur. As a slaughter house of MCD has already been constructed, the matter might pertain to MCD, which is being dealt by MSW Cell..

Decisions Taken by BMW Committee No. 1 in the Meeting Held on 01.06.2009

File to be Put-up administratively.
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Action Taken Report w.r.t Decision Taken in the Meeting Held on 01.06.2009

File was put up and as decided , a letter has been issued to Directorate of Health Services regarding feasibility study for the CBWTF at Gazipur. A complaint of Resident Welfare Association of DDA Flats Gazipur, through the  Office of Chief Minister , has been received. regarding  CTF etc. 

Decisions Taken by BMW Committee No. 1 in the Meeting Held on 04.09.2009

Inspection by MSW Cell of the site regarding CTF etc w.r.t complaints received.

            (Dharmentra )        (Dr. A. K. Ambasht)       ( Dr.T.K.Joshi)             ( Dr. Chander Prakash ) 

         Chairman,DPCC         M.S.,DPCC                 COEH, MAMC                    SEE (BMW ) 

             (Dr. Chetna Harjai)                ( D.K.Singh )     (D.K.Srivastava )    ( M.I.Siddiqui)        Scientist, Env.Deptt, GNCTD            EE ( BMW)            AEE ( BMW)                   AEE ( BMW) 

DECISIONS TAKEN BY BMW COMMITTEE NO.1IN THE MEETING HELD ON 4TH,7TH  & 8TH SEPTEMBER,2009 W.R.T. AGENDA NO.2(80 CASES OF PVT.HOSPITALS/COMMON OPERATORS/OTHER MISCELLANEOUS CASES) (ANNEXURE–1)    

	   Sl.    NO.
	Name and Address  of the Unit 
	Authorization status
	Consent  Status
	Decision of the committee on 31-8-2007
	Action Taken  w.r.t Decision Taken on .31-8-2007 /  Remarks
	Decision of the committee  in the  Meeting  on 04-10-2007
	Action Taken w.r.t Decision Taken on 04-10.2007

	58.


	M/s Synergy Waste Management Pvt. Ltd.    Near Composite Plant, Sukhdev Vihar      Okhla, New Delhi-20.  


	 Applied for authorization on 22.06.06 for 3 years as per Rules. Authorization was granted on 07.11.06 for 1year 
	Applied for Consent on 27.06.06 with 3 years fee.  Consent to operate was granted on 07.11.06 for 1year.
	1. SCN under rule 7 of BMW Rules is issued for the following: 1. waste should not be kept in open. 2. ‘On Govt. Duty’ on vehicles should not be display. 3. Sludge dewatering device be provided with ETP.4. Manual mode on PLC should not be used. 5. Measures to control smell from BMW be taken. 6. Rota meter should be provided at PC &SC of incinerator.
	1.SCN has been issued on 03.09.2007

2. Inspection has been conducted on 27-9-2007.

 3. SCN u/s 5 of EP Act was issued by CPCB on 7-9-2007 after the inspection on 24-7-2007

4. Operator has submitted reply to both the notices mentioned above.

 5. The fact finding committee has been constituted by DHS for the complaints received from residents of Sukhdev Vihar and the representations received from the operators.

6. Letter issued to The Principal Secretary (Health) for allotment of alternative site.

7. Meeting of Committee constituted by Pr. Secy.(Health) GNCTD, was held on 24.10.07.

8. Authorization under BMW Rules & Consent to operate under Air Act granted to the Operator of CBMWT Facility was upto 06.11.2007.

9. Letter from CPCB dated: 05.10.07 to  CBMWT facility with directions for taking certain measures for the compliance of BMW Rules may also be perused.( Copy enclosed) 
	 The case was discussed in detail  & Show Cause Notice issued to the operator on 03.09.2007, Reply received from the Operator of the CBMWT and inspection carried out on 27.09.07, were also considered  and following decisions were taken :

(i) W.r.t deficiency “The Bio – Medical Waste should be kept in closed bins” mentioned in the said Notice, Reply is factually incorrect and the Committee has decided to issue Show Cause Notice for Closure of the Facility. 

(ii) Regarding  erasing of “ On Government Duty “ printed on the vehicles used for collecting BMW ,  the Committee accepts the reply.

(iii)  Regarding installation of Filter Press with the ETP for dewatering of sludge as mentioned in the said Notice, despite clear Notice the unit has not complied with the directions and given justifications which is not acceptable to the Committee. The Operator of the CBMWT Facility is once again directed to install Filter Press within three weeks and confirm through an Affidavit before next date of meeting of the Committee i.e on 15.11.2007.

(iv) Regarding “The manual mode of operation in the installed programmable Logic Control (PLC) based control system should be removed “  mentioned in the said Notice, Committee is not satisfied with the reply  and the Committee insists that Automatic System (PLC)  Should only be used as  mentioned in th CPCB Guidelines and an Affidavit should be filed by the Operator with in three weeks and he should comply with this direction before the next meeting of this Committee i.e. on 15.11.2007.To ensure that Operator of the said  CBMWT Facility, complies with this direction, the Operator of the Facility , will  submit a  Bank Guarantee of Rs. One Lakh ,  valid for Six month period , in favour of Delhi Pollution Control Committee, within three weeks along with the said Affidavit.

(v) Regarding “Necessary measures should be taken for controlling the smell generated from BMW within the facility “mentioned in the Notice, the Committee accepts the reply, however any discontinuance or irregularity in the action will result in filing of another Bank Guarantee of Rs. One Lakh valid for Six month period, in favour of DPCC, by the Operator of the said Facility.

(vi) Regarding “ Rota – meters and pressure gauges should be installed in the primary and secondary chamber of the Incinerator “ mentioned in the said Notice , the Operator of the said Facility has not filed factually correct reply since the Rota meter and pressure gauges not found installed during the inspection on 27.09.07. The Committee directs him to file an Affidavit after installation of Rota meters and Pressure Gauges, within three weeks.   
	Show Cause Notice u/s 5 of EPA issued on 12.10.07 for the decisions taken by the committee. Reply along with the affidavit received for the compliance of the decision taken by the committee. Informed that provided filter press, informed regarding never use of manual mode of operation in the installed PLC, and regarding installation of Rota meters and pressure gauges, lids provided to all BMW plastic containers and necessary measures taken to control the smell, display sign (on Govt. Duty have been erased, no segregation is done within the facility, records of BMW collection and   incineration / autoclaving are being maintained. Operator of the CBMWT requested for exemption from depositing the Bank Guarantee. As directed by Chairman DPCC letter issued on 07.11.07 informing that no exemption from Bank Guarantee is possible. Operator submitted the Bank Guarantee of Rs. One Lakh , valid for 6 months.

The Operator of the facility had requested for grant of authorization under BMW Rules since earlier granted authorization expired on 06.11.07.( Consent to operate also expired on 06.11.07.)


 Decision  Taken by the Committee  in the  Meeting  on 15-11-2007:   Since  a complaint against this unit has been processed & submitted to Hon’ble Lt. Governor , Delhi, and since  its Authorization under BMW Rules & Consent  under the Air / Water Act , lapsed on 06.11.07 , full yearly authorization or 3 yearly authorization / consent under the said Rules / Acts is not possible under the circumstances. An interim extension of the  Authorization under BMW Rules and  Consent to operate under the Air / Water Acts , upto 31.12.2007, is granted by which time the status of the complaint will be decided. Meanwhile Member Secretary, DPCC, will speak to  Medical Deptt./ Directorate of Health Services & get the report of the Committee  set up by them for deciding on shifting  his location.

Action Taken Report w.r.t. meeting on 15.11.07:  (i) Authorization under BMW Rules and consent to operate under the Air & Water Acts extended upto 31.12.07. (ii)  Letter issued to the  Convenor of the Committee constituted for said operator seeking report of the committee. Report waited.   

(III) The operator has submitted a list of 8 units w.r.t the letter issued seeking the list of the units (drug mfg units) from which the operator is collecting BMW waste however the units not applied for authorization.. 
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        M/s Synergy Waste Management Pvt. Ltd, Near  Composite Plant, Sukhdev Vihar, Okhla, Delhi-20. 

Decision Taken by BMW Committee No. 1 in the Meeting Held on 15.01.2008 : “Both, the decision of Hon’ble Lt. Governor and the inspection report are not yet available on file. These reports may be expedited and put up on file formally through Member Secretary, DPCC and other members of the Committee to the Chairman. Since this may take 15 days, the authorization under BMW Rules and Consent to operate under Air & Water Acts may be extended for interim period of one month i.e. 31st January, 2008.”

Action taken w.r.t Meeting on 15.01.2008:  

In view of the above decision taken by the said BMW Committee No. 1, the extension of the Authorization under BMW Rules and Consent under the Air / Water Acts up to 31.01.2008, has been issued on 25.01.2008. Report of the Independent Committee received and  put up in file . As directed  by the Chairman, DPCC, the same is placed before the BMW Committee No.1 for the decision. 

Decision Taken by BMW Committee No. 1 in the Meeting Held on 08.02.2008 : 

The report of the Committee constituted by Pr. Secretary (Health) to enquire into the case of M/s Synergy Waste Management Pvt. Ltd. was placed before BMW Committee No-I today. The report is clear that in the long run it would not be advisable to keep the operation of Bio Medical Waste treatment facility at the existing premises at Okhla. Several options of alternate space were discussed. According to Dr. T.K. Joshi, there are three places which can be inspected and a decision can be taken in one of them which is free from all possible health hazards for operating such a facility. These are (a) Deen Dayal Upadhyaya Hospital, Hari Nagar, New Delhi (b) Rao Tula Ram Memorial Hospital, Jafferpur, Delhi & (c) Maharishi Balmiki Hospital, Pooth Khurd, Delhi. 

The above three premises may be inspected by a team headed by Dr. T.K. Joshi, Mr. D.K. Singh and the management of Synergey Waste Management Pvt. Ltd. so that an amicable solution could be found out. The report will be submitted on or before 29.02.2008. The authorization & consent of M/s Synergy Waste Management Pvt. Ltd. may be extended upto 29.02.2008 in view of the above and in the extension letter; one of the deficiencies noted would be communicated.  

Action Taken w.r.t Meeting on 08.02.2008:
(i) Authorization under BMW Rules and Consent to Operate under the Air & Water Acts extended upto 29.02.08 vide letter issued on   22 .02.08 & one of the deficiencies noted has       been communicated.

(ii)A letter dated 29.02.08,  was received from the director of M/s Synergy Waste Management Pvt. Ltd. requesting for extension of authorization under BMW Rules  for one year. As directed by      Chairman, DPCC, a letter has been issued to the said operator informing that the extension of authorization under the said Bio-medical Waste Rules, for a year, is not possible.       
(iii) A team headed by Dr. T.K.Joshi inspected the following three sites on 27.02.08 ;  1. Deen Dayal Upadhyaya Hospital, Hari Nagar, Delhi-64  2. Rao Tula Ram Memorial Hospital, Jafferpur,        Delhi-      43.   3.Maharishi Balmiki Hospital, Pooth Khurd, Delhi-39 and report was submitted to Chairman DPCC in file. The team found that none of the above mentioned three sites of the       Hospitals are       suitable for the establishment of a Common Bio-Medical Waste Treatment Facility. As directed by the Chairman, DPCC, the matter is placed before the BMW Committee No.1.(iv) A letter dated 29.02.08, has also been received from the director of M/s Synergy Waste Management Pvt. Ltd., requesting to provide a copy of the said report of the team.

Decision Taken by BMW Committee No. 1 in the Meeting Held on 18.03.2008 :

(i) While Directorate of Health Services (DHS) , Govt. of NCT Delhi and the Private     Operator (M/s Synergy Waste Management Pvt. Ltd, Near Composite  Plant, Sukhdev  

     Vihar, Okhla, Delhi- 20.) will follow up with DDA for allotment of land for    the Common Bio Medical  Waste Treatment Facility  , this matter will be raised in the    list of issues to be taken up by      Chairman, DPCC with Vice Chairman, DDA.

(ii) Authorization under BMW Rules and Consent to Operate under the Air & Water Acts extended upto 30.04.2008.(iii)Operator must get the land organized by  himself or  through DDA.  

Action Taken w.r.t Meeting on 18.03.2008:

(i) Aforementioned decision taken by the BMW Committee No.1, was sent to CMC for inclusion in the list of issues to be taken up by  Chairman, DPCC with Vice Chairman, DDA.

(ii) Authorization under BMW Rules and Consent to Operate under the Air & Water Acts extended upto 30.04.2008 vide letter issued on 09.04.08 mentioning the aforementioned decision taken by the BMW Committee No.1 in the meeting held on       18.03.08. 

(iii) Copy of the said letter was also sent to Directorate of Health Services (DHS) , Govt. of NCT Delhi.

(iv) A letter dated 28.04.08 has been received from the director of M/s Synergy Waste Management Pvt. Ltd., requesting for extension of  authorization. Vide another letter dated 28.04.08 the Director of the unit has stated the back ground / brief of       the allotment of the said site by DDA to DHS for the said facility and also stated that the said site was inspected by officials of DHS, CPCB,  DPCC & COEH prior to its establishment. The said site is on the allotted land by DDA to DHS for       carrying out the activities of treatment and disposal of BMW. It is also mentioned that in the surrounding area is being used for waste management activities e.g. Okhla STP, MCD compost plant, NDMC waste to power project etc. It is mentioned       that DHS and DDA are in a better position to explain about the site that was already given to the operator or suggest an alternate site for  the treatment and disposal of BMW. It is also mentioned by the operator that whatever directions were given to       the operator, the same was complied and also enclosed the copy of stack monitoring report and water analysis report dated 19.09.07. showing parameters within the prescribed limit. It is also mentioned that the operator has approached DHS for       looking for an alternate land also. Requested for looking the matter sympathetically and for grant of authorization under BMW Rules and Consent to Operate under Air and Water Act.

v. A representation has been received from the residents of Sukhdev Vihar, DDA flats regarding health hazards due to treatment of large quantity of BMW at the said plant of CBMWTF. Near the residential area of Sukhdev Vihar    

Decisions Taken by BMW Committee No. 1 in the Meeting Held on 06.05.2008 :

(i) For finding a suitable alternative site for this  Common BMW Treatment Facility, a letter may be written by Chairman, DPCC, to Vice Chairman, DDA, and Commissioner, MCD, since this unit will have to be trans-located soon.

(ii) Authorization under BMW Rules and Consent to Operate under the Air & Water Acts extended upto the   next BMW Committee meeting  on 13.06.2008.

Action Taken w.r.t Meeting on 06.05.2008: 

(i) Letter issued to, Vice Chairman, DDA, and Commissioner, MCD, for finding a suitable alternative site for this  Common BMW Treatment Facility .
(ii)Authorization under BMW Rules and Consent to Operate under the Air & Water Acts extended upto  13.06.2008 vide letter issued on  21.05.08.Representatiom from the operator  received regarding extension of Authorization.  
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Decisions Taken by BMW Committee No. 1 in the Meeting Held on 13.06.2008 : Authorization  under BMW Rules and Consent to Operate under  the Air & Water Acts extended upto the next BMW Committee meeting  on 14.07.2008.

Action Taken w.r.t Meeting on 13.06.2008:  (i) Authorization under BMW Rules and Consent to Operate under the Air & Water Acts extended upto  14.07..2008 vide letter issued on  27.06.08.
(ii)  A  letter  from CMO ( BMW) , Deptt of Health Govt. of NCT , Delhi  received informing that Deptt of Health & Family Welfare ,GNCT  Delhi, has already taken up the matter   with  the DDA & has applied for an alternative land for  the present CTF at Okhla. 

         Decisions Taken by BMW Committee No. 1 in the Meeting Held on 14.07.2008 : “Ask the two operators that on what basis they are charging the fee and how are they increasing the fee overnight by 100 %. A formal clear justification of          increasing the fee may be submitted that must be examined properly and file may be submitted administratively.If the unit does not behave, no further extension of authorization will be granted.  Reply must come within 15 days and file to be put up          administratively. 

         Action Taken w.r.t Meeting on 14.07.08:     Letter issued to both the Common Operators of Bio- Medical Waste Treatment Facilities in Delhi . 

 Decisions Taken by BMW Committee No. 1 in the Meeting Held on 27.08.2008 : Both Metro-Biocare & Synergy are unauthorizingly increasing prices. File to be submitted administratively without waiting for minutes.

Action Taken w.r.t. Meeting on 27.08.2008 :  File  submitted administratively. As directed by Chairman, DPCC,  information has been tabulated and dealt in common file on the issue of rates /service charges. A PIL has been filed against the operator . Representations  have been received from the unit ( also from Chief Minister Office ) regarding request for extension of authorization. 
Decisions Taken by BMW Committee No. 1 in the Meeting Held on 29.09.2008 :  (i)  Action as per the decisions taken today  in  case of  Agenda No. 1 (Regarding  rates / service charges  for BMW ). 

                                                                                                                                       (ii) The same Committee which  inspected earlier  will inspect now for PLC system  and file report by 30.10.2008 at which time Bank Gaurantee  issue will be decided. 

Action Taken w.r.t. Meeting on 29.09.2008 : (i) Letter issued Regarding  rates / service charges  for BMW.

                                                                            (ii) Inspected on  15.10.08.

                                                                            (iii) There is PIL/High Court Case WP(C) 6976 of 2008 “P.K. Nayyar & Others Vs U.O.I & Others, regarding case filed against M/s Synergy Waste Management Pvt. Ltd. by the residents of DDA Flats Sukhdev Vihar, Delhi. DPCC is one of the respondents and Affidavit has been filed in the Court. High Court vide order dated 24.09.08 had requested Chief Secretary, GNCT Delhi, to convene a meeting of the Secretaries of the concerned departments and key personnel of the concerned agencies with  a view to taking urgent steps for relocation of the BMW   treatment facility.  The meeting was taken by the Chief secretary on 22.10.08.  Two  Letters  received from the Operator,  one regarding the representation w.r.t. meeting of Chief Secretary, Delhi regarding the High Court Case and another one in reply to the letter issued to the Operator on the Rate/charges for BMW  issue.     
Decisions Taken by BMW Committee No. 1 in the Meeting Held on 30.10.2008:

Chief Secretary, Govt of  NCT Delhi,  took a meeting  on  22.10.2008 & follow up action is being taken accordingly . The  BMW Committee  will be apprised of the updated position on 28.11.2008 . Regarding  letter received from the Operator on the issue of Rates / Service Charges for BMW ,  Operator  be asked to follow the Directorate of Health Services(DHS) agreement. Place a copy on the file.  Inspection of the unit was conducted by Independent Committee headed by Air  Mashl (Retd.) L.K.Verma , Dr. T.K..Joshi  & DPCC official  on 15.10.08 . The inspection report was placed before the Committee. Installed Programmable Logic Control (PLC) based control System was  found in use & found  operating satisfactorily. Independent Committee had recommended in its report to segregate Cat 6 waste in red bags (and not in yellow bags) to reduce load on the incinerator in order to reduce emission and particulate matter pollution. Both  the Operators be issued a letter in this regard to convey this to their member units  for proper segregation of the Bio-Medical Waste.

Action Taken w.r.t. Meeting on  30.10.2008 :  (i)  Letter issued to both the Operators to follow the Directorate of Health Services(DHS) agreement & to convey  the aforementioned decision of the Committee  to their member units for proper segregation of the Bio-Medical Waste. (ii) Team constituted for visit of  area  for Rural Growth Centre Site  at Ghogha  Village , not found the site suitable since the area is being developed by MCD for Relocation of Dairies & it was also revealed that in the nearby area there is Air Base of Armed Forces.   
(iii) A Team constituted by Chief Secretary ,GNCTD ( as decided in the meeting on 22.10.08), also visited the sites on 31.10.08, as suggested by the representatives of the  Association of  residents of  DDA Flats Sukhdev  Vihar , Delhi, and submitted its report . 

(iv)Next Date of Hearing in the said PIL is on 14.01.2008. 


 (v) M/s Synergy Waste Management Pvt. Ltd , has given representation and requested for extension of the Authorization under BMW Rules.

Decisions Taken by BMW Committee No. 1 in the Meeting Held on  28.11.2008:

Extension of Authorization allowed up to today i.e. up to 28.11.2008 . Further action will be taken based on the decision  about the  location. Dr. Chetna to Talk to Dr. K.S. Baghotia , CMO( BMW) of DHS regarding the representation received from the Operator on the Issue of  rates / service charges for BMW.

Action Taken w.r.t. Meeting on  28.11.2008:                           Letter issued

Decisions Taken by BMW Committee No. 1 in the Meeting Held on  29.12.2008:

Ask the unit to comply with the prescribed  standards  with a stringent warning that if any of the parameters are not met authorization will be cancelled. Also if the unit does not abide by any of the  cluase of the agreement with DHS its authorization will be cancelled. Unit may be directed to contact DHS and get his premises shifted to the new site as per the minutes of the meeting taken by the Chief Secretary, Govt. of Delhi last week. The relocation has to be done at his own cost and risk as DPCC is not happly with his style / system of functioning as noted during the various inspections of the unit. Call on 29.01.2009. 

Action Taken w.r.t. Meeting on  29.12.2008:                  Letter issued. 
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Decisions Taken by BMW Committee No. 1 in the Meeting Held on 29.01.2009 : 
                                                                                                                                       Ask the unit to file full compliance of directions issued to it earlier. Call on 02.03.2009.

Action Taken w.r.t. Meeting on 29.01.2009: Letter issued. Reply received. Informed regarding the measures taken & requested for extension  of authorization. During the hearing on 25.02.09, in the said High Court Case, Hon’ble High Court has directed DPCC to inform the Court regarding the Criteria if any, regarding the distance of Common Bio Medical Waste Treatment Facility (CBWTF) from the Residential area, available in the guidelines of CPCB or evolved by Delhi Pollution Control Committee or any other State Pollution Control Boards/Pollution Control Committees.
Decisions Taken by BMW Committee No. 1 in the Meeting Held on 02.03.2009

Call for personal hearing on 27.04.2009 at 3.10 PM. The operator will follow the rates for collection, transportation and treatment of Bio-Medical Waste as decided by the Directorate of Health Services (DHS) earlier and also communicated to the operator vide letter dated 24.02.2009, If  the operator flouts, Authorization will be cancelled.

Action Taken w.r.t. Meeting on 02.03.2009:                  

Letter issued. Representation received from the operator. 

In the High Court Case “P.K. Nayyar and others Vs UOI and others” in W.P.(C) 6976/2008, pursuant to the court order dated 04.03.2009, local Commissioner appointed by the court had inspected the site identified for CBWTF, on 05.03.09 and given its report to the court, pointing out certain observations regarding several residential areas, residential staff quarters, MCD primary school in the nearby of the said identified site for CBWTF. It is also mentioned in the said report that several residents of nearby colonies gathered at the site and were  expressing objections to the installation of BMW treatment facility at the proposed location. Thereafter vide order dated 06.03.2009, the court had directed the Asstt. Commissioner, DJB, to identify the site within one week, in the presence of the representative of the petitioners, the Pollution Control Board, Department of Health, NCT of Delhi and respondent no. 7. The Pollution Control Board was directed to submit a detailed report in the light of the report of the Commissioner.

Hon’ble High Court has given following order on 01.04.2009 “Counsel appearing for the Pollution Control Board seeks four weeks’ further time to make a report. She says that the board will inspect the site in presence of the officers of the Delhi Jal Board. Learned counsel appearing for the Delhi Jal Board states that the Board officers will accompany the officers of the Pollution Control Board at the time of the site inspection. The SHO of the concerned Police Station shall extend police protection, if necessary, to carry out the site inspection by the Pollution Control Board. Adjourned to 6th May 2009”. 

Reply dated 02.03.2009 was received from the Operator along with analysis report of Volatile Compound in ash (for sample collected by Guru Gobind Singh Indraprastha University on 06.02.09) showing the Volatile Compound in ash with in  the limit. 

As directed by Chairman, DPCC, inspection was carried out by the team of Dr. T.K. Joshi in presence of officials of DJB on 22.04.09

and the report of the team and affidavit, as approved by Chairman, DPCC has been filed in the High Court.

Decisions Taken by BMW Committee No. 1 in the Meeting Held on 27.04.2009 : 

The representatives of the CBWTF came for personal hearing today. Case to be taken up on 25.05.2009 after confirmation on the rates from Directorate of Health Services GNCT Delhi.

Action Taken w.r.t. Meeting on 27.04.2009: Letter issued to DHS on 08.05.09, reply awaited. Letter dated 25.05.09 received with request for extension of the authorization 

        High Court case in the aforesaid matter is pending.
Decisions Taken by BMW Committee No. 1 in the Meeting Held on 01.06.2009 : 






        Call on in next meeting.

Action Taken w.r.t. Meeting on 01.06.2009 : (i) Reply w.r.t letter dated 08.05.09 received from DHS and it has been informed that  there is no provision of extra Bio-Medical Waste in the contract entered with DHS under clause 2 of the agreement with M/s Synergy Waste Management Pvt. Ltd. and informed that proposal as mentioned in the letter of DPCC cannot be agreed. 

(ii)  Earlier Director DHS vide letter dated 01.05.09, had  requested to look into the matter regarding grant of  authorization to the operator having agreement with DHS for 10 years for operation of       CBWTF.  

(iii) The Operator has applied for the renewal of Authorization on 11.08.2009 and requested for renewal of the authorization for a further period of 3 years from the date of authorization given to the        operator on 07.11.06. 

(iv)  A letter  dated  24.07.09 has been received from Delhi Medical Association regarding non compliance w.r.t rates decided by DPCC  by both the operators. 

(v)  High Court case  in the aforesaid matter is pending and next date of hearing is on 28.10.09.
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       M/s Synergy Waste Management Pvt. Ltd, Near  Composite Plant, Sukhdev Vihar, Okhla, Delhi-20. 

Decisions Taken by BMW Committee No. 1 in the Meeting Held on 08.09.2009 : 

                                             Inspection to check PLC & also issue a letter to DHS regarding rates. 


     (Dharmendra)              (Dr. A.K.Ambasht)               (Dr.T.K.Joshi)      (Dr.Chandra Prakash)          (Dr. Chetna Harjai)             (D.K.Singh)          (D.K.Srivastava)          (M.I.Siddiqui)

  Chairman,DPCC    Member Secretary,DPCC           COEH ,MAMC              SEE (BMW)               Scientist,DOE,GNCTD           EE(BMW)                AEE(BMW)              AEE(BMW)        
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