Minutes for Meeting of the BMW Committee No. 1 held on 10.10.2012

The following officials attended the meeting:

1. Sh. Sanjeev Kumar                                                                        --- In Chair

2. Sh. Sandeep Mishra, Member Secretary, DPCC                           --- Member 
3. Dr. Ashok Khurana, MS, G.B. Pant, Hospital                               --- Member

4. Dr. Chetna Harjai, Scientist, Deptt. of Env. GNCT, Delhi            --- Member

5. Sh. B. Kumar, Additional Director, DPCC                                    --- Member 

6. Ms. Ajeeta D. Agarwal, SEE (WMC-I), DPCC                            --- Member      

7. Sh. Sanjay Vatts, EE (WMC-I), DPCC                                         --- Member      
The meeting of the BMW Committee No. 1 constituted for deciding Authorization under the BMW Rules, was held on 10.10.2012.  For the present meeting, decisions recommended agenda wise are as follows: 
Decision on Agenda 1 :  
Representative of the hospital has attended personal hearing. However, he was not aware of the issues involved. The said Committee has decided to issue Show Cause Notice (SCN) for closure u/s 5 of Environment (Protection) Act , 1986, addressed to the hospital & CPWD.
Decision on Agenda No. 2: 
· Issues regarding three CBWTFs operating in Delhi (listed at S.No. 1 to 3), have been deferred till next meeting.    
· Decisions/ Recommendations w.r.t 39 Pvt Hospitals & other miscellaneous cases etc are mentioned in the individual sheets of Annexure-1.
Decision on Agenda 3: 
· Decisions/ Recommendations w.r.t  49 Cases of Govt. Hospitals/Research Institutes etc are  mentioned in the individual sheets of Annexure-2.
· A status regarding formation of Environment Management Group (EMG), installation/ maintenance of Effluent Treatment Plant (ETP)/ Sewage Treatment Plant (STP) , Rain Water      Harvesting System (RWHS) , Solar Water Heating System (SWHS) is to be prepared w.r.t  Government Hospitals & the same will be apprised to  Principal Secy. (Health) , through a D.O. letter requesting for a meeting at the level of Chief Secretary Delhi, for ensuring proper co-ordination between Hospitals & CPWD/PWD.

It was also decided that the files requiring immediate/ urgent action (after inspection) will be put up administratively for appropriate decision & same may be put up before Committee later in its meeting for ratification of the decision.
Decision on Agenda 4: 
Committee ratified the decision of issuance of CTE, CTO & Authorization under E-Waste Rules to M/s Parth Sarthi Environment Engineers, A-115, Okhla Industrial Area, Phase-II, New Delhi-20. 
(Sh. Sanjeev Kumar)                          (Sh. Sandeep Mishra)                       (Dr.Ashok Khurana)                   In Chair                                   Member Secretary, DPCC               MS, G.B. Pant, Hospital    

                                (Sh. B. Kumar)                                            (Ms. Ajeeta D. Agarwal)                                             

                            Addl. Director, DPCC                                        SEE (WMC-I), DPCC                          

                                Dr. Chetna Harjai,                                     (Sh. Sanjay Vatts)
                         (Scientist, Deptt. of Env. GNCT)                    EE (WMC-I), DPCC
	Sl.No
	Name and Address of Unit 
	Distt. No.
	Bed (No.)
	Authorisation Status
	CTO Status
	CTE Status
	SWHS Status
	RWHS Status
	ETP Status
	Brief Status 
	Decisions Recommended  in the Meeting on 
19.01.12
	ATR/Status
	Decisions Recommended  in the Meeting on 10.10.12

	1
	Lok Nayak Hospital, 
J. L. Nehru Marg, New Delhi-2
	C-001
	1649
	Applied on 17.02.10 
	Applied on 03.03.08 (3 years lapsed)
	Applied on 13.10.11
	Under process
	Not provided due to high water table
	Installed (found  non functional) 
	1.Hospital was inspected as per the approval of MS, DPCC as News Item was telecast on News 24 Channel regarding improper Management of  BMW in Govt. hospitals , on 16.02.12.  following were the deficiencies observed:
(i) Segregation not found proper (e.g. some plastic waste like gloves found in incinerable waste). 
(ii)Syringe cutter cum needle destroyer found defunct. 
(iii)Sharp containers found in use in casualty ward but were not found properly sealed /   whole needle & syringe assembly  found kept in the sharp boxes.
(iv)General waste from Lok Nayak Hospital is dumped in the MCD Dhalao near the incinerator plant. Bio-medical waste also found mixed in some of the general waste bags, which were opened during inspection. MCD Dhalao found full of black bags.
(v)The space for Dhalao is not sufficient since the quantity of waste being dumped is more and not properly maintained (due to delay in lifting of the waste by MCD), which causes unhealthy condition and foul smell.
(vi)Isolated storage room for incinerable and autoclavable waste not provided. Incinerable waste found stored in trolleys without cover in open near incinerator plant. Autoclaved & non-autoclaved waste found kept nearby autoclave in  the same room.
(vii)STPs installed and found operational however, adequacy report from the Empanelled Consultant of DPCC  not submitted.
 (viii)There are nine D.G. Sets installed by the hospital however, Noise Monitoring Report  of D.G. Sets have not been  submitted. 
	Letter for rectification  of deficiencies & for rest of the things
	1. Hospital was inspected as per the approval of MS, DPCC as News Item was telecast on News 24 Channel regarding improper Management of  BMW in Govt. hospitals , on 16.02.12. deficiencies observed. 
2. Show Cause Notice u/s 5 issued.
3. Hospital has submitted point wise  reply w.r.t SCN.  
4. As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. No reply received.  
	Reminder for EMG & rest of the things.


Granted (valid upto09.05.14)


Letter  seeking fresh application for  CTO & for  rest of the things.


1.Letter issued.

2.No reply received.  

	3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. No reply received.  
	Reminder for CTO, EMG & rest of the things.

	3
	Safderjung Hospital, Aurobindo Marg New Delhi-29
	S-002
	1531
	Granted (valid upto31.01.13) 
	Applied on 09.02.12
	Granted 
	matter under process
	installed
	matter under process.
	1. Hospital was inspected  on  09.05.11  & deficiencies were observed were : (i) Segregation of bio-medical waste was not found proper
(ii) Incinerator not found functional due to choking of I.D.fan , smoke was found in the incinerator room. (iii) Microwave found non operational  .  Reply dated 09.06.11 &  04.08.11 received regarding rectification of deficiencies.   
2. As decided in meeting held on 09.03.11Request of the DG , DGHS  regarding  closure of the incinerator of Safder Jung Hospital accepted.
 Letter issued to inform hospital that Bio Medical Waste must be treated and disposed off through any of the authorized Common Bio Medical Waste Treatment Facilities (CBWTF) in Delhi.
Reply received  on 08.11.11
3. Letter received regarding outsourcing for BMW stating that due to non -participation of any CBWTF in bidding process, hospital could not  outsource the BMW for disposal.  
	Letter  seeking fresh application for   CTO & for rest of the things.
	1.Letter issued. 
2. Hospital has applied for CTO on 09.02.12. .                                                    3.Hospital has submitted NMR & SMR of two DGSets(1700 KVA ) (by SIIR, meeting the norms).                                                                                             4.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. No reply received.                                5.Hospital has informed that they are outsourcing BMW to CBWTF.
	Reminder for EMG & status w.r.t 5 points. 


Granted (valid upto 

13.06.13)


1. Hospital inspected  on 17.06.11 following were the main observations: 

(i) Hospital is having agreement with Synergy Waste Management.

(ii)  Segregation found but needs improvement w.r.t collection in bags as some    bags were torn containing autoclave able waste at autoclave site.   

 2. As decided in meeting held on 27.09.11 letter w.r.t rectification of deficiencies issued. Reply received on 09.12.11  stating that measure to segregate BMW has been strengthened and Installation of ETP is in advance stage of completion.


1.Letter issued. 

2. No reply received. 

3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. No reply received.     

	
	Reminder 


1. As decided in meeting held on 09.03.11 hospital was inspected on 10.05.11 and following were the main observations: 

(i) One shredder provided but was not functional. 

(ii)CFLs partially change.

(iii) RWHS, ETP under consideration / process with engineering division. 

(iv). DG Set (2 no.s) of 320 KVA installed in a room without acoustic treatment. 

2.As decided in meeting held on 27.09.11 Letter for rectification of deficiencies and fresh application for renewal of Authorization issued. Reply received stating that medical college has been proposed and to be commissioned in the campus of the hospital.  The ETP & RWHS will be initiated for RBIPMT & MVID hospital jointly as per the medical design of medical college.


1.Letter issued. 

2.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. EMG constituted.     

3.Application for auth. Recd. By post. DD has expired. The same is being sent back for re-validation. Till then the application will be kept pending.

	4. However,  status  w.r.t 5 points has not submitted by the hospital. 
	Letter seeking  status w.r.t 5 points.


installed


1. Letter received on  18.08.11 stating that the incinerator plant  which was not in operation has started  functioning and submitted stack monitoring report from empanelled  lab. Parameters  found meeting the prescribed limits. 

2. As decided in meeting held on 27.09.11 Reminder letter for ETP & rest of the things issued. Reply not received. 


1.. Hospital has submitted monitoring report for Incinerator not meeting the prescribed norms, on 02.02.12 (monitoring conducted on  21.11.2011)            

2. Show Cause Notice u/s 5 and refusal of authorization issued instead of reminder after approval on the file as the hospital was not meeting the prescribed standards of Perticulate Matter, NOx & Temperature in primary chamber of incinerator.                                                              3.Hospital has informed CBWTF that the Incinerator is under repair & make necessary arrangements for removal of BMW.                                                                       4. Representation received from the hospital w.r.t 5 points status, requesting for exemption of ETP. Submitted quaterly monitoring report of incinerator & microwave.                                  

	5.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. No reply received.     
	Reminder w.r.t EMG & rest of the things.


under process


1. Hospital was inspected on 14.02.11 and following were the main observations.

(i) Incinerator not in operation, incinerable waste sent to MVID for incineration.

(ii) Autoclave was not in operation during inspection as there was some leakage in autoclave; same was under repair as informed it will be functional within few hours as engineer was doing his job during inspection.

2.As decided in meeting held on 09.03.11 Authorization &

Letter seeking status w.r.t 5 points issued. 

3.As decided in meeting held on 27.09.11 reminder letter issued. Reply not received. 


1.Letter issued.

2. Reply  received on 30.03.12.  Hospital has informed that work of ETP is likely to be started from May, 2012. SWHS  :  expected to complete by 30.05.12. RWHS: being rocky area it is not technically required as reported by Engg. Dept. of MCD. 

	3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. Reply received.     
	Letter seeking fresh application of CTO & rest of the things.


Solar Water heating System: Solar panels installed on OPD block & remaining work is under process.


Provided on director Bungalow and in rest of the areas it is under process.


1. As decided in meeting held on 27.09.11, letter seeking fresh application for CTO , present status w.r.t 5 points & informing  hospital that incinerator is not to be operated considering the observations/ monitoring in the past has been issued. no reply received.                                                                                                        2. Hospital was inspected as per the approval of MS, DPCC as News Item was telecast on News 24 Channel regarding improper Management of  BMW in Govt. hospitals , on 17.02.12.  following were the deficiencies observed: 

(i) Red, blue & yellow bags were found mixed with general waste at general waste site. 

(ii) it was informed by the representatives of the hospital that color bags found at the MCD dhalo/general waste storage site contains general waste & not BMW. And color bags were used by default.


1. Show Cause Notice u/s 5,  issued instead of reminder letter .

	2.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. 3. No reply received.                   4.However, directions of hospital to EE, PWD received w.r.t incinerator, monitoring report of DGSets & boiler. However, no reply in response to SCN received.
	Reminder for EMG & rest of the things.


Rajiv Gandhi Super Speciality Hospital

Near GTB Hospital, Tahirpur, Delhi-93


Not installed


1. Representative of the hospital attended the personal hearing on 15.09.10. It was informed that tender document is being prepared for handing over the work related to operation & maintenance of the hospital to the selected agency. Only OPD is running on temporary basis. 

2. As per the decision Letter regarding 5 points status issued. Reply received on 27.12.10 informing that ETP is not made operational as the hospital is not fully functional.

8.As decided in meeting held on 09.03.11 & 27.09.11 Letters  seeking status w.r.t 5 points issued. Reply not received. 


1.Letter issued .

2. Reply not received. 

	3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued.  No reply received.     
	Reminder for EMG & rest of the things.

	10
	G.B.Pant Hospital, J.L. Nehru Marg, New Delhi-2 
	C-002
	601
	Granted (valid upto 13.06.13)
	Granted (valid upto 13.06.13)
	Granted
(for additional Block/Building.)

 
	Matter with PWD
	Matter with PWD
	installed
	1.Hospital was inspected on 16.06.11.  Following are the main observations:  (i)Hospital is having agreement with  Synergy Waste Management Pvt Ltd.   (ii) Bio-Medical Waste Management was found satisfactory.
 Hospital has submitted adequacy report   (parameters meeting the prescribed limit) from empanelled lab on 12.03.11. Reply received stating ETP is functional ,  status of DG sets along with flue gas analysis report received. Hospital has submitted spore validation report of autoclave.
2.As decided in meeting held on 27.09.11 Letter  seeking fresh application for CTO & rest of the things issued.
	Reminder 
	1.Letter issued
2. Reply received on 02.03.12  w.r.t incinerator, in which hospital is asking for permission to dismantle incinerator.
3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. No reply received.     
	Reminder letter for EMG and permission for dismantling of incinerator.


Granted

(for existing Building)


Under process


1. The hospital was inspected on 13.09.10 and following were the main observations.

(I) Segregation needs improvement.

(II) Autoclavable waste given to some private Kabariwala.

(iii) ETP- installed and found functioning.

2. As decided reminder letter was issued.

3. As per the decisions on 15.09.10 letter was issued seeking  application for CTE for proposed medical college & renovation and also for remaining things including deficiencies observed during inspection.                                                                                                                                                      4. As decided in meeting held on 23.11.10 Letter for rectification of deficiencies observed during inspection has been issued. Reply received on 01.03.11 regarding 5 points stating: (i) SWHS and RWHS will be installed after completion of the college and new hospital building. (ii) Adequacy report for ETP is under process.

5. As decided in meeting held on 09.03.11 Letter issued.

6.As decided in meeting held on 27.09.11 Letter for CTE for proposed medical college & renovation  and also for corrective measures to control noise for DG Sets and for submission of fresh  NMR & status w.r.t SWHS, RWHS & CFLs issued. No reply received.

	
	Letter seeking present status w.r.t 5 points & for rest of the things.
	1. Letter issued.                                                                2. No reply received.                                                      3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. No reply received.     
	Reminder for EMG & rest of the things.


1. As decided in meeting held on 09.03.11 Final Reminder  seeking application for renewal of Authorization & CTO and status w.r.t  5 points issued. Hospital was inspected on 06.05.11. Bio-Medical Waste Management was found satisfactory. Reply received w.r.t status 5 points on 16.06.11 informing that PLC/Graphic recording system for incinerator has been installed & functioning properly.

2. As decided in meeting held on 27.09.11 Letter seeking status w.r.t 5 points issued. Hospital has submitted stack monitoring report for incinerator and spore test report for autoclave.. Hospital has submitted status w.r.t. installation of ETP & SWHS on 12.12.11. 

	
	Letter seeking present status w.r.t SWHS & ETP.
	1. Letter issued.                                       2.Reply received on 11.04.12  w.r.t  ETP & SWHS along with analysis report of flue gas & ash (of DTU) , meeting the norms.                                                                                3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. Reply received.
	Letter seeking status w.r.t ETP.


1. As decided in meeting held on 27.09.11 Final Reminder & for  fresh application for  Authorization & CTO issued. Hospital has submitted status w.r.t ETP (will be completed by this year) & DG Sets ( 750 KVA(2 no, ), 380 KVA (2No.), 500 KVA & 125 KVA. 


1. Hospital was inspected as per the approval of MS, DPCC as News Item was telecast on News 24 Channel regarding improper Management of  BMW in Govt. hospitals , on 15.02.12.  following were the deficiencies observed: 

(i) use of color coded bags & containers were not as per rule.

(ii) Blue bags are being used for general waste. 

(iii) Isolated site provided without Bio-Hazard symbol & very near to general waste site. 

(iv) Hospital is having DG Sets of 750 KVA (2 Nos) , 380 KVA (2 No.s), 320 KVA (1 No.) , 500KVA (1 No.) & 125 KVA (1 No.) . 

	2.Show Cause Notice u/s 5 issued.   3. Reply received on 15.03.12 stating deficiencies have been rectified & Incomplete application of  CTO received at DPCC 'By Post'.  3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. no reply received.   4. Letter seeking   documents required for CTO issued on 17.08.12.   5. Hospital has  submitted  NMR of DGSets installed & stack monitoring report of boiler (of DPCC, meeting the norms) .
	Reminder  


Dr. Baba Saheb Ambedkar Hospital Sector-6, Rohini

, New Delhi-85 


under process.(90% done).


1. The hospital was inspected on 31.8.10.

      (i)  Autoclave and shredder started working since June 2010.

      (ii) ETP,SWHS,RWHS,CFL matter with PWD.

      (iii) Noise monitoring report of DG Sets required.

2. As per the decisions on 15.09.10 letter was issued for rectification of the deficiencies observed during inspection & also for seeking fresh  application for renewal of authorization & CTO.

3. Reminder Letter issued.  Reply received on 01.02.11 w.r.t 5 points and also informed that acoustic enclosure has been installed for DG Set.

4.As decided in meeting held on 09.03.11 letter seeking status of 5 points. Hospital has directed PWD Zone III seeking status of 5 points & NMR. Hospital has not replied regarding status w.r.t 5 points. 

5. As decided in meeting held on 27.09.11 1. Hospital was inspected on 29.12.11 Bio-Medical waste management found satisfactory. 


Authorization granted.

+ Letter seeking status w.r.t ETP etc


1.Authorization issued. 

2.Letter issued.

3. Reply not received

	4.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. EMG constituted.     
	Reminder w.r.t ETP etc.


 Installed 


1. Hospital was inspected on 15.11.10 and deficiencies were observed.

2. As decided in meeting held on 23.11.10 letter seeking Letter for rectification of deficiencies observed during inspection issued. Reply received on 01.02.11  w.r.t earlier letter  informing that work for ETP will start shortly and other deficiencies have been taken care of.

8. As decided in meeting  held on 09.03.11. Authorization and letter seeking status w.r.t 5 points issued. Reply  for rectification of deficiencies & status w.r.t 5 points received .

9. As decided in meeting held on 27.09.11 Letter seeking status w.r.t 5 points issued. 


1. Letter issued.

2. Reply not received.

	3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. EMG constituted.     
	Final reminder.


Northern Railway Central Hospital, Basant  Lane

 New  Delhi-55


not installed


As decided in meeting held on 09.03.11 letter for rectification of deficiencies observed during inspection dated 10.02.12, status w.r.t 5 points and for fresh application for CTO issued. Reply not received.

5.As decided in meeting held on 27.09.11 Reminder letter issued. No reply received.. 

	
	Call for personal hearing in the next meeting.                      Inspection                    Call the concerned Officials (Chief Electrical Engineer & Principal Chief Engineer) regarding installation of ETP, SWHS, and RWHS.        
	1. Letter issued.                                                                     2.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued.                                                                         3.As per the decision of the meeting held on 18.04.12 hospital was inspected on 12.09.12.    during inspection deficiencies observed were:  (i) Segregation of BMW was not as per Rule. (ii) Bio-hazard symbols were not provided on containers.(iii) Area for isolated storage site for BMW was not sufficient and without proper demarcation for different types of BMW . During inspection, site was fully filled up with non segregated  BMW. (iv) Hospital is having 2 DG Sets of 500 KVA& 320KVA without adequate stack height.                                                                                    4.As informed letter regarding constitution of EMG issued to Divisional Manager, General Manager & Principal Cheif Engg Northern Railway.                                                         5. Directions of Hospital to DRM w.r.t 5 points received. 
	SCN for closure u/s 5 of EPA , addressed to Hospital & CPWD/PWD. 


not installed


CTE Granted. 

Reminder seeking adequacy report for ETP.


1.CTE issued.

2. Letter issued.

3.No reply received.

4.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. Reply received.     

	
	Reminder for adequacy report for ETP & fresh application of Authorization.


installed.


1. Hospital was inspected on 12.11.10 and following were observed.

  (I) ETP/STP not installed as informed designing is under process.

  (II) SWHS installed but not functional which is to be rectified as informed.

2. As decided in meeting held on 09.03.11 Letter seeking status  of ETP issued. Reply received dated 26.05.11 informing that ESIC Headquarter has appointed govt. agency for installation of ETP.  It was also informed that staircase has been provided for monitoring  of boiler

3.. As decided in meeting held on 27.09.11 Medical Commissioner of ESI, has called upon for personal hearing.


Representatives of the hospital & of the Medical Commissioner attended personal hearing on 19.01.12 and given a letter regarding steps/ measures taken by the hospital and informed that there is proposal to increase the  bed strength upto 400 Beds and additional / new construction is proposed and  accordingly the ETP etc will be designed  

Hospital be asked to apply for Environmental Clearance for the new/additional proposed constructions and  to submit  Time Bound Action plan for installation of ETP.


1. Letter issued. 

2.No reply received.                                    3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. EMG constituted.     

4. Hospital has informed that  there is proposal to increase the  bed strength upto 400 Beds and additional / new construction is proposed and  accordingly the ETP, SWHS , RWHS will be designed.  

	5.Hospital has requested to provide list of venders recognized by DPCC, for disposal of X-ray film & developer. 
	Letter seeking fresh application of CTE, CTO and Authorization for increased no. of beds & status w.r.t ETP.                                  


90% completed.


1. Hospital was inspected on 12.11.10 and following were the observations:

  (i) incinerator was not found in operation as it is operated on alternate days.

  (ii) Stack provided with incinerator approx. 30 mts from ground level.

2. As per the decision Authorization & Letter seeking status w.r.t 5 points issued. Reply received w.r.t 5 points.

3. As decided in meeting held on 09.03.11 Letter to DC (Shahdara Zone ) with copy to Commissioner ,MCD, regarding compliance w.r.t 5 points issued. Reply received. 

4. As decided in meeting held on 27.09.11 Letter seeking status w.r.t 5 points issued..


1. Letter issued.

2. No reply  received w.r.t 5 points status.   

	3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. EMG constituted.  
	Reminder

	20
	Chacha Nehru Bal Chikatsalya, Geeta Colony, Delhi-31
	E-179
	216
	Granted (valid upto 02.03.13)
	Granted (valid upto 31.03.14) 
	Granted
	Installed 
	Installed 
	Installed 
	This is a Delhi Govt. hospital having ETP, SWHS, RWHS, CFLs etc. and have been granted Authorization and CTO. Adequacy report for ETP submitted by the Hospital. 
	No Action
	As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued.EMG constituted.  
	No Action


Installed


1. Hospital was inspected on 18.11.10 and segregation found satisfactory. Incinerator found operating. Incinerable BMW from Kasturba Hospital, G.L. Maternity Hospital, RBTB and Hindu Rao Hospital is also incinerated at the the incinerator at M.V.I.D Hospital. Temperature in secondary chamber observed during inspection on 18.11.10 were 1145 C(at 3:15 PM), 1157 C(at 3:30 PM) and 1145 C(at 3:40 PM).

2. As decided in meeting held on 23.11.10 Letter for status w.r.t 5 points & observations during inspection about temperature in secondary chamber etc issued. 

3. As decided in meeting held on 09.03.11 Letter to DC (Civil Lines Zone ) with copy to Commissioner MCD, regarding compliance w.r.t 5 points & letter seeking  fresh monitoring report for incinerator issued. Hospital has submitted the flue gas analysis report along with analysis report of ash of incinerator (parameters meeting the prescribed limits) from empanelled lab. No reply from DC

4. As decided in meeting held on  27.09.11 Reminder to DC issued. 


1. Letters issued.

2. No reply from DC.

3.Hospital has submitted status w.r.t 5 points.

	4.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. EMG constituted.  
	Reminder


1. Letter issued.

2. Reply  received on 09.04.12. it was informed that work of ETP is under process & work of SWHS will be completed very shortly.

3. it was also informed that RWHS is not required as ground water table is above 6.00 mts below ground level

	4.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. No reply received.  
	Reminder for EMG & rest of the things.


Installed


1. Representative of the Unit attended personal hearing on 09.03.11 & informed that RWHS, SWHS & ETP has been installed. It was also informed that    piping   work for ETP is yet to be completed by PWD due to which ETP could not be made functional. As decided letter to principal secretary PWD with copy to Chief Engineer PWD for completion of the work related to ETP by April 2011 was issued.

2. As decided in meeting held on 27.09.11 Letter asking for Adequacy and test report for ETP issued. No reply received.


1. Letter issued.

2. Reply not received.

	3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued.  EMG constituted.
	Final reminder.

	24
	Jai Prakash Narayan Apex Trauma Centre, Ansari Nagar, Raj Nagar, New Delhi-29
	SW-131
	200
	Granted (valid upto 23.09.12)
	Applied on 17.06.11.
	Granted
	No information

	Constructed 18 pits.
	Installed
	1. As decided in meeting held on 27.09.11 Hospital was inspected on 30.12.11 . following were the observations: (i) BMW  bags found stored in open. Though isolated storage area provided but it was open from the top & no door has been provided. (ii) No. bio-hazard symbol provided
	Letter for rectification of deficiencies.
	1. Letter issued.
2.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. No reply received.  
3.However, reply w.r.t rectification of deficiencies & EMG not received.
	Reminder


1.As decided in meeting held on 27.09.11 letter for adequacy report of ETP & fresh application of CTO issued. Fresh CTO/Adequacy report for ETP not submitted


1. Letter issued.

2. Reply not received.

3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. Reply received w.r.t EMG.  

	4. As per the approval Hospital was inspected on 19.09.12. deficiencies observed were: (i) isolated storage site provided but bio-hazard symbols were not provided. (ii) etp/stp installed but non-operational. (iii) sewage was being discharg without any treatment.  (iv) hospital is having 2 DGSets of 775 KVA each. with inadequate stack height. (v) trolleys meant for transfer of BMW was not labeled & covered.                                       5.Directions of Hospital to CE,PWD, w.r.t point raised by DPCC official during said inspection received at DPCC.
	Letter for  rectification of deficiencies & fresh application of CTO.


Bhagwan

 Mahavir Hospital  , H – 4/5, Pitampura, Delhi -34.


Installed


1. As decided in meeting held on 09.03.11 Letter seeking fresh application for CTO and for status  w.r.t installation of ETP &  clarification from the hospital regarding water Table  in the area issued. Reply received on 14.09.11 regarding non-submission of CTO due to lack of NMR which was not provided by DPCC authorized lab.    

2. As decided in meeting held on 27.09.11 Letter seeking fresh application of CTO & status w.r.t 5 points issued.  


1. Letter issued.

2.  Hospital has applied for CTO & submitted NMR Report from empanelled Lab meeting the prescribed norms.                                                                           3. Reply received w.r.t ETP & RWHS.

	4.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. EMG constituted.  
	Letter seeking status w.r.t 5 points.


Granted

(for phase I & II )


Installed


1. There are two phases I&II for which CTE granted separately.

2.Authorization & CTO  Granted for phase I.

3.Letter issued seeking item wise compliance w.r.t Environmental Clearance for Phase II. 

4.As decided in meeting held on 27.09.11 Letter seeking  item-wise compliance of the Environmental Clearance conditions during the construction and the general conditions on an Affidavit and  an Affidavit  that it will follow the  conditions of Environmental Clearance  and  mention the date of start of construction and completion of construction, submit approved architectural drawing and  Completion Certificate issued.  Reply not received


1.Letter issued. 

2. Reply not received.

	3.Institute has applied for renewal of Authorization. Fresh NMR not submitted.
	Reminder


Installed


1. As decided in meeting held on 09.03.11 Letter seeking status w.r.t 5 points. & clarification from the hospital regarding Water Table in the area issued. Reply received on 03.06.11 informing that (i) Sanctioned amount issued to PWD.(ii)RWHS is not advisable since  water table is very high in the campus. (iii) SWHS has been installed by PWD.

2. As decided in meeting held on 27.09.11 Letter seeking status w.r.t 5 points issued. Reply not received. 

3. Three year of  CTO application dated 09.03.2009, has already been lapsed and hospital has not  submitted fresh CTO application . 


1. Letter issued. 

2. Hospital has submitted status w.r.t 5 points.  

	3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. No reply received.  
	Reminder for EMG & rest of the things.


Charak 

Palika Hospital,  Moti Bagh ,  New Delhi-21


Installed


1. Representatives of the hospital attended personal hearing on 19.01.12 and informed regarding rectification measures taken.


Representatives of the hospital attended personal hearing on 19.01.12 and informed regarding rectification measures taken and also informed that they will  submit fresh application for CTO within 15 days.

Ask for DG Set  status & Noise Monitoring Report.

+ Inspection

	
	 1. Letter issued.                                                                 2. Incomplete application of CTO received 'By Post' on 03.05.12.                                                               3. Hospital has submitted NMR of year 2009.                                                                                           4.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. EMG constituted.                                                       5. Hospital was visited however inspection could not be carried out due to non availablity of concerned officials.                                             
	Reminder  + Inspection to be expedited


1. As per decision on 25.11.2009, 24.02.2010, 15.06.2010 & 15.09.2010 various letter were issued to unit with respect to present status of compliance of 5 points and fresh application of CTO.

2. As per the decision final reminder issued. Reply received on 04.02.11 regarding compliance report and also informed that CTO application is under process.

3. As decided in meeting held on 09.03.11 Authorization & 

Letter seeking status w.r.t 5 points & CTO issued.  Reply /Letter received on 19.08.11 regarding status of 5 points and also sought status of CTO earlier applied on 28.09.2006.

4. As decided in meeting held on 27.09.11 & 19.01.12 reminder letter seeking fresh application for CTO & status w.r.t 5 points issued. 


1. Letter issued. 

2. Hospital has submitted status w.r.t 5 points .                                                              3. Hospital has replied w.r.t application of CTO that they have applied for CTO on 28.09.2006 , which is still pending & has requested to clarify whether the CTO shall be granted in absence of ETP.    

	4.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. No reply received w.r.t EMG.  
	Reminder for EMG & rest of the things.

	31
	Central Jail
 Hospital, Tihar, Delhi
	W-005
	240
	Applied on 20.09.12
	Not Applied
	Applied on 16.03.11
	Installed.
	Installed 
	Installed
	1..Hospital was inspected on 16.09.11 , Isolated site for storage of  bio-medical waste  not provided. Hospital has informed that Effluent Analysis has been conducted by Shree Ram Institute For Industrial Research.  Adequacy report for STP not submitted.
3. As decided in meeting held on 27.09.11 Letter for rectification of deficiencies and fresh application of CTO issued. Proper reply not received.
4. As per decision on 19.01.2012, another reminder issued but no reply/CTO application received.  
	Reminder
	1.Letter issued.                                                                                      2. Hospital has submitted that they have constructed the isolated site for BMW.
2.Not applied for CTO. 
3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. EMG constituted.                                                                         4. Hospital has applied for Authorization. 
	 Letter seeking application of CTO 

	32
	ESI Hospital, Shree Maa Anandmayi Marg, Okhla phase-1, New Delhi- 20
	S-012
	150
	Granted (valid upto 04.08.13)
	Not applied
	Granted
	under process
	under process
	Exempted by BMW Com-1. 
	1. As decided in meeting held on 09.03.11 Authorization issued. Hospital was called on personal hearing. Letter received on 30.05.11 regarding proposed expansion of ESI hospital.
2. Representatives of  the Hospital attended personal hearing on  27.09.11 . They were informed regarding the pending issues in respect of their hospital. Hospital will apply for Consent to Establish for the additional  284 beds proposed to be constructed letter w.r.t Consent to Operate for the existing Hospital and submit present status w.r.t SWHS, RWHS, CFL etc issued. Response not received.
3. As per decision on 19.01.2012, letter issued for sought application for CTE for additional 284 beds proposed to be constructed, CTO for existing hospital and status with respect to SWHS, RWHS & CFLs  etc,. No reply received.
	Letter seeking application for CTE for additional 284 beds proposed to be constructed, CTO for existing hospital & status w.r.t SWHS, RWHS, CFLs etc. 
	1.Letter issued.                                                                         2. No reply received.                                                            3. As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued.  E.M.G constituted.  
	Reminder

	33
	HAH Centenary Hospital  Jamia Hamdard, IHMMR Campus, Hamdard Nagar, New    Delhi-62
	S-009
	136
	Granted (valid upto 11.03.13)
	Applied on 30.05.11
	Applied on 14.03.11
	Installed
	Installed
	Installed
	1. Hospital is having ETP, SWHS, RWHS, CFLs etc and have applied for Authorization and CTO.
2. Adequacy report for ETP is required to be submitted. 
3. As decided in meeting held on 27.09.11 Letter seeking status of ETP issued. Hospital was inspected on 03.02.12. Bio-Medical Waste Management found satisfactory. ETP found installed.
4. As pre decision on 19.01.2012, authorization granted and letter for seeking adequacy report for ETP issued. 
	Authorization granted.

+ Letter seeking adequacy report for ETP.
	1. Authorization issued.
2. Letter issued.
3.Hospital has submitted Adequacy Report  & Test Certificate of ETP (of JMI , meeting the norms).
4.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. EMG constituted. 
	Letter seeking fresh NMR for DGSet(s).

	34
	Aruna Asaf Ali Hospital, 5 Rajpur Road, Delhi-54
	N-005
	100
	Granted
(valid upto 24.05.13) 
	Applied on 25.02.11
	Granted
	Installed.
	Not required
	Under process.
	1.Hospital has applied for renewal of CTO along with NMR  but the stack height of DG Set is less.
2. As decided in meeting held on 27.09.11 & 19.01.2012 letter for providing adequate stack  height for DG Sets send suitable reply w.r.t RWHS issued. Reply not received.
 No reply received.
	Reminder
	1. Letter issued. 
2. Reply received. 
3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. No reply received.  
	Reminder

	35
	Sanjay Gandhi Memorial Hospital, Mangolpuri ,Delhi
	NW-012
	300
	Applied on 01.05.12
	Granted (Expired on  18.03.12)
	Granted
	Installed
	Installed.
	Installed 
	1.Hospital has installed ETP, SWHS, RWHS etc and have submitted adequacy report for ETP.
2.Authorization and CTO have been granted to the hospital. 
	No Action
	1. Not applied for renewal of CTO. 
3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. No reply received.  
	Reminder

	36
	Lal Bahadur Shastri Hospital, Khichripur, Delhi.
	E-002
	100
	Applied for renewal on 28.04.10 
	Applied on 28.12.07 (3 years lapsed) 
	Granted
	Installed
	Installed
	Under process
	1. As decided in meeting held on 27.09.11 & 19.01.12 Reminder letter for   fresh application for CTO & status w.r.t 5 points &  informing hospital to apply for environmental clearance for the proposed up gradation / new construction issued. 
	Reminder + Also  seek fresh  application for  CTO.
	 1. Letter issued. 
2. Hospital has informed that they have approched National Productivity Council (NPC) for NMR & Stack Monitoring Report but gas analyser of NPC is not in working condition therefore, the said reports is still awaited                                                                                     3.Hospital has informed that due to unavialability of said reports they are not applied for CTO.
3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued.  EMG constituted.  
	Reminder

	37
	Nehru Homeopathic Medical College, Defense Colony, New Delhi-24
	S-013
	100
	Granted (valid upto 16.08.13
	Applied for renewal on 16.08.10
	Granted
	Installed
	Installed
	Matter with PWD.
	1.As decided in meeting held on 27.09.11 Reminder letter issued. Reply received. 
	Letter seeking present status .
	1. Letter issued. 
2. Reply not received. 
3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. No reply received.  
	Reminder

	38
	Ayurvedic Hospital, MCD, Haiderpur, Delhi-52
	NW-008
	100
	Not applied for renewal. (Last authorization valid upto 13.11.10)
	Not applied for renewal. 
	Granted
	Installed
	Under process
	Exempted being Ayurvedic Hospital
	1. As per the decisions letters & reminder seeking status of  RWHS & seeking application of CTO issued. Reply not received.
	Letter seeking application for CTO
	1.Letter issued.
2.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. No reply received.   
	Reminder

	39
	Babu Jagjeevan Ram M
memorial Hospital, Jahangirpuri, Delhi-33
	NW-009
	100
	Granted (valid upto  10.11.13)
	Applied on 25.11.11
	Granted
	Installed 
	Not recommended by CGWB
	Under process.
	1. As decided in meeting held on 27.09.11 Hospital was inspected on 05.01.2012. Bio-medical waste management found satisfactory. 
2. As per decision on 19.01.2012, authorization granted and letter issued for seeking present status w.r.t ETP. No reply received.
	Authorization granted

Letter seeking present status w.r.t  ETP
	1.Authorization  issued.
2.Letter issued.
3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued.                                                               4.No reply received.                                                                 5. Hospital has submitted NMR (of DPCC, meeting the norms).
	Reminder

	40
	Rao Tula Ram Memorial Hospital, Jafferpur, Delhi
	SW-003
	100
	Applied for renewal on 24.02.12
	Applied on
21.02.12 
	Applied on 21.02.12
	Installed.
	Installed
	Installed 
	1. As decided in meeting held on 09.03.11 Hospital was inspected on 02.05.11. following were the main observations: (i) Bio-Medical Waste found mixed in yellow bags. (ii) ETP installed but not found functional since 10 days due to cleaning. Reply received on 28.02.11 regarding compliance report along with the directions send to PWD (Elect.) regarding NMR, however CTE, CTO & NMR not received.
2.As decided in meeting held on 27.09.11 Letter to hospital for rectification of deficiencies and rest of the things  and D.O letter from Chairman, DPCC to Pr. Secy. (Health)  issued. 
3. Hospital has submitted application for Authorization  & CTO . Hospital has not submitted Water Analysis Report  from  approved Lab.
	Case to be taken up in next meeting.
	1. Hospital has submitted reply w.r.t rectification of deficiencies observed during inspection dated 02.05.11.               2. Hospital has submitted NMR of DGSets of 500 KVA.(of DPCC, meeting the norms)                                                                                             3.Hospital has submitted application for Authorization  & CTO .
4. Hospital has  submitted Water Analysis Report  (from Sigma Test & Research Centre, which is not authorized by DPCC). Therefore , application of CTO is not updated/entered online)                                                             4.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued.                                                                                   EMG constituted.
	Letter seeking Adequacy report & test report from empanelled consultant/Lab. 

	41
	Guru Gobind Singh Govt. Hospital, Raghubir Nagar, New Delhi-27
	W-006
	100
	Granted (valid upto 11.6.13)
	Applied on 29.07.11
	Granted
	installed
	Not recommended due to high water table. 
	Installed 
	1. As decided in meeting held on 23.11.10 letter seeking fresh application for CTO & status w.r.t 5 points issued. 
2.As decided in meeting held on 09.03.11 reminder letter issued. Hospital has applied for CTO  on 29.07.11 along with photographs of STP and NMR.  
3. As decided in meeting held on 27.09.11 Letter for  adequacy report for ETP issued.
4. As per decision on 19.01.2012, reminder letter issued. No reply received.
	Reminder
	1.Letter  issued.
2.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued.                                     3.No reply received.
	Reminder

	42
	ESI Hospital, Sector-15. Rohini, Delhi-85
	NW-010
	300
	Applied on 01.03.11
	Applied on 18.07.08
(3 years lapsed)    
	Granted
	Proposals received are under process.3
	 Estimates are under process
	Estimate received. Time was asked upto 31.03.10.
	1. Representatives of  the Hospital attended personal hearing on  27.09.11 however Medical Commissioner of ESI  could not attend the hearing. Representatives  informed  that the concerning issues were  pending  with  Head Office for necessary action. And as decided in the said meeting  Medical Commissioner of ESI, called upon  personal hearing .
	Representatives of the hospital and of the Medical Commissioner, attended personal hearing on 19.01.12 and informed the present status w.r.t 5 points etc.
Hospital to apply  afresh for CTO and to submit Time Bound action plan for  installation of ETP, SWHS & RWHS within 3 months .
	1. Letter issued . 
2. As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued.                                     3.No reply received.
	Reminder

	43
	Maharishi Balmiki Hospital, Pooth khurd , New Delhi-39
	NW-011
	100
	Granted (valid upto 29.01.13)
	Applied for renewal on 20.09.10 
	Granted
	Installed
	Not required since water table is high (5.20 mtr.)
	Installed 
	1. As per the decision Hospital was inspected on 31.05.11 main observation are: (i) Segregation  at emergency was not properly maintained. (ii) yellow bags were mixed with red bags at isolated site.  (iii) STP was not operational during inspection and it was not working since 4 days as informed by operator.  Hospital has submitted effluent analysis report (parameters meeting the prescribed limits) from empanelled lab. on 06.04.11. 
2. As decided in meeting held on 27.09.11 Letter for rectification of deficiencies &Adequacy report for STP issued. Proper reply not received. 
3. As per decision on 19.01.2012, inspection of the hospital was done on 21.02.2012 and the following were observed:
 (i) STP found functional but log book not maintained. 
4. Hospital has submitted reply on 04.04.12 w.r.t deficiencies observed during inspection on 31.05.11. It was informed that   (i) Proper segregation of BMW  is carried out.  (ii) Separate trolleys have been installed in the storage area for yellow & red bags

	Inspection
	1.Hospital was inspected on  21.03.12.. Following were the deficiencies: (i) STP found functional but log book not maintained. 

2. Hospital has informed that at the time of inspection the upgradation work of STP was in progress and as per PWD authorities same is likely to be completed by 31.03.12 with proper record. 
3.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued.  EMG constituted.
	letter seeking status  w.r.t STP/ETP. 

	44
	G.L. Maternity Hospital (MCD) , Ajmeri gate, Kamla Market, Delhi-6
	N-006
	107
	Granted (valid upto 30.5.13)
	Applied on 16.03.2012. 
	Granted
	Installed
	matter under process
	Installed
	1. Representatives of  the  Hospital attended personal hearing on  27.09.11 and informed  the present status. Hospital has not submitted application for renewal of CTO & Environmental Clearance for the proposed  up gradation /new construction . Hospital has submitted  present status w.r.t 5 Points
	Reminder
	1.Letter issued.
2.Hospital has applied for CTO on 16.03.12.  and submitted NMR for 125 KVA DGSet. (of DPCC , meeting the norms)
3. Reply w.r.t 5 points received. 
4.As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued.  EMG constituted.                              5.Hospital has submitted effluent analysis report (of DTU, meeting the norms). 
	Letter seeking status w.r.t RWHS. 

	45
	International Centre for Genetic Engineering & Bio Tech, ICGEB  Campus, P.O. Box  10504, Aruna Asaf Ali Marg, Delhi -67.
	SW-054
	   ---- 
	Applied for renewal on 09.03.2012
	Applied afresh on 17.01.12
	Granted
	Not asked for
	Not asked for
	Installed
	1.There is a High  Court case  WP( C) No. 6914 / 2011 “ Malvika Kaul Vs. GNCTD & ORS ”.  Ex. Engr(S –I)of DJB, on the basis of team inspection of site of Neela Hauz Water Body in Vasant Kunj area, dated 25.07.11 and Chief  Engineer (S) of DJB, has informed regarding discharge of waste water near the said water body from the premises of ICGEB . As decided , Show Cause Notice u/s 33(a) of the Water Act, was issued to the unit on 08.11.11.                 2.Reply to the said notice has been submitted by the unit  vide letter dated  24.11.11 informing that (i) ICGEB was reusing the effluent discharge for horticulture purpose within the premises (ii) there was no leakage of discharge from the STP (iii) Rise in the water level of Neela Hauz was resulting in backflow of water from the Huaz into ICGEB causing great inconvenience. 
3. As decided, inspection of the ICGEB was carried out on 17.01.12 and BMW management found satisfactory. STP  provided however found non functional ( to be repaired & revamped as decided by the centre) . Adequacy report sought by DPCC for STP is awaited. Waste water from the institute is reportedly  being used for horticulture purpose  with in the premises  a report of SIIR for the sample collected from final discharge point  on 16.12.11 indicates that  parameters are within the prescribed standards for discharge.
4. Copy of the Noise monitoring reports provided during the inspection shows that out of 5 DG Sets, 2 DG Sets ( 750 KVA each) are not meeting the prescribed standards. 
5.Reply received from the unit  w.r.t Show Cause Notice issued  to the unit u/s 33( A ) Water Act .Unit has replied that they have already  submitted the application of CTO & will submit application for authorization as the earliest.  
	Issue Directions u/s 33(A) of Water  Act to repair and revamp the STP and submit Adequacy report along with analysis report of the treated effluent,  within 3 months and to ensure that there is no effluent discharge from the institute into Neela Hauz Water Body .
Also ask the Institute to submit fresh Noise Monitoring Report for 2 DG Sets (of 750 KVA each) after taking corrective measures.
	1. Directions u/s 33 (A) issued on 16.02.12                                                                                           2.Institute has submitted that they have repaired & revamped the STP & have submitted effluent analysis report (of SIIR, meeting the norms) .        3. Institute has also submitted NMR of DGSets of 625 KVA (2 no.). (of SIIR, not meeting the norms).
	Letter seeking fresh NMR after taking corrective measures.

	46
	National Institute of Immunology,Aruna Asaf Ali Marg, New Delhi-67
	S-149
	nil 
	Granted( valid upto 30.04.13) 
	Applied on 13.02.09
	Granted
	 ………
	 ………
	matter under process (with consultant) 
	1. Inspected on 11.02.10.
• Incinerator closed down since July 2009.
• Dead animals are kept in deep freezer and disposal through CBWTF.
• BMW management found satisfactory.
2. . As decided in the meeting held on 24.2.10 a letter was issued for installation of ETP.
3. Followed by Reminder Reply received dated 11.8.10 stating that matter is with Consultant
4. As decided in the meeting held on15.09.10 letter was issued seeking present status w.r.t installation of ETP. Letter was received from the institute on 04.11.10 stating installation shall be completed within 6 -7 months tentatively.
5. Representative of the Unit attended personal hearing on 09.03.11 & informed that  matter regarding installation of ETP is  under process .unit given 4 months time for installation of ETP. . Letter received on 14.03.11 w.r.t ETP
6.As decided in meeting held on 27.09.11 Letter seeking status of ETP issued.
	Letter seeking present status w.r.t  ETP.
	1. Letter issued. 
2.Reply received stating matter of ETP is under process. 
	Letter seeking fresh application of CTO & status w.r.t ETP.

	47
	Govt. of Delhi Hospital. (200 Bedded) at Kokiwala Bagh, Ashok Vihar, Phase-IV, New Delhi-52.
	 ………
	 ………
	200 (proposed
	 ………
	Applied on 26.06.08.
CTE Granted on 22.09.08 for one year (Requested for Extension).
	 ………
	 ………
	 ………
	1. Hospital was inspected on 20.08.08 and it was found that
Construction of the hospital was not  started so far. Boundary wall/ fencing exist. Gate of the boundary found locked.
2. Vide letter dated 22.10.08, hospital was asked to file item-wise compliance of Environmental Clearance Conditions through an affidavit, however the same has not been filed by the unit so far.
3. Reply received on affidavit on 03.03.11, requesting to extend the CTE  for another one year.
4. Hospital has submitted item-wise compliance of Environmental Clearance given by MOEF through an affidavit on  28.02.2011. 
5. Request was received for extension of the CTE earlier granted  for  the Hospital
6.As decided in meeting held on 27.09.11 letter asking the unit to deposit fee for additional period (extended period) at the time of submission of application for Consent to Operate issued.
	Inspection
	1.Hospital was inspected on 19.03.12. Hospital was found under construction and will be completed by Sep., 2012.
	Letter seeking present status.

	48
	Institute of Human Behaviour & Allied Sciences, Near GTB Hospital, Dilshad Garden, Delhi-95
	NE-003
	190
	Granted (valid upto14.06.13)
	Granted (valid upto 24.07.14) 
	Granted
	Installed
	Installed
	Installed
	As decided in meeting held on 09.03.11 Letter  seeking status of ETP issued. Hospital has submitted Adequacy Report , NMR & ETP Test Report on 23.08.11 (parameters meeting the prescribed limits) from empanelled lab.
	No Action
	As per the common decision of BMW Committe No.1, in its meeting held on 18.04.12 letter w.r.t constitution of Environment Management Group (EMG) issued. EMG constituted.  
	No Action

	49
	All India Institute of Ayurveda, Gautampuri, Mathura Road, Sarita Vihar, Delhi-110076
	 ………
	200
	 ………
	 ………
	Applied on 11.04.12
	 ………
	 ………
	 ………
	This is fresh case of Ayurvedic Hospital to be constructed in plot area of 40530.76 sq.mts. of 200 beds.                                                                         2. proposed date of commisioning is 2013 (of phase only) . 
	 
	Applied for CTE on 11.04.12.
	Letter seeking item-wise compliance report of EC conditions.


	Sl.No
	Name and Address of Unit 
	Distt. No.
	Bed (No.)
	Authorisation Status
	CTO Status
	CTE Status
	SWHS Status
	RWHS Status
	ETP Status
	Brief Status 
	Decisions Recommended  in the Meeting on 
19.01.12
	ATR/Status
	Decisions Recommended  in the Meetingof Meeting 10.10.12

	4
	Sembramky Environmental Management  Pvt. Ltd
Khasra No. 83/22, Nale Wali Gali, Mundka Udyog Nagar, Delhi-41
	W-370
	CBWTF
	_______
	____
	Applied on 23.06.08
	__
	__
	__
	(1)  Applied for CTE on 23-06-08 for the Establishment of Common Bio-Medical Waste Treatment Facility (CBWTF) at Mundka.
(2)  The activity “ Hazardous Waste Processing viz.hospital/medical/industrial waste” is mentioned at sl no. 46 of the list of prohibited / negative list of industries (Annexure III) of MPD 2021.  As per  the note given in the said Annexure III a Public utility service involving any of the activities referred to above shall be permitted subject to environmental laws.  (3) Plot area for the said facility is one acre. (4) It is informed that all the required equipments like incinerator (Double Chamber) with venturi scrubber, autoclaves, shredder etc. shall be installed.  ETP shall be installed and treated effluent shall be reused. (5)  Letter was received from COI. informing that the  area for the site is not a conforming industrial area as on date. 
	Consent to Establish under the Air & Water Acts  Refused to the unit since present installed treatment capacity of  all the three CBWTFs( 43  Tons/Day) operating in Delhi is much more than the Bio Medical Waste generated in Delhi (10.125 Tons/Day as per Annual Report for Bio Medical Waste , for year 2010). 
	1. Letter issued.
	No action.Policy issue to be deallt separately. 

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 
	However for setting up BMW Treatment Facility in the area, DPCC may decide on its own level depending upon dire need of Delhi as well as, as per provision of MPD-2021 in consultation with DDA, if needed. (6)  Representations received from  the unit requesting for grant of CTE.                                                            (7)  Meeting with DDA, MCD & Industries Department officials was held on 4th & 8th march 2010 regarding permissiblity of the CBWTF considering the povisions of MPD-2021 particularly provisions for Redevelopment of unplanned industrial areas.A letter was  issued to DDAon10.03.10 seeking clarification on the issue. 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 
	Reply dated 06.04.10 was received from DDA mentioning " Those industrial units covered under public utility as per MPD-2021 but are involved with the processing and treatment of the hazardous waste may be allowed to continue provided they confirm to the environmental laws to be examined by DPCC concerned Environmental Body." The matter was put up in the file & as decided was placed before BMW Committee NO.1.                                                                                                                                     8. As decided in meeting held on 09.03.11  letter to DHS w.r.t draft policy on CBWTF issued. Response not received so far.                                                                       9. As decided in meeting held on 27.09.11  reminder letter to DHS w.r.t draft policy on CBWTF issued. Response not received so far.
	 
	 
	 

	5
	Shriram Institute for Industrial Research , 19, University Road, Delhi-07.
	N-069
	Research Institute
	Granted
(Valid upto 19.04.13)
	Applied on  27.03.12. 
	Granted
	Installed
	Installed
	Installed
	1.This is a case of Research Institute which is having animal house and generates BMW.
2.ETP installed & adequacy report submitted.                                                                                                            3.As decided in meeting held on 09.03.11   Institute was inspected  on 22.06.11 . Bio-Medical Waste Management was found satisfactory.                                                                                                                                                                                        4.  Institute has submitted NMR & stack monitoring report on 19.09.11
	Letter seeking application for renewal of CTO
	1. Letter Issued.                            2. Hospital has applied for CTO on 27.03.12.                   3.Hospital has submitted Adequacy Report (of DTU , meeting the norms) along with NMR & Stack Monitoring Report (SIIR).
	  CTO  granted

	6
	St. Stephen's Hospital Tis Hazari, Delhi-54
	N-002
	595
	Applied on 11.06.12 
	Applied on 21.11.11
	Granted
	Installed
	Representation received regarding high water table. Letter from CGWA submitted.
	Installed
	1. It was  informed that some portion of ETP is coming under the proposed bridge of MCD for which aeration tank will be demolished.
2. Letters were issued  seeking present status of ETP.                                                                                                                                                                                                                                                 3. As decided in meeting held on 19.01.12  Hospital was inspected on 07.03.12 . It was observed that no syringe cutter/niddle destroyer  used in the hospital, as it was informed that tips/niddles were removed from the syringes and kept in sealed plastic container and  thereafter hand over to CBWTF.                                                                                                                                                                            4. Hospital is having D Sets of 320 KVA (2 no.s) & 160 KVA (2 no.) . NMR submitted .
	Letter seeking fresh Adequacy  report for ETP.                         +  Inspection
	1.Letter issued.                                                    2. Hospital was inspected on  07.03.12 .                                           3. Hospital has applied for renewal of Authorization on 11.06.12.                                                              4.Hospital has submitted Adequacy Report  & test report for reconstructed ETP (of JMI , meeting the prescribed norm) 
	CTO & Authorization  to be  considered/granted after inspection as the hospital has reconstructed its ETP.

	7
	Batra Hospital & Medical Research Centre, 1, Tughlakabad Institutional Area,Mehrauli  Badarpur Road, Delhi
	S-005
	495
	Applied on 27.04.12
	Granted
(Valid upto 27.09.13)
	Granted
	Installed
	Installed
	Installed
	1.As decided in meeting held on 25.11.09 Hospital was inspected on 08.02.10 & 
(i) BMW Management found satisfactory.
(ii) ETP: found operational
2.Adequacy Report for ETP submitted on 22.08.10 
3.Flue gas analysis report dated 19.04.10, NMR dated30.04.10 & Effluent analsis report dated 25.04.2010 submitted.                                                       4.Hospital  vide letter dated 20.09.11 has submitted NMR from empanelled  Lab showing not meeting the prescribed standard for Insertion loss.                                                                                                                     5. As decided in meeting held on 27.09.11 Letter for rectification of deficiencies w.r.t accoustic enclosure for DG Set. Also seek fresh Noise Monitoring Report for DG Set has been issued.
	Reminder 
	1.  Hospital has applied for renewal of Authorization under BMW Rules                                2.                                                                        Hospital has submitted NMR (from  SIIR, meeting the prescribed norms).
	Authorization granted

	8
	Sir Ganga Ram Hospital, Rajender Nagar, New Delhi - 60
	C-005
	675
	Granted (valid upto 17.03.13) 
	Granted (valid upto 17.03.13) 
	Applied on 06.03.12
	Installed
	Installed
	Installed
	1.Hospital has applied for authorization under HWM Rules on 13.05.11.                                                                                                                     2.Hospital was inspected on 22.03.12. Bio-Medical Waste Management was found satisfactory.                                            3.The hospital has applied for "Expansion and modernization of the hospital" for which it has applied for Environmental Clearance  and also Consent to Establish.                  
	Inspection 
	1. Hospital was inspected on 22.03.12. Bio-Medical Waste Management was found satisfactory.                                                               2. Hospital has applied for CTE on 06.03.12                                      3.Hospital has submitted spore test report for autoclave and effluent analysis report from empannelled lab. meeting the prescribed norms.                         4.Hospital has submitted Environmental Statement for the period of 01.04.11 to 31.03.12.                                                                 5. Hospital has submitted Environment Clearance by SEIAA. 
	CTE   granted with condition that the unit  will submit   item-wise compliance of the Environmental Clearence conditions 

	9
	Society of Unique Hospital & Research Institute ( Multi Super Speciality Hospital & Research Institute)  Sector-19 Dwarka, Delhi.
	NW-414
	400
	…………
	____
	Granted (valid upto 20.10.10)
	__
	____
	___
	1.This is a case of New Hospital.The unit had applied for CTE on 14.07.06 & CTE has been granted. 
2.ETP (design capacity of 150KLD secondary and tertiary treatment) DG sets- 3 nos of 750 KVA capacity each (with acoustic enclosure) 3nos. oil fired boilers (1500Kg/hours). 
3.As decided in the meeting on 07.09.09 CTE was issued with the condition that acoustic enclosure shall be provided within a month.                                                                                                                                                                                                   4.Hospital has submitted compliance report  on 16.04.11   w.r.t letter issued on 05.04.11.                                                                                                                                                      5. As decided in meeting held on 27.09.11 Letter seeking clarification w.r.t    D G Set issued. Reply received stating height of D.G.Set of capacity 75 KVA is 4mts      
	Inspection 
	1. Hospital was inspected on 14.03.12. . Construction of hospital is complete and will start soon. 
	Issue letter for seeking extension of CTE, applying for CTO and for submission of  item-wise compliance of EC conditions.

	10
	Maharaja Agrasen Hospital, West Punjabi Bagh, New Delhi- 26
	W-003
	350
	Granted (valid upto 31.05.13) 
	Granted (valid upto 31.10.13) 
	Granted
	Installed
	Installed
	Installed
	1. Complaint received egarding pollution created by Genset. Hospital was inspected on 20.07.11 and BMW manegement found satisfactory  . Letter seeking Noise Monitoring Report for DG Sets issued.  Reply / NMR awaited.                                                                                                                                4. As decided in meeting held on 27.09.11  reminder letter seeking Noise Monitoring Report for DG Sets issued.  Hospital has submitted NMR. 
	Final Reminder 
	1. Hospital has submitted NMR & Effluent Analysis Report from approved lab. meeting the norms along with copy of log book for ETP.       
	Inspection

	11
	Jaipur Golden Hospital, 2, Institutional Area , Sector-3, Rohini, Delhi-85
	NW-003
	256
	Applied on 21.06.14
	Applied on 05.09.11
	Granted
	Installed
	Installed
	Installed 
	1.Hospital was inspected on 05.05.10 & BMW management was found satisfactory and work for ETP was under progress .It was informed that ETP will be completed within 3 months.
2. Construction for additional block near ETP was going on for O.T.  However not applied for CTE for this additional construction.                                                                                                                                                     3. Representative of the Unit attended personal hearing on 23.11.10 & informed regarding status of ETP. Letter was issued seeking Adequacy Report for ETP & application for CTE by 31st December 2010 .                                                                                                                 4. As decided in meeting held on 09.03.11 reminder has been issued to the hospital.  Reply received on 26.04.11 regarding installation and operation of STP.                                                                             5. Hospital has submitted Adequacy report for ETP.                                                       
	Authorization Granted .                 + Inspection for ETP installed
	1. Authorization  issued.                                        2. Hospital was inspected on 27.04.12. Following deficiencies were observed:   (i) BMW  was not properly stored at the isolated storage site. (ii) paramedical staff was unaware about handling BMW especially sharp waste.   (iii)  Stack height of  DG Sets (380 KVA & 1010 KVA) was inadequate.  (iv) Sharp Waste was disposed in plastic bags. (v) Segregation of BMW was not as per Schedule.                
	Letter for  rectification of deficiencies.

	12
	Escorts Heart Institute & Research Centre, 
Okhla Road New Delhi-25
	S-007
	310
	Applied on 06.06.12
	Applied on 11.05.11
	Granted
	Installed
	Installed
	Installed
	1.Hospital  was inspected on 19.05.10 & :
(i)BMWM found satisfactory.
(ii) ETP found operating.
(iii) Adequacy Report was to be submitted. Flow meter was to be installed for ETP.
2. As decided in meeting  on 15.06.10 Reminder for Adequacy Report of ETP & for installation of flow meter was issued.                                                                                                                3.Effluent analysis report of DPCC labdated 03.01.2011 submitted. Adequacy report from Jamia Milia Islamia submitted on 10.01.11.                                                                                                                                                     4.Hospital has submitted effluent analysis report on 09.08.11 . As decided in meeting held on 27.09.11 File was put up administratively.  Not meeting the norms w.r.t Stack emission for DG Set.                                                                                                   
	Letter  seeking fresh Stack  Monitoring Report for DG Sets after taking rectification measures.
	1. Letter issued.            2.Hospital has submitted stack monitoring report of DGSets (of SIIR , meeting the prescribed norms)                                                          Hospital has submitted Effluent Analysis Report.        3.A complaint was received on 26.07.12 regarding non functioning of pollution equipment & discharging of untreated effluent direct into public sewer. Hospital is yet to be inspected   
	Inspection to be expedited

	13
	Mata Chanan Devi Hospital, C-1, Janak Puri,New Delhi-58 
	W-004
	210
	Applied on 17.07.12
	28.09.10   (Renewal)
	Granted
	Under Process
	Installed
	Under Process
	1. Hospital was inspected on 11.11.10 & following were the main observations  :
(i) BMW management found satisfactory.
(ii) ETP found under construction &  reported that it will be completed within 3 months.
(iii)SWHS was yet to be provided.
(iv) RWHS, plantation & CFL done.                                                                                    4.) Reply dated 19.01.11 received informing that SWHS installation will be completed within a month.                                                                                                                               5.) As decided in meeting held on 09.03.11 reminder letter has been issued to the hospital seeking compliance report. Reply received vide letter dated  18.05.11  in which hospital has informed that compliance report will be submitted as soon as possible.                                                                                                                               6. As decided in meeting held on 27.09.11 Show Cause Notice issued.  Hospital has submitted  an Affidavit stating  work of ETP & SWHS shall be completed in 90 days.                                                                                                                              
	Letter asking the Hospital to complete the work in given time of 90 days.  + Inspectiobn
	1. Letter issued.             2. Hospital was inspected on 21.03.12. Bio-Medical waste management was found staisfactory. Construction of ETP has been completed approx. 80%                                          3. Hospital has submitted Adequacy report & test report (of DTU  , meeting the prescribe norms)      4.Hospital have 2 D.G.Sets of 625 KVA each and has submitted NMR of one DGSet (of DPCC, meeting the norms). 
	Authorization granted & Inspection thereafter. 

	14
	Rajiv Gandhi Cancer Institute &Research Centre, Sector-V, Rohini, Delhi-85
	NW-005
	241
	Applied on 21.05.12
	Applied on 13.04.10.
	Granted
	not installed
	Under Process
	Installed
	1.Hospital was inspected on 15.11.10 and following were the main observations : 
(i)BMW Management found satisfactory.
(ii) STP installed however  septic conditions were observed in primary settling tank,& other tanks which indicate proper cleaning of sludge is not being done. (iii) RWHS is to be provided (iv)Earlier installed SWHS removed & new SWHS is reported to be installed.                                                                                                                        2. As decided in meeting held on 23.11.10 Letter for rectification of deficiences  & also for SWHS & RWHS was issued. No reply received.                                                                                                                                 3. As decided in meeting held on 09.03.11 reminder letter has been issued to the hospital . Reply received.                                                            8. As decided in meeting held on 27.09.11 reminder  issued.                                                                                                                Reply received regarding rectification of deficiencies.  EC  received from Dr. Cetna Harzai during meeting of  BMW Committee No. 1 on 19.01.12.                                                                                    
	Letter seeking   item-wise compliance of the Environmental Clearance (given by SEAC) conditions  during the construction and the general conditions on an Affidavit within a month. Unit to also submit  an Affidavit  that it will follow the  conditions of Environmental Clearence  and  mention the date of start of construction and completion of construction, submitapproved architectural drawing and  Completion Certificate.                                                                                                                                               + Inspection  
	1. Letter issued.                                                                 2. Hospital was inspected on 27.04.12 During inspection following deficiencies were observed: (i) Improper segregation of BMW. (ii) Flow meter with ETP/STP was non functional.   (iii) stack height of 1250 KVA DGSet is inadequate. (iv) Records of BMW were not maintained.  (v) SWHS&RWHS were not provided. (vi) Staff was un educated about BMWM. (vii) bins for BMW have not proper label/color code/signs.  
	Letter for deficiencies,NMR & item-wise compliance of EC conditions.

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 
	 
	 
	(viii) hospital does not have isolated storage site forBMW with proper sign & labeling.                                                             3.Hospital has submitted action taken to rectify the deficiencies observed during the said inspection.                                                                                       4.  SWHS & RWHS shall be under taken along with expansion as expeditiosly as possible.                                                5. Hospital has DG Set of 1250 KVA  & 800 (2 No.s)  for which NMR is awaited.  
	 

	15
	Moolchand Hospital, Lajpat Nagar-III , New Delhi-24
	S-008
	256
	Granted (valid till 30.08.13)
	Applied on 04.08.10 (Renewal)
	Granted
	Installed
	Installed
	Under Process
	1.Hospital was inspected on 11.11.10 & following were main observations :
(i) Segregation of BMW found satisfactory.
(ii) Color coded bags found in use.
(iii) STP/ETP not installed neither any progress w.r.t  construction / excavation observed.                                                                                                                                           2.Hospital was called for personal hearing.                                                                   3. Representatives of the Unit attended personal hearing on 09.03.11 & informed that digging for ETP has been started & work of ETP is expected to be completed within six months. The unit will send monthly progres report w.r.t ETP and also an affidavit regarding completion of the work within six months. Affidavit received on 08.05.11 regarding completion of construction work of ETP within 6 months. Progress report of ETP received on 01.06.11 & 29.08.11.                                                               
	Letter for rectification of deficiencies & for status  w.r.t ETP. 
	1.  Letter issued.                                                      2.  Reply received on 28.June.12. hospital has informed that  work of ETP/STP will be complete by the end of 15 July 2012.                                   3. Hospital has submitted progress report of STP & informed  that STP will take 20-30 days to start. 
	SCN for closure u/s 5 of EP Act

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 
	4. As decided in meeting held on 27.09.11  Hospital was inspected on  22.12.11 . Following were the observations : (i) Segregation of BMW not found proper, general waste found mixed with incinerable waste.  (ii) color coded bins not found in use.  (iii) Bio-hazard symbol not provided on the bins and also on the isolated area.   (iv) STP found under construction . Hospital has submitted progress report of STP. 
	 
	 
	 

	16
	Shanti Mukund Hospital, 2, Institutional Area, Vikas Marg Extension, Delhi-92
	E-003
	144
	Applied on 15.09.10
	Applied on 15.09.10
	Applied
	Installed
	Installed
	Installed
	1..NMR submitted from RITES Limited which is not an approved laboratory from DPCC and results do not indicate Insertion Loss.     2.  Representative of the hospital Sh. G.S  Mathur, MS and Sh. N.K.Jain came during the meeting of the committee and given hearing on their request .They informed that    quotations for ETP  were invited however, due to lack of space, lot of changes required w.r.t shifting of pipelines  and also due to  high cost of ETP ,  the  work of  ETP could not be started  and requested for exemption from installation of ETP. 
	Inspection 
	Hospital was inspected on 16.03.12. During inspection it was observed that :  (1) D.G Sets of capacity 250 KVA (3 No.) & 225 KVA (4 NO.) are with inadequate stack height.  (2) Bio-Medical Waste management was not found proper. (3) color coded bags and containers were not found in use. (4)  Nurse (casualty) not aware regarding Bio-Medical Waste Management.    
	CTE   granted                                                                                                                                                                                                                                        Issue SCN u/s 5 of EP Act for rectification of deficiencies.

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 
	After hearing the representatives of the hospital and considering the information avialable in the records / inspection reports , representatives  of the hospital were  clearly told that ETP is to be installed as per the decision taken by DPCC & communicated to the hospital  through various letters / notices  in the past. Hospital will submit time bound action plan for installation of ETP & also submit  NMR for DG Sets . In case of non compliance  suitable action will be taken against the hospital and as decided letter issued. Hospital has submitted letter w.r.t pending issues of hospital.  Hospital replied stating that work of ETP has been executed and will be completed within two months                                      
	 
	(5) Isolated site (BMW storage site) not having Bio-Hazard symbol while it is observed that general waste storage site.    (6) Yellow bags and Blue bags were found in general waste. (7) Blue bags were observed  in black bags at general waste site.  (8) work of installation of ETP has been started in the hospital.                                                                                  Hospital has submitted Adequacy Report of DTU 
	 

	17
	Vidyasagar Institute of Mental  Health and Nuero Sciences, 1, Institutional Area, Nehru Nagar, New Delhi – 65
	S-011
	110
	Granted (valid upto 14.02.14)
	NA  (earlier expired on 
05.11.11)
	Granted
	Installed
	Installed
	Installed
	1 Adequacy Report for ETP submitted.
2. Hospital was inspected on 11.02.11 & following are the observations:
(i)ETP installed & found operational.
(II) Isolated storage area for BMW provided.
(iii) BMW segregation found satisfactory.              
	Letter seeking application for renewal of CTO.
	1. Letter issued.                                                   2. No reply received. 
	Issue SCN u/s 21/22 of Air Act and u/s 25 /26 of Water Act.

	18
	Brahm Shakti Hospital , U-1/78, Budh Vihar , Delhi – 86
	NW-013
	100
	Applied on 25.01.12.
	Applied on 02.04.12
	Granted
	Installed
	Installed
	Installed
	1.Hospital was inspected on 31.08.10 & following  deficiencies were observed:
(i)Sharp Waste Management not found proper.
(ii)Isolated storage site not provided.
(iii) Flow Meter not installed at the outlet of ETP.
(iv)Log Book for ETP not properly maintained.
(v)NMR required for D.G Sets.                                          
 2. Hospital was again inspected on 01.11.10 & BMW management found not satisfactory . ETP found operating                                                                                                                                                    3.As decided  in meeting held on 23.11.10 1, letter for rectification of deficiences  issued. Reply dated 30.12.10 received  informing that work for isolated storage site is under progress, photographs of Flow meter & NMR dated 23.11.10  submitted.                                                                                                                                                                                       
	Letter seeking fresh application for  Authorization & CTO 
	1. Hospital has applied for renewal of Authorization on 25.01.12.                                                                        3.Hospital has applied for CTO on 02.04.12 and submitted  Adequacy report and test report from JMI along with NMR ( meeting the prescribed norms) 
	CTO & Authorization to be granted and  inspection thereafter.

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 
	4. As decided in meeting held on 09.03.11 Letter seeking Final Adequacy Report for the ETP & also regarding completion of the work related to isolated storage site issued.  Reply  w.r.t rectification of deficiencies observed during inspection  received  along with Adequacy report & effluent analysis report from empanelled consultant shows parameters meeting the prescribed limits.                                                                                                                                                                                  5. Hospital has submitted Adequacy report for ETP. 
	 
	 
	 

	19
	R.L.K.C  Hospital ( A Unit of Dr. R.L.Khera Charitable Trust )   Pandav nagar, near . Shadipur Depot, Delhi 08
	W-341
	102
	Applied on 13.04.12
	Granted (valid upto 15.12.13)
	Granted
	Installed
	Installed
	Installed
	1.Hospital is having ETP , SWHS, RWHS, CFLs etc and have submitted adequacy report for ETP. Authorization & CTO have been granted to the hospital. 
	Letter seeking application for renewal of  Authorization.
	1. Letter issued.                                     2. Hospital has applied for authorization . Hospital is having DG Set of 380 & 320 KVA.         
	Authorization to be granted and  inspection thereafter.

	20
	Kukreja Hospital & Heart Centre, C-1, Vishal Enclave, New Delhi-27
	W-018
	103
	Applied on 12.10.11      
	Applied on 12.10.11       
	Granted
	Installed
	Installed
	Installed
	1.Representative of the hospital attended personal hearing on 27.09.11 and informed that application for renewal of  authorization and consent to operate  were filled up however, could not be submitted  since the concerned person left the hospital. The hospital will submit application for renewal of Authorization and Consent to Operate within 15 days.                                                                                                                                   2. Hospital has applied for renewal of Authorization & CTO.                              
	Inspection 
	1. Hospital was inspected on 06.03.12.Bio-Medical Waste Management found satisfactory.                               2. During inspection it was observed that RWHS is yet to be provided.                                          3. Representation has been received from the hospital informing that they have installed RWHS along with the photographs.
	CTO and Authorization granted and Inspection thereafter.

	21
	City Hospital,B-1/1, N.E.A. Pusa Road, New Delhi-60
	C-101
	120
	Applied on 29.03.12
	Granted (valid upto 29.12.13)
	Granted
	Installed
	Installed
	Installed
	1.Hospital is having ETP , SWHS, RWHS, CFLs etc and have submitted adequacy report for ETP. Authorization & CTO have been granted to the hospital. 
	Letter seeking application for renewal of Authorization. 
	1. Letter issued.                         2. Hospital has applied for renewal of Authorization on  29.03.12.  Hospital is having DGSet of 380 KVA. NMR not submitted.
	Letter for submission of  NMR

	22
	PCL-JRDC Joint Venture Ltd, Sector -8, Phase-1,Dwarka, Delhi
	SW
	300
	____
	___
	Granted 
	____
	____
	____
	1.The hospital has got Environment Clearence from SEAC.      2. As decided in meeting held on 27.09.11 Consent to Establish under the Air & Water Acts  issued with condition that the unit  will submit   item-wise compliance of the Environmental Clearance conditions during the construction and the general conditions on an Affidavit within a  month.   Unit to also submit  an Affidavit  that it will follow the  conditions of Environmental Clearance  and  mention the date of start of construction and completion of construction, submit approved architectural drawing and  Completion Certificate. CTE returned. 
	Contact the concerned person for  receiving of CTE. 
	Concerned person has been contacted still nobody came from the hospital to receive CTE.
	Inspection 

	23
	Delhi Heart and Lung Institute, 3-M.M II ,Panchkuian Road,Delhi-55
	C-089
	101
	Granted
(Valid upto 31.08.13)
	Applied on 05.01.12
	Granted
	Installed
	Installed
	Installed
	1.Hospital was inspected on 09.11.10 & following are the main  observation :
(i) BMW management found satisfactory.
(ii)Seperate Storage Room for BMW provided.
(iii) ETP found installed & Operational.                                                                                                                    2. Adequacy Report for ETP submitted                                                                                         3. As decided in meeting held on 27.09.11 Letter seeking application for renewal of CTO has been issued.  Hospital has applied for CTO.                                                                                                   
	Inspection 
	1. Hospital  was inspected on 06.03.12. Bio-Medical Waste Management found satisfactory.  Hospital is having DGSet of 500 KVA, have submitted NMR, (of DPCC, meeting the norms)
	CTO  granted

	24
	G.M.Modi Hospital and Research Centre for Medical Science, Mandir Marg, Saket , New Delhi -17
	S-010
	100
	Granted (valid upto 03.10.13)
	Granted (valid upto 07.10.13)
	Granted
	Installed
	Installed
	Installed
	1.Hospital is having ETP , SWHS, RWHS, CFLs etc and have submitted adequacy report for ETP. Authorization & CTO have been granted to the hospital.                                                                                2.Hospital has applied for Environmental Clearance to SEIAA and  a letter has been received from SEIAA.                                                                                                                                                                                                                                           
	Inspection 
	1. Hospital was inspected  on 20.03.12. Bio-Medical Waste Management found satisfactory.                  3.Hospital has submitted Effluent Analysis Report (of DTU , meeting the prescribed norms).
	Letter seeking copy of registration with DHS regarding number of beds .

	25
	Indian Hospital;AG-35 Shalimar Bagh, Delhi-88
	NW-419
	117
	Applied on 19.02.10
	Applied on 22.02.10
	Applied on 24.06.09
	Not Installed
	Not Installed
	Not Installed
	1.Hospital was inspectd on 15.11.10 & following  deficiencies were observed:
(i) Segregation of BMW not as per rules.
(ii)Isolated area for BMW  needs improvement.(iii) Bio Hazard symbol on containers not provided.(iv) SWHS, RWHS & ETP not provided.(v) No record for BMW maintained.                                                                                                                              2. As decided in meeting held on 23.11.10 letter for rectification of deficiences observed during the inspection issued .  Reply not received.
3. As decided in meeting held on 27.09.11 hospital has called upon personal hearing on 19.01.12. 
	No one from the hospital  came to attend the personal hearing  on 19.01.12.  Issue   Show Cause Notice  for refusal of  Authorization, CTE & CTO  and also Show Cause Notice  u/s 5 of EP Act for closure of the hospital and for disconnection of  Electricity & Water Supply to the Hospital.
	1.Show Cause Notice  issued.                                         2. No reply received.
	Issue Directions  u/s 5 of EPA for closure

	26
	Shri Ram Singh Memorial Hospital, B-26, East Krishna Nagar, New Delhi-51. 
	E-011
	100  (earlier have 27 beds)
	Applied on 03.03.10   
	Applied on 23.07.09
	Granted
	__
	__
	___
	1.Hospital was inspected on 08.11.10 & following  deficiencies  were observed:
(i) SWHS, RWHS, ETP not installed, plantation not done.
(ii)Separate  Storage site for BMW not provided. Segregation of BMW not as per rules.
(iii)Syringe Cutter/ Needle destroyer not provided.
(iv) Staff was unaware about segregation of BMW.
(v) Records for BMW Not maintained.                                                                                                                     4. As decided in meeting held on 23.11.10 letter for rectification of deficiences issued.  No reply received.                                                                  5. As decided in meeting held on 09.03.11 reminder letter issued . reply not received.                                                                                                          6. As decided in meeting held on 27.09.11 hospital has called upon personal hearing on 19.01.12
	Representative of the hospital attended the personal hearing on 19.01.2012 . Issue   Show Cause Notice  for refusal of  Authorization,  & CTO  and also Show Cause Notice  u/s 5 of EP Act for closure of the hospital and for disconnection of  Electricity & Water Supply to the Hospital giving 30 days time for compliance. 
	1. Show Cause Notice issued.                                       2. Reply received on 19.03.2012 stating that they have taken steps for rectification of deficiencies w.r.t BMW Rules and have requested for an inspection to check the same.
	Inspection

	27
	Nazar Kanwar Surana Hospital(A Unit of Bram Health Care (P) LTD), 219/220, N.K. Surana Marg, Gulabi Bagh, Delhi - 07
	N-095
	102
	Applied on 15.03.12
	Applied on 
05.01.12
	Applied on 30.01.12
	Installed
	Installed
	Installed
	1.As decided in meeting on 25.11.09 Show Cause Notice  u/s 5 of EPA was issued. Letter to DHS for de registration of the hospital issued.Reply received on 04.02.10 from DHS informing that Show Cause Notice has been issued  to the hospital for cancellation of provisional registration and later on vide letter dated 08.03.10 it was informed by DHS that DHS has cancelled the registration of the Hospital.
2. As decided in meeting held on 15.06.10 letter issued to the hospital that Application for Consent & Authorisation  become infructous since DHS has cancelled the registration of the  hospital vide letter dated 08.03.10.                                                                                                           3. Hospital was inspected on 11.11.10 and deficiencies were observed w.r.t BMW management.  Components /Parts of ETP (in dismantled condition )found lying in the adjoining plot .                                                                                                              
	Letter seeking fresh application for CTE & Authorization. 
	1. Hospital has applied for CTE & Authorization.             2. Hospital has submitted Adequacy report (of GGSIPU) , EffluentAnalysis Report & NMR (of DTU), meeting the prescribed norms. 
	CTE, CTO & Authorisation granted

	 
	 
	 
	 
	 
	 
	 
	 
	 
	 
	4. DHS has given fresh authorization to the hospital for 105 beds valid upto 31.03.2011.                                                                                                                                              5. As decided in meeting held on 23.11.10 letter issued to DHS  seeking clarification regarding registration certificate issued to the hospital .                                                                                                                                                                          6.It is brought to the notice that this hospital has taken over by the new management which got new registration from DHS for 105 beds (valid upto 31.03.11).  As decided in meeting held on 09.03.11 .  letter to DHS referring our earlier letter issued .
7.Letter seeking  fresh application for CTE, CTO & Authorization from the hospital issued. .Reply received from hospital regarding rectification of deficiencies in the form of affidavit. 8.                                                                                                                                                                                                     As decided in meeting held on 27.09.11 Hospital was inspected on 20.12.11 bio-medical waste management found satisfactory.
	 
	 
	 

	28
	Metro Hospital & Cancer Institute ( Earlier Anand Hospital,) 21, Community Centre, Preet Vihar, Delhi-92
	E-007
	155
	Granted (valid upto 27.05.13)
	Applied on 08.03.11
	Granted
	Installed
	Installed
	 Installed
	1. Representatives of the Unit attended personal hearing on 09.03.11 & informed regarding installation of ETP, SWHS, RWHS and also informed that applied for CTO on 08.03.11 . The unit will submit adequacy report for ETP & NMR for DG Set(s) within a month and also apply for CTE for additional 92 beds which have been added after the grant of earlier CTE by DPCC.                                                                   2.Complaint regarding excessive pollution created by  the hospital received & hospital was inspected & letter was issued to control noise. Reply received regarding rectification of deficencies on 08.08.11 along with photographs.
3.As decided in meeting held on 27.09.11 Consent to Operate not issued as hospital has not submitted the adequacy report for ETP. 
	Decision recommended on 27.09.11 reviewed. Issue letter seeking adequacy report for ETP.
	1. Letter issued.        2. Hospital has not submitted adequacy report.                               3. Hospital has informed that they have approached consultant for Adequacy Report. 
	SCN  for closure u/s 5 of EP Act for Adequacy Report. 

	29
	Action Cancer Hospital (A unit of Manav Sevarth Trust) FC-34, A-4, Paschim Vihar Delhi-63
	W-408
	150
	Granted (valid upto 22.03.13)
	Granted (valid upto 09.12.13)
	Granted
	Under Process
	Installed
	Installed
	1.Hospital is having ETP , SWHS, RWHS, CFLs etc and have submitted adequacy report for ETP. Authorization & CTO have been granted to the hospital.                                                                                                                      2. As decided in meeting held on 27.09.11 Letter seeking status of SWHS issued. Reply received stating SWHS is under process. 
	Letter seeking status/time frame for installation of  SWHS.
	1. Letter issued .                           2. Reply not received.    3.Hospital has submitted Effluent Analysis Report (of DTU , meeting the norms).
	Reminder letter for SWHS

	30
	Max Super Speciality Hospital ( A unit of Max Health care Institute limited.)     FC-50 Block C & D Shalimar Bagh Delhi-88 
	NW-406
	300
	Granted (Valid till 27.6.14)
	Granted (Valid till 27.6.14)
	Granted
	Installed
	Installed
	Installed
	 1. Hospital was inspected on 05.01.12 . Bio-Medical waste management found satisfactory.Hospital has submitted adequacy report of ETP from Empanelled consultants meeting the  norms.                                                                                                                                                                                        2. Hospital has got registration for DHS for 80 beds and has started operation since 12.11.11
	Authorization under BMW Rules  & Consent to Operate under Air & Water Acts, granted.
	1. Authorization & CTO issued. 
	Issue letter seeking  item wise compliance w.r.t EC conditions. 

	31
	"Shri Agrasen International Hospital" (of Shri Agrasen North EX Welfare Society (REGD) ) l, Plot no. - PSP, Sec - 22, Rohini,             New Delhi 85
	NW-
	455
	 ----
	 ----
	Granted
	 
	 
	 
	1. It is a fresh case of hospital.                                                                                                    2. Applied for CTE on 21.06.2011                                                                                                 3. Environmental clearance obtained by the hospital from SEAC vide letter Dated 30.05.11                                                                                                                                     4. The hospital is yet to start construction.                                                                                  5. Plot Area - 10000 Sq.meter, Built up Area-   35100 sq. meter.                                                                                                               6. Expected Date of start of Construction 2011.                                                             7. STP- 280 KLD, Water consumption- 398KLD, Waste (Water Discharge- 233 KLD)                                                                                                                         8. DG Sets - 2 X 1000 KVA , 1 X 500 KVA                                                                                 9. As decided in meeting held on 27.09.11 Consent to Establish under the Air & Water Acts  issued. 
	Letter seeking item-wise compliance w.r.t Environmental Clearance Conditions referring the CTE. Unit to also submit  an Affidavit  that it will follow the  conditions of Environmental Clearence  and  mention the date of start of construction and completion of construction, submit approved architectural drawing and  Completion Certificate.  
	1. Letter issued.                               2. Hospital has submit Architectural Drawings on  30.03.12.                                                         3. Hospital has submitted  item wise compliance of EC during construction on an affidavit & also informed that construction of building shall start on 01.04.12 & will complete in 31.04.14
	No Action

	32
	Madhukar Multispecialty Hospitals and Reaserch Center, C-4/35, Safdarjung Development Area, New Delhi - 16
	S-318
	125
	 ----
	 ----
	Granted 
	 ---
	 ---
	 ---
	1. Applied for CTE on 24-07-08.                                                                                                                                                                                   2.  Proposed date of commissioning 2010. 3. Reply dated 14.10.08 received informing: ETP will be installed at the time of construction. Noise monitoring will be sent after installation of DG sets. Applied for CGWA clearance.                                                                                                                                         3. SIT inspected on 29.10.08                                                                                                                                            4. Water Consumption- 105 KLD, Waste water- 75 KLD                                                                                                                             5. As decided on 30.10.08 CTE was issued on 11.11.08.(for one year valid upto 09.11.09)                                                                                                                                                       6. Hospital has requested vide letter dated 15.04.11 for Extension of Consent to Establish  up to November, 2012.                                                                       7. As decided in meeting held on 27.09.11  letter regarding  fee for additional period (extended period) at the time of submission of application for Consent to Operate.                                                                                             
	Inspection 
	1.Unit was inspected on 20.03.12. Hospital was found under construction. It will take about 1 year approx. 
	No Action

	33
	Bhagwati Hospital ( A unit of Sarvodaya Health Foundation (Regd.) Delhi), CS/OCF-6, Sector 13, Rohini, Delhi -85
	NW
	105
	Applied on 22.09.11
	Applied on 22.09.11
	Granted
	Installed
	Water Table is high 
	Installed
	1. Earlier  Hospital  was granted authorization for 30 beds . the hospital had applied for CTE, CTO  and for Authorization on  22.09.11 for 80 beds and later on vide letter dated 12.01.12 informed regarding increase of beds ( additional 25 beds) and also submitted additional fees for 25 beds. Informed that ETP proposed will be  for 105 beds.                                                                                                                           2.  As per application ETP shall be installed. Having 1000 Sq. Meter plot area & 1275 Sq.meter of Built up area.                                                                                                                      3.As decided in meeting held on 27.09.11 Letter seeking application for CTO &  installation of ETP, SWHS, RWHS, CFL &  Plantation issued. Letter  dated 12.01.2012 received regarding increase of beds from 80 to 105 beds and submitted additional fee for 25 beds.                                             
	Issue amended CTE for 105 beds.  + Reminder w.r.t 5 points. 
	1.  Amended CTE for 105 beds.  issued.                                    2. Letter issued.                                             3. Hospital has submitted Adequacy Report of STP  (of DTU) & effluent analysis report (of DPCC, meeting the norms). Hospital in its letter dated 15.4.2012  has stated that water table is high in area and they will submit a soil test report shortly. NMR has been submitted only for 1 DG Set out of 3 DG Sets.       
	Authorization granted  & letter seeking NMR of remaining DG Sets.

	34
	Dr. B.L.Kapur Memorial Hospital, Pusa Road, Delhi  05
	C-108
	300
	Applied 01.02.12.
	Applied on 09.11.11
	Granted
	Installed
	Installed
	Installed
	1.Adequacy report for ETP submitted on 29.12.09.
2.Unit was inspected on 21.04.10 & :
(i) BMW found satisfactory.
(ii) Isolated storage site provided.
(iii) ETP found operating & Treated Effluent is being used for horticulture  & cooling plant.                                                                                                        3. As decided in meeting held on 15.06.10 letter for installation of flow meter within 15 days.Reply received on 23.07.10 informing that 2 flow meters have been installed.                                                                                         4. Hospital has applied for renewal of CTO along with NMR (of two D.G Sets of 800 KVA ) , Effluent Analysis Report & Adequacy Report of ETP.                                                                                                                                                                                                         
	Letter seeking application for renewal of Authorization.         + Inspection 
	1. Hospital has applied for  Renewal of Authorization &  CTO.                                                                                                     2. Hospital was inspected on 22.03.12.  Bio-Medical Waste Management was found satisfatory.                                                                                   3. During inspection it was observed that hospital is having 2 D.G.Sets of 1010 KVA and 1 D.GSet of 500 KVA.                                                                                                                                                           4. Hospital has submitted  Adequacy Report of DTU  & effluent analysis report (of DPCC, meeting the norms)                                                        5. Hospital has submitted  NMR of DGSets & Stack Monitoring Report of stack attached to DGSets of 800 KVA each (of SIIR, meeting the norms). 
	CTO & Authorization granted and inspection thereafter

	35
	ALTIUS Sonia Hospital , 1, Gulshan Park, Main Rohtak Road, Nangloi, Delhi-41 
	W-376
	100
	Applied on 30.11.11
	Not applied
	Not applied
	  __
	  __
	  __
	Case was shifted from BMW Committee No. 2 to BMW Committee No. 1. Earlier the hospital is having 45 beds only. Hospital has applied for Authorization under BMW Rules with 100 beds.
	Letter  seeking application for CTE , CTO  within  30 days & for installation of  ETP, SWHS, RWHS, CFL & for Plantation within 3 months. Also ask the copy of registration with DHS.
	1. Letter issued.                                           2. Hospital has submitted NMR report for DG Sets from empanelled lab. meeting the prescribed norms.   
	Issue SCN for closure u/s  31 (A) of Air Act and u/s 33 (A) of Water Act. 

	36
	Hi-Tech Waste Solutions Pvt Ltd.,    5 , SSI industrial Area , GTK Road ,Delhi -33
	NW-
	CBWTF
	 -----
	 -----
	Applied on 10.01.12  
	  __
	  __
	  __
	1. It is a fresh case of operator of facility for Bio-Medical Waste (Common Bio Medical Waste Treatment Facility).                                                                                                                                                                                 2. Plot Area - 3000 sq. m. (On rent for 3 years ), Built up area-- 2000 sqm. .   Plot Exists in Approved Industrial area of SSI at G.T. Karnal Road, Delhi.                                                                          4.Proposed date of Commissioning-- May, 2012. Capacity -5- 6Tons/Day.                               5. Incinerator--2 No (250 Kg/Hr, with PLC),  Autoclave (2000 litre), Shredder (200-250 kg/Hr)                                                                                    6. ETP -- Shall be installed.  Trade  Effluent --  4.4 KLD                                                                                      7.DG Sets-- 82  KVA(one No) , Boiler - one (oil fired baby boiler).                                                                       8. ECS (Venturi Scrubber with Droplet Seperator shall be provided for Incinerator . Project Report submitted.                                                                                                                                          
	Consent to Establish under the Air & Water Acts  Refused to the unit since present installed treatment capacity of  all the three CBWTFs( 43  Tons/Day) operating in Delhi is much more than the Bio Medical Waste generated in Delhi (10.125 Tons/Day as per Annual Report for Bio Medical Waste , for year 2010). 
	1. Letter issued 
	No Action/ file closed

	37
	Holy Family Hospital, Okhla Road,Delhi-25.
	S-006
	298
	Granted (valid upto 21.06.13)
	Granted  (valid upto 11.10.13)
	Granted
	Installed
	Installed
	Installed
	A complaint was received on 26.07.12 regarding non functioning of pollution equipment & discharging of untreated effluent direct into public sewer. 
                                                                                                        
	  __
	1. Hospital  is yet  to be inspected. 
	Inspection to be expedited.

	38
	I.P Medical Corporation (Apollo Hospital) Ltd.,Sarita  Vihar , Mathura Road , New Delhi-44
	S-003
	615
	Applied for renewal on 19.06.12 
	Granted    (Valid upto 19.01.13)
	Granted
	Installed
	Installed
	Installed
	1.Hospital was granted consent to establish for additional 200 beds.and has been asked to apply for Consent to Operate for additional 200 beds as and when applicable.
2.Letter received on 13.01.10 requesting  to extend the earlier granted CTE for additional 200 beds by a period of one year. 
3.As decided in meeting held on 15.06.10 unit was asked  to deposit fee for 1 year(extended period) at the time of submission of application for Consent to Operate for additional 200 beds.                                                                                                                                                          4.As decided on meeting held on 09.03.11. hospital was inspected on 07.06.11. Bio-Medical waste management was found satisfactory. Hospital is having 4 DGSet of 750 KVA.   NMR  submiited .                                                          
	  __
	Hospital has applied for renewal of Authorization 
	Authorization granted.

	39
	Fortis Hospital  Ltd.  A- Block Shalimar Bagh, Delhi-88
	NW-434
	200
	Applied on 10.09.2012 
(earliar for 155 beds was valid upto 09.03.13)   
	Applied on 07.09.12
(earliar Valid upto 22.09.12) 
	Granted
	Installed
	Installed
	Installed
	as per the decision of the BMW Committee No.1 hospital was inspected on 01.04.11. Bio-Medical waste management found satisfactory. 
	  _______   
	1. Hospital has applied for CTO & Authorization.                                                        2. Hospital has submitted Adequacy report of ETP & effluent analysis report (of DPCC, meeting the norms) along with Stack Monitoring Report of DGSets of 1010 KVA (2 no.) (of SIIR, meeting the norms)                                                                                                                      
	Letter  seeking fresh Adequacy Report of ETP & copy of  registration with DHS. 

	40
	Yashraj Bio-Technology Ltd., C-34.Mulund (West), Mumbai-80 ( Correspondence. Add. -Plot No -C-232, TTC Industrial Area, MIDC, Navi Mumbai-400705)
	Mumbai
	NA
	04.05.12
	Not Applicable
	____
	__
	__
	__
	 The unit is engaged in collection and transportation of body fluids from the various hospitals in Delhi to its unit at Mumbai for further processing.
	__
	Unit has applied for renewal of Authorization under BMW Rules.
	Authorization granted with conditions regarding movement out of Delhi

	41
	Pushpawati Singhania Research Institute, Sheikh Sarai Ph-II , Press Enclave Marg, New Delhi-17
	S-014
	106
	Granted (valid upto 19.07.13)
	Applied on 14.09.12
	Granted
	Installed
	Installed
	Installed
	Unit was inspected on 08.02.10 & (i) Construction of STP was under process and BMW Management found satisfactory.
	__
	1. Institute has applied for CTR                                                               2. Institute has submitted Adequacy report (GGSIPU) , test report (dated 01.04.11) NMR & Stack Monitoring Report of boiler (of DPCC , meeting the norms)      
	CTO granted 

	42
	Jeewan Nursing Home & Hospital, 2-B, Pusa Road, New Delhi-05
	C-016
	100
	Granted (valid upto 25.10.13)
	Not Applied for renewal (earliar valid upto 08.10.12)
	Granted
	Installed
	Installed
	Installed
	1.Unit was inspected on 11.02.10 & following was observed:
(i)BMW management  found satisfactory.
(ii) ETP provided & found operational.
	__
	Not Applied for renewal of CTO 
	Letter for seeking application of Renewal of CTO u/s 21/22 of Air Act and u/s 25/26 of Water Act.


