MINUTES OF THE MEETING OF BMW COMMITTEE  NO. 1  HELD ON   14.07.08

The following officials attended the meeting:-
1.  Sh. J. K. Dadoo, Chairman, DPCC                                          --    in Chair

2.  Sh. K. Mahesh, Member Secretary, DPCC                              --   Member

3.  Dr. T. K. Joshi, COEH, MAMC                                                 --   Member

4.  Dr. Chetna Harjai , Scientist, Deptt of Env. GNCT, Delhi         --   Member

5.  Sh. D.K. Singh, EE (BMW), DPCC 

                        --   Member

6.  Sh. Sanjay Vatts AEE (BMW), DPCC 

                        --   Member

7.  Sh. Shyam Sunder, AEE (BMW), DPCC 

             --   Member

   

The  meeting of the  BMW Committee No. 1 ,  constituted  for deciding Application for grant of Authorization under the BMW Rules  and  Consent under the  Air / Water Acts was held  on 14.07.2008 . 12 agenda items were taken & discussed by the Committee and   decisions taken are given  below :  

1.Decisions taken w.r.t. Agenda No 1 (Total   52 Cases ,Govt. Hospitals (51 cases)    &  Govt. Research Institute (one case at S.No. 46 ) ) are at Annexure 1 .

2.Decisions taken  w.r.t. Agenda No.2 ( Total  74 Cases , Private Hospitals (59    cases), Common Operator of BMW Treatment Facility(2 Cases at S.No.57 & 58),    one case  of Collector & Transporter of  BMW ( Yashraj Bio- Technology Ltd at    S.No. 56), two cases of Research Institute ( S.No. 62 & 73) , 3 cases of    Pharmaceutical / Drugs manufacturing(S. No. 59,60 & 61) & 7cases ofDrug  Stocki   st (storage & Distribution) (S.No. 63 to 69) are at   Annexure2. 
3.Decisions taken w.r.t Agenda No. 3 (Cases of 510 Health Care Units wherein    Show Cause Notices and reminders were issued earlier to apply for authorization    under BMW Rules) are at  Annexure  3 . 

4.Decisions taken w.r.t Agenda No.4 (regarding letters issued for acoustic enclosure,   noise monitoring report for DG sets, affidavit for compliance,in respect Health Care   Units / Nursing Homes) are at Annexure 4.
5.Decisions taken w.r.t Agenda No.5 ( Drug Manufacturing  Units,  Approved Testing    Laboratories &  Blood Banks , based on the Lists collected from the Drugs      Controller of GNCT Delhi ) are at Annexure 5.
6.Decisions taken w.r.t Agenda No. 6 (i) Proposal received from Dr. T.K.Joshi for     Study on the Lead  (iii) Proposal received from Dr. T.K.Joshi for Study on the    effect of  Mercury waste are at Annexure 6.
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 7.Decision taken w.r.t Agenda No.7(Management of Sharp Waste)is at Annexure 7.
 8.Decision taken w.r.t Agenda No.8 ( News Paper Item “Bio – medical waste     plagues NCR” published in Times of India (Delhi Edition) on  5th May, 2008     regarding Training through  ASSOCHAM) ) is at Annexure 8.
9.Decision taken w.r.t Agenda No.9 (Surveillance/Monitoring of Health Care Establis     hments in Delhi),  is at Annexure 9.
10.Decision taken w.r.t Agenda No.10(Case  of M/s Jagat Diagnostic Pvt. Ltd. B -82,       G.T.K. Road Industrial Area,  Delhi-33) is at Annexure 10.
11.Decision taken w.r.t Agenda No.11 (Complaint  against Ayurveda Kendra , B- 5/       99 , Safderjang Enclave , New Delhi -29) is at Annexure 11.
12.Decision taken w.r.t Agenda No.12 (Service Charges for Bio Medical Waste Man      agement by the  Operators  of Common Bio Medical Waste Treatment Facilities      in Delhi) is at Annexure  12
Where ever inspections have been decided by the BMW Committee No. 1, the same shall be conducted by a 4 member team consisting of  (i)Dr. T.K.Joshi (ii) Dr. Chetna Harjai  (member from the Environment Deptt. Govt. of NCTDelhi) (iii) EE (BMW Cell)
(iv) Trainee in BMW Cell. In case Dr. Chetna Harjai is not available, the  inspections shall be carried out by the remaining members of the said team.

The next meeting of the BMW CommitteeNo.1 will be held on 27.08.2008 at 3 : P.M.
             The meeting ended with a vote of thanks to the Chair.
	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	1.
	Lok Nayak Hospital, New Delhi-2
	1600


	C-001
	12-Jan-04
	03-Mar-08 
	1. Authorization is valid up to 18-2-2010.

2. SCN u/s 21/22 of Air Act was issued on 6-3-2007(C/241) and on 11-6-2007(C/243) but HCU did not reply to the SCN u/s. 21/22 of Air Act received.

3. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Pr. Secy  (Health).

4. Complaint received regarding mismanagement of BMW.

5. Balance Fee for Rs. 496500 not received.

6.  Meeting taken by Pr. Secy. (Health) on 25.09.07, it was decided that MS of the Hospital should submit Consent application within 15 days. 

7. vide letter dated 28.07.06 & 7.12.06  it was informed that  ETP will be completed by end of Feb.07. However, present status w.r.t. ETP not provided. 

8. Noise Monitoring Report for DG sets received from DPCC Laboratory shows Insertion loss meeting the norms. 

9. EE(BMW) talked to the official of the hospital as decided on 15.11.07. 

10.  Applied for Consent to operate on 03.03.08.

11.  As decided in the meeting on 18.03.08, letter for deficiencies was issued. 

12.  As per the general decision taken on 06.05.08, letter issued.
13. Hospital was inspected w.r.t News Paper Clipping & also reference was received from Hon’ble Lt. Governors office . Incinerator & Autoclave etc. were 
also inspected. Air Pollution Control  Device ( APCD) installed with the incinerator was found not operational. By pass system found existing for the discharge of the emissions of the incinerator. Acoustic Enclosure / acoustic treatment of the rooms where DG Sets are kept  not provided  & adequate stack height not provided for the DG Sets installed at various locations in the hospital. ETP is yet to commissioned. 
14. Reply  Letter  sent  to Lt. Governor’s  office. 




	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .


	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals.  
	Common letter prepared & submitted. To be issued after approval. 
	Call on 27.08.2008



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	2.
	Guru Teg Bahadur Hospital, Shahdara , Delhi-95


	938
	NE-001
	22-May-07
	19-Dec-07
	1. Authorization is valid up to 18-2-2010 (C/234).

2. SCN u/s. 21/22 of Air Act was issued on 6-3-07(C/233) and 11-6-07(C/237) but HCU did not submit any reply.

3. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Pr Secy  (Health).

4.  Meeting taken by Pr. Secy. (Health) on 25.09.07, it was decided that MS of the Hospital should submit Consent application within 15 days.  

5. A meeting was also taken by Pr. Secy. (Health) on 25.10.07 regarding installation of ETP .

 6. EE (BMW) talked to the official of the hospital as decided on 15.11.07.

7. Consent to operate  application received however noise report for DG Sets &  stack monitoring report for Boiler  not submitted. 

8 . As decided in the meeting on 18.03.08, letter for deficiencies was issued..

9.Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

10.Reply not  received


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .


	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals. 
	Common letter prepared & submitted  . To be issued after approval.
	Call on 27.08.2008



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	3.
	Deen Dayal Upadhya Hospital, Hari Nagar, New Delhi-64
	500
	W-002
	13-Oct-04


	16-Jan-08
	1. SCN u/s 5 of EPA was issued on 6-3-2007(C/282) but HCU did not submit any reply.

2. SCN u/s 21/22 of Air Act was issued on 6-3-2007(C/281) and on 11-6-2007(C/283) but HCU did not submit any reply.

3. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Pr Secy  (Health).

4.  Meeting taken by Pr. Secy. (Health) on 25.09.07, it was decided that MS of the Hospital should submit Consent application within 15 days. 

5. EE (BMW) talked to the official of the hospital as decided on 15.11.07.

6. Applied for Consent to Operate on 16.01.08

7. As decided in the meeting on 18.03.08, letter for deficiencies was issued.
8. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

9.Reply not  received.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .


	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals.  
	Common letter prepared & submitted  . To be issued after approval.
	Call on 27.08.2008



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	4.


	Charak Palika Hospital,  Moti Bagh ,  New Delhi-21
	150


	ND-003


	09-Jun-06
	Not Applied
	1. Reply to SCN u/s 5 of EPA received with the remarks that all the deficiencies mentioned in SCN have been rectified (C/202).

2. SCN u/s 21/22 of Air Act was issued on 16-3-207(C/201) and on 11-6-2007(C/203) but HCU did not submit any reply to SCN.

3. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Chairperson, NDMC.

4. Reminder letter issued on 28.09.07, however reply / consent application not received.

5 EE (BMW) talked to the official of the hospital as decided on 15.11.07. However not applied for consent under the Air Act.

6. As decided in the meeting on 18.03.08, letter for deficiencies was issued.
7. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

8.Reply dated 19-06-08.w.r.t letter dated 26-05-08 received  informing about doing the needful as directed.



	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .Reply  received
	Letter from Chairman, DPCC to Chairman NDMC.


	Letter Issued. 
	Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	5.
	Ram Manohar Lohia Hospital, Baba Kharak Singh Marg ND-1
	1000
	ND-002


	29-Jun-06
	20.09.07
	1. Authorization is valid up to 18-02-2010 (C/183).

2.. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Jt. Secy  (Health), GOI..3. Reminder letter was issued for consent application & applied for consent to operate on 20.09.07.

4..  Deficiencies observed w.r.t. consent application received e.g. noise monitoring report of all the DG sets not submitted & it also not clear that all the DG sets are having acoustic enclosure & as well as adequate stack height. Stack monitoring report of the boilers (2nos.) not submitted. Affidavit submitted is not proper. HCU has requested for review of the decision taken for installation of ETP referring the prescribed standard under EPA.. 

 5. Noise Monitoring Report for DG sets received from DPCC Laboratory shows meeting the norms. 

 6..  As decided in the meeting on 18.03.08, letter for deficiencies was issued.. 
7.. Letter submitted on 22.5.2008 enquiring that whether installation of ETP is required or not.
8.. Letter issued on  26.05.08 regarding ETP , rain water harvesting , solar water heating systems etc as per the decision taken on 06.05.08.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Letter submitted on 22.5.2008 enquiring that whether installation of ETP is required or not.

EE(BMW)  talked to the official (s)

of the hospital .


	A common letter be sent to Jt. Secretary (Health), GOI with copy to D.G. (CPWD), from Chairman, DPCC  as per the general decision taken for Central Government Hospitals
	Common letter prepared & submitted  . To be issued after approval.
	Call on 27.08.2008



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	6.


	G.B. Pant Hospital, J.L. Nehru Marg, New Delhi-2 


	601
	C-002


	30-Jun-06
	26.09.07
	1. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Pr Secy  (Health).

2. Complaint received regarding mismanagement of BMW.

3.. Applied for consent under Air Act on 26.09.07, however stack monitoring of boiler not submitted. Acoustic enclosure has not been provided for all the DG sets.

4.. As per application ETP was under construction & was expected to be completed by 31.07.07. However information not provided regarding commissioning of ETP.

5..  As decided in the meeting on 18.03.08, letter for deficiencies was issued. 

6. Letter has been received requesting to issue clearance certificate to operate the incinerator.
7. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

8..Reply dated 02-07-08.having point wise reply w.r.t letter dated 26-05-08 received.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Letter has been received requesting to issue clearance certificate to operate the incinerator.

EE(BMW)  talked to the official (s)

of the hospital .


	Inspect and report in next meeting.
	To be inspected.
	Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	7.


	Northern Railway Central Hospital, Medical Director, Northern Railway Basant  Lane

 New  Delhi-55
	312
	C-006


	25-Aug-06
	19-Nov-07
	1.. Application received for consent however Stack monitoring report for the Boiler & Noise Monitoring report for DG Sets not submitted. 

2. As decided in the meeting on 18.03.08, letter for deficiencies was issued. 
3. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

4..Reply dated  11-06-08 w.r.t letters dated 21-04-08and 26-05-08 regarding doing the needful as directed was received.

5..Asked to submit a list of authorized agencies by DPCC in order to process installation of ETP in hospital .
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .
	Call on 14.07.2008
	
	Supply list of empanelled consultants and direct them to comply with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008. Call on 27.08.2008.



	8.
	Guru Nanak Eye Centre, Maharaja Ranjit Singh Marg , New Delhi
	184


	C-003


	11-Sep-06
	30-11-06
	1. Authorization is valid up to 18-2-2010(C/157).

2.. Application for consent under Air act is received.

3. Noise report shown that Insertion Loss was not as per norms.

4. Meeting taken by Pr. Secy. (Health) on 25.09.07, HCU was directed ( in the meeting) to comply with norms/standards prescribed for DG Sets and submit compliance report along with the Noise Monitoring report to DPCC. However compliance report/fresh noise monitoring report not received.

5. As decided in the meeting on 18.03.08, letter for deficiencies was issued. 

6. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

7.Copy of communication with PWD regarding Noise monitoring report  submitted.
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital . Reply  received

	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals.. 

Call on 14.07.2008
	Common letter prepared & submitted  . To be issued after approval.
	Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	9.


	E.S.I. Hospital , Basai Darapur,Ring Road , New Delhi-15
	600


	W-001


	30-Nov-06
	Not Applied
	1. Authorization is valid up to 18-2-2010(C/99).

2. SCN u/s 21/22 Air Act was issued on 11-6-2006 (C/103).

3. HCU submitted the reply on 13-6-2006(C/106) with the remarks that they have deposited the fee for noise monitoring and intent to apply under Air Act.

4. DO letter was issued to J.S (Labour), GOI with a copy to DG, ESI, reply received from DG ESI, however consent application not received.

5 EE (BMW) talked to the official of the hospital as decided on 15.11.07. However not applied for consent under the AIR Act.

6. As decided in the meeting on 18.03.08, letter for deficiencies was issued.
7. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

8. Letter dated 19-06-08 was received.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .
	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	EE(BMW) to chase up. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	10.


	All India Institute of Medical Science, Ansari Nagar, New Delhi-29
	1596
	S-001


	28-Dec-07
	Not Applied
	1. SCN for refusal of authorization was issued on 21-2-2007(C/204).

2. Reply to SCN u/s 5 of EPA received with the remarks that necessary instruction for strict compliance of the statutory provisions have been issued to concerned officer (C/207).

3. HCU was inspected on 8-8-2007(C/212) during which various deficiencies were observed regarding BMW management

4. DO letter issued to Director AIIMS with copy to JS (Health) GOI on 03.10.07 reply / Consent application not received.

5 EE (BMW) talked to the official of the hospital as decided on 15.11.07. However not applied for consent under the Air Act.

6. As decided in the meeting on 18.03.08, letter for deficiencies was issued. 
7. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

8.Reply dated 11-06-08.w.r.t letter dated 26-05-08 received informing about doing the needful as directed.  


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .

	A common letter be sent to Jt. Secretary (Health), GOI with copy to D.G. (CPWD), from Chairman, DPCC  as per the general decision taken for Central Government Hospitals 

EE to chase up. Call on 14.07.2008.
	Common letter prepared & submitted  . To be issued after approval.

EE(BMW)  talked to the official (s)

of the hospital .


	Call on 27.08.2008.



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	11.
	Safderjung Hospital, Aurobindo MargNew Delhi-29
	1531
	S-002


	05-Mar-07
	13-09-05
	1. Authorization is valid up to 30-01-2010(C/268).

2. SCN u/s 21/22 of Air Act to submit noise monitoring report of DG sets was issued on 21-06-2007 (C/275).

3. Noise monitoring report of D.G. sets yet to be received.

4. DO letter issued to JS (Health) GOI on 03.10.07.

5. As decided in the meeting on 18.03.08, letter for deficiencies was issued.
6. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

 7.Reply  not received.
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .
	A common letter be sent to Jt. Secretary (Health), GOI with copy to D.G. (CPWD),from hairman, DPCC as per the general decisiontakenfor Central Government Hospitals EE to chase up. Call on 14.07.2008.
	Common letter prepared & submitted  . To be issued after approval.

EE(BMW)  talked to the official (s)

of the hospital .


	Call on 27.08.2008.

	12.
	Aruna Asaf Ali Hospital, 5 Rajpur Road, Delhi
	100
	N-005


	11-Aug-04
	18.09.07
	1. Authorization is valid up to 30-01-2010 (C/186).

2. Applied under Air Act on 18.09.07. Acoustic enclosure with the DG set provided, however noise monitoring report not submitted. 

3. As decided in the meeting on 18.03.08, letter for deficiencies was issued..

4. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

5. Reply not  received.

	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .

	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals.  
	Common letter prepared & submitted  . To be issued after approval.
	Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	13.


	Sanjay Gandhi Memorial Hospital, Mangolpuri ,Delhi


	100
	NW-012
	30-Nov-04
	27.04.04
	1. SCN under BMW Rule was issued on 21-2-2007(C/80).

2. Consent under Air Act expired on 26.04.07. 

3. Reply to SCN u/s 5 of EPA received with the remark that corrective measures have been taken(C/81).

4. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Pr Secy (Health).

5. Meeting taken by Pr. Secy. (Health) on 25.09.07, HCU was directed (in the     meeting) to inform DPCC about the rectification measures. 

6.. Three years expired after the submission of the earlier consent application;     however HCU has not applied afresh for consent under the Air Act.

7. Talked to the official of the hospital as decided on 15.11.07. However not    applied a fresh for consent under Air Act.

8. As decided in the meeting on 18.03.08, letter for deficiencies was issued.
9. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

10.Reply dated 16-06-08.w.r.t latter dated 26-05-08.regarding doing the needful as directed was received.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .


	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals. 

  
	Common letter prepared & submitted  . To be issued after approval.
	Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	14.
	Vallabhai Patel  Chest Institute, University of Delhi, PO-Box.No-2101, Delhi-7
	60
	N-007


	14-Dec-04
	10.09.07
	1. Authorization is valid up to 30-01-2010 (C/31). 

2. HCU has applied for consent to operate under Air Act on 10.09.07.   Noise Monitoring Report received  , shows meeting the norms. 

5 As decided in the meeting on 18.03.08, letter for deficiencies was issued. 
6.Reply not  received.
	EE(BMW)  talked to the official (s)

of the hospital .


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	EE(BMW) to chase up. Call on 27.08.2008.

	15.
	Dr. B.R. Sur Hemopathic College & Hospital, Nanakpura, Moti Bagh, New Delhi-22
	50
	SW-038


	22-Feb-05
	24.10.07


	1. Authorization is valid up to 30-10-2010(C/46).

2. SCN u/s 21/22 of Air Act was issued on 11-6-2007(/47) but HCU did not apply under Air Act.

3. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Pr Secy  (Health).

4.  Meeting taken by Pr. Secy. (Health) on 25.09.07, it was decided that MS of the Hospital should submit Consent application within 15 days. However Consent Application under Air Act not received so far. 

 5. HCU applied for consent under Air Act on 24.10.07. Noise Monitoring Report for DG Sets submitted. Shows meeting the norms. 

6. As decided in the meeting on 18.03.08, letter for deficiencies was issued.
7.Reply not received..                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                                


	EE(BMW)  talked to the official (s)

of the hospital .


	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals. 

EE to chase up. Call on 14.07.2008.
	Common letter prepared & submitted  . To be issued after approval.

EE(BMW)  talked to the official (s)

of the hospital .


	Trainee to visit and persuade MS of the Hospital to apply quickly. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	16.


	Rajan babu Hospital,  GTB Nagar, Kingsway Camp,Delhi-9pital, 
	1155
	NW-001


	02.Aug-05
	13-Nov-07
	1. SCN under Rules 7 of BMW Rules was issued on 21-2-2007(C/142) and 11-6-2007(C/142). Reply received informed regarding corrective measure taken w.r.t BMW management. 

3. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 & 01.10.07 to Addl. Commissioner, MCD./ Commissioner MCD., seeking consent application under Air Act.4. Letters/ Several representations requesting permission to operate the Incinerator for trial testing. Since Hospital has installed APCD after issuance of Directions u/s 5 of EP Act issued on 17.04.06 (c/112). Application received for consent however, noise monitoring report for DG Sets not submitted. 5. A letter on 08.01.08 received, requested to allow to operate the plant on trial testing.

6. Applied for Consent to Operate under Air Act. 

7. HCU is having 2 No 320 KVA DG Sets Without Acoustic Enclosure.   Unit has submitted a letter requesting to grant permission to run its incinerator on regular basis as APCD  has been installed.

8. As decided in the meeting on 18.03.08, letter for deficiencies was issued.

9.  Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

10.Reply received dated 12-06-08.w.r.t letter dated 26-05-08.informing about doing the needful as directed .
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .


	Inspect and report. Call on 14.07.2008.
	To be inspected.
	Call on 27.08.2008.



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	17.
	E.S.I Hospital, Jhilmil, Delhi-110095
	250
	E-001


	03.07.07
	14-Mar-08
	1. Authorization is valid up to 7-3-2010 (C/132).

2.. Applied for consent under the Air Act on 14.03.08 along with Noise Monitoring report of both DG sets of 312.5 and 180 KVA.  As per the report the insertion loss meeting the prescribed norms. Stack monitoring report of the boiler not submitted.

3. As decided in the meeting on 18.03.08, letter for deficiencies was issued.
4. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

5.Letter dated 10-06-08 requesting for no objection certificate for installation of x- ray unit at hospital received.

	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d) ETP (e) Plantation of trees along side of the periphery of the Hospital building. Letter dated 04.06.08 has been received wherein HCU has requested for issuance of NOC of X-Ray Unit.

EE(BMW)  talked to the official (s)

of the hospital .


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	Trainee to visit and persuade MS of the Hospital to apply quickly. Call on 27.08.2008.



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	18.
	G.L. Maternity Hospital (MCD) , Ajmeri gate, Kamla Market, Delhi-6


	97
	N-006


	24-Apr-07
	Applied
	1. Authorization is valid up to 30-5-2010(C/82).

2. Applied for Consent to establish & Consent to Operate ON 17.06.08.

3. Paid balance fee of Rs. 17800 ,  asked earlier. 
	EE(BMW)  talked to the official (s)

of the hospital . Unit has paid a balance fee of Rs. 17,800.


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	4 member team comprising of Dr.T.K. Joshi, EE(BMW), Dr. Chetna &  Trainee to inspect. Call on 27.08.2008.

	19.
	M.V.I.D Hospital (MCD),  Kingsway Camp, Delhi-9


	227
	NW-004


	22-Dec-04

&  09.06.08


	20-Apr-07(CTO)& 26.06.08(CTE)
	1. HCU has applied under Air Act on 20-4-2007 (C/115).

2. HCU has also submitted the noise monitoring report (C/109). 

3. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 & 01.10.07 to Addl. Commissioner, MCD./ Commissioner MCD., seeking for appropriate action w.r.t. deficiencies pointed  (c/126), however reply not  received.

4. As decided in the meeting on 18.03.08, letter for deficiencies was issued. 

5. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.Reply  was  received.

6.Applied for renewal of authorization on 09.06.2008.

7.Reply dated 01-07-08.w.r.t letter dated 25-04-08.regareding submission of test report of waste water generated from hospital  was received.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building. Applied for renewal of authorization on 09.06.2008.

EE(BMW)  talked to the official (s)

of the hospital .

	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	4 member team comprising of Dr.T.K. Joshi, EE(BMW), Dr. Chetna &  Trainee to inspect. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	20.


	Lal Bahadur Shastri Hospital, Khichripur
	100


	E-002


	8-Aug-06
	 28-Dec-07
	1. Authorization is valid up to 30-5-2010((C/197).

2. HCU submitted a letter on 18-7-2007(C/220) wherein they have requested to know about the justification of balance fee in respect to authorization issued on 20-6-2007(C/197). 

3. HCU was inspected and BMW management found as per rule.(C /  221).4. Reply received along with copy of letters to PWD for comments/consent applications.4. EE (BMW) talked to the official of the hospital as decided on 15.11.07 .5. Application received for consent to operate however, noise monitoring report for DG Sets and stack monitoring report for boiler not submitted. 6. As decided in the meeting on 18.03.08, letter for deficiencies was issued.
7. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

8.Reply received  dated. 24-06-08.w.r.t latter dated 25-04-08.  


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .


	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals.  
	Common letter prepared & submitted  . To be issued after approval.
	Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	21.
	A&UTibbia College Hospital, Karol Bagh, New Delhi-5
	150
	C-007


	22-Sep-06
	28-Sep-06
	1. Authorization is valid up to 30-5-2010.

2. HCU has applied for Consent to operate under Air Act .
3. HCU was inspected on 23-8-2007(C/110) and the BMW management found as per rule.

4. The stack height with the DG set is yet to be increased.

6. Meeting taken by Pr. Secy. (Health) on 25.09.07, HCU was directed ( in the meeting) to comply with norms/standards prescribed for DG Sets and submit compliance report along with the Noise Monitoring report to DPCC. However noise monitoring report not received.

7.  As decided in the meeting on 18.03.08, letter for deficiencies was issued. 
8.Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

9. Reply not recived.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .


	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC as per the general decision taken for Delhi Government Hospitals.  
	Common letter prepared & submitted  . To be issued after approval.
	Trainee to visit and persuade MS of the Hospital to apply quickly. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	22.
	Dr. Baba Saheb Ambedkar Hospit Sector-6, Rohini, New Delhi-85al, 


	500
	NW-002


	 02.08.07


	13-Aug-07(CTO) , applied for CTE also.


	1. SCN under EPA was issued on 23-3-2007(C/68) & 11-6-2007(C/70) .

2. HCU has applied for consent to operate  under Air Act on 13-8-2007.

3. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Pr Secy  (Health).

4. Meeting taken by Pr. Secy. (Health) on 25.09.07, HCU was directed ( in the meeting) to inform DPCC about the rectification measures. 

5. No response received after the said meeting. 

6. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 21.04.08
7. Reply dated 02.06.08 w.r.t. letter dated 21.4.2008 received regarding  rectification of deficiencies  observed  during inspection  

  (i) Applied for con sent to establish under Air and Water ActS .

  (ii) Painting of Bio Hazard symbol act storage site of B MW .

  (iii) Proper labeling of  BMW collection  Bags.

  (iv).Procper acoustic treatment to 2 DG sets.

  (v).Installation of ETP is in process.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .


	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals.  
	Common letter prepared & submitted  . To be issued after approval.
	4 member team comprising of Dr.T.K. Joshi, EE(BMW), Dr. Chetna &  Trainee to inspect. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	23.
	LRS Institute of Tuberculosis,  Sri Aurbindo Marg New Delhi-30
	515
	S-004


	17-Jul-06
	06-Aug-07
	1. Authorization is valid up to 7-3-2010(C/248). ( with condition that HCU shall close down the incinerator).2. SCN u/s 21/22 of Air Act was issued on 23-3-7(C/239) and 11-6-207(C/253).

3. DO letter issued to JS (Health), GOI. On 01.10.07 seeking replies of the notices issued on 23.03.07 & 11.06.07. 4. HCU applied for consent to operate under Air Act on 6-8-2007(C261) alongwith the noise monitoring report(C/255).5.. HCU has also requested to operate the incinerator(C/252) as APCD has been installed.6. ETP not installed. HCU Is having 520. Beds.7. Letter was issued for the trial run of the incinerator seeking stack monitoring report within 30 days and the hospital to install the ETP.8. The hospital has submitted stack analysis report but the parameter of Volatile Organic Compound was not  analyzed for the ash generated from the incinerator. No information regarding ETP was submitted. No waste water analysis report was submitted.9. As decided in the meeting on 18.03.08, letter for deficiencies was issued.10. Reply received w.r.t. letter dated 02.05.2008. CTE not applied. Analysis report of incinerator ash  submitted however not within the limit.11. Letter dated 26-05-08 was issued as per the decision taken on 05.08.12.Reply received dated 13-06-08 w.r.t letter dated 26-05-08 regarding doing the needful as directed  received. 
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Reply received w.r.t. letter dated 02.05.2008. CTE not applied. Analysis report of incinerator as submitted.

EE(BMW)  talked to the official (s)

of the hospital .
	Inspect and report. Call on 14.07.2008.
	To be inspected.

	Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 


	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	24.
	Kasturba Hospital, Near Jama Masjid, New Delhi-2
	450
	C-004


	3-Aug-06
	17-Jan-05


	1. HCU has applied For Consent to Operate  under Air Act on 17-1-2005.

2. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 21.04.08. 

3. Reply received w.r.t. letter issued on 21.4.2008.    NMR submitted.
4. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

8.Reply dated  03-06-08. 

9. Another letter received on 14.07.08 w.r.t letter dated 26.05.08, informing that needful is being done.

	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Reply received w.r.t. letter issued on 21.4.2008. NMR submitted.

EE(BMW)  talked to the official (s)

of the hospital .


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	Trainee to visit and persuade MS of the Hospital to apply quickly. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	25.
	Sardar Valabh Bhai Patel Hospital, East Patel Nagar, New Delhi-8
	50
	W-206


	7-Jul-06
	18-Dec-07


	1. As per direction HCU was inspected on 19-3-2007(C/31) but BMW Management not found as per rule.

2. Applied for Consent however Noise Monitoring report for DG Sets not submitted.

3  As decided in the meeting on 18.03.08, letter for deficiencies was issued on 21.04.08 
4.Reply dated 12-06-08. received w.r.t letter dated 21-04-08. requesting one month time to submit required information .
5. Letter recived dated 07.07.08.
	EE(BMW)  talked to the official (s)

of the hospital . Reply  received


	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals. EE to chase up. Call on 14.07.2008.
	Common letter prepared & submitted  . To be issued after approval.

EE(BMW)  talked to the official (s)

of the hospital .


	Call on 27.08.2008

	26.
	Nehru Homeopathic Medical College, Defence Colony, New Delhi-24


	100
	S-013


	1-Dec-06
	5-Dec-06
	1. Authorization is valid up to 07.03.2010

2. Consent to Operate is valid up to 07.03.2010.

3. Noise Monitoring Report for DG Set submitted for 125 KVA  DG.Set.

4. As decided in the meeting on 18.03.08, letter for deficiencies was issued.
5. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

6.Reply dated 12-06-08,w.r.t letter dated 26-05-08.received. 
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.
	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals. EE to chase up. Call on 14.07.2008.
	Common letter prepared & submitted  . To be issued after approval.

EE(BMW)  talked to the official (s)

of the hospital .
	Trainee to visit and persuade MS of the Hospital to apply quickly. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	27.
	Satyawadi Raja  Harish Chander hospital, Plot No.30,Sector-7A, Narela, Delhi-40


	200
	NW-278


	13-Jun-07 
	 Not Applied
	1. HCU applied for authorization on 13-6-7(C/56).                             2.  HCU did not apply for consent to operate  under Air Act.

3. SCU under BMW Rules was issued on 11-6-2007(C/46).

4.. As decided on 1-8-2007, D.O. letter was  issued on 17-8-2007 to Pr Secy  (Health).

5.  Meeting taken by Pr. Secy. (Health) on 25.09.07, it was decided that MS of the Hospital should submit Consent application within 15 days. 

6.. Talked to the official of the hospital as decided on 15.11.07.However Consent Application under Air Act not received.
7.. As decided in the meeting on 18.03.08, letter for deficiencies was issued .

8. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

9.. Copy of Communication to EE(PWD) received w.r.t. letter dated 26.5.2008.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Copy of Communication to EE(PWD) received w.r.t. letter dated 26.5.2008.

EE(BMW)  talked to the official (s)

of the hospital .
	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals.

EE to chase up. Call on 14.07.2008.
	Common letter prepared & submitted  . To be issued after approval.

EE(BMW)  talked to the official (s)

of the hospital .


	Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	28.
	Shastri Park Hospital,Govt. of NCT of Delhi, Shastri Park,Delhi-53
	200
	NE-104


	 25-Oct-06
	 Not Applied
	1. Authorization is valid up to 7-3-2010 (C/29).

2. SCN under Air Act was issued on 23-3-2007(C/28) and 11-6-2007(C/33) but HCU did not submit any reply to the SCNs.

3. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Pr Secy (Health).

4.  Meeting taken by Pr. Secy. (Health) on 25.09.07, it was decided that MS of the Hospital should submit Consent application within 15 days. However Consent Application under Air Act not received so far. 

5. EE (BMW) talked to the official of the hospital as decided on 15.11.07. 

6. However Consent Application under Air Act not received so far.

7. As decided in the meeting on 18.03.08, letter for deficiencies was issued.
8.Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

9. Reply not  received. 


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .


	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals. EE to chase. Call on 14.7.2008
	Common letter prepared & submitted  . To be issued after approval.

EE(BMW)  talked to the official (s)

of the hospital .


	Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	29.
	Northern Railway Divisional Hospital, S.P. Mukherjee Marg, Delhi-6
	50
	C-010


	 20-Aug-04
	 21-Nov-07
	1. Authorization is valid up to 7-3-2010(C/56).

2. SCN under Air Act was issued on 23-3-7(C/55) and 11-6-2007(C/57) but HCU did not submit any reply to the SCNs.

3. As decided on 31-8-2007, D.O. letter was issued on 01.10.07 to GM Northern Railway, seeking consent application under  Air Act, 

4. EE (BMW) talked to the official of the hospital as decided on 15.11.07. 

5.Blank application received for consent without any information regarding     DGSets & Boiler etc. Consent Fee submitted.

6.  As decided in the meeting on 18.03.08, letter for deficiencies was issued.  

	EE(BMW)  talked to the official (s)

of the hospital .


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	Trainee to visit and persuade MS of the Hospital to apply quickly. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	30.
	Ayurvedic Hospital, MCD, Haiderpur, Delhi-52
	100
	NW-008


	 14.11.07
	Not Applied
	1. SCN under Air Act (C/84) was issued on 11-6-7 and BMW Rules (C/82 & C/85) was issued on 23-3-07 and 11-6-2007.

2..As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 & 01.10.07 to Addl. Commissioner, MCD./ Commissioner MCD., seeking consent and authorization application,. Applied for authorization on 14.11.07,  

3. EE (BMW) talked to the official of the hospital as decided on 15.11.07. 
4.Vide letter dated 18.12.07 informed regarding having DG Set of 75 KVA which is not working since 2005 and in future it will function under the Air Act. 5.. However Consent Application under Air Act not received so far.
6. As decided in the meeting on 18.03.08, letter for deficiencies was issued.
7. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

8. Note received from RMS stating that necessary proceedings have been initiated and Engineering department has been apprised about the directions of DPCC. Claims that there is no BMW generation in the hospital being a Ayurvedic Hospital.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .
	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	Trainee to visit and persuade MS of the Hospital to apply quickly. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	31.
	Babu Jagjeevan Ram Memorial Hospital, Jahangirpuri, Delhi-33
	100
	NW-009


	 29-Jun-06
	27.09.07
	1. Authorization is valid up to 7-3-2010(C/112).

2. Applied for Consent.. Stack Monitoring report for    DG Set submitted, shows emissions within limit.    Noise monitoring  report for DG set(125 KVA)  not    submitted.

3.. As decided in the meeting on 18.03.08, letter    for deficiencies was issued.
4.Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

5.Reply received. 


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital
	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals.

EE to chase up. Call on 14.07.2008.
	Common letter prepared & submitted  . To be issued after approval.

EE(BMW)  talked to the official (s)

of the hospital .


	Call on 27.08.08



	32.


	Majeedia Hospital, Jamia Hamdard, IHMMR Campus, Hamdard Nagar, New Delhi-110 062


	136
	S-009


	 23-Feb-07
	08.10.07


	1. Authorization under BMW Rules is  valid upto 7-3-2010(C/180).

2. SCN u/s 21/22 of Air Act was issued on 23-3-2007 and 11-6-2007(C/179 & C/196).

3. HCU submitted the reply that in response to SCN(C/195) with the remarks that there is no DG set being operated by the hospital, however they get the electricity in case of no power from DG set being operated by Hamdard University.  HCU did not reply to the SCN under Air Act. 4.As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 toJt.Secy(Health), GOI. Seeking   consentapplication..5. Applied for Consent to Operate on 08.10.07.

6. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 29.04.08..

7..Reply dated 22-05-08.w.r.t letter dated 29-04-08. received. 
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.  EE(BMW)  talked to the official (s)of the hospitalReply received w.r.t. letter dated 29.4.2008

	MS, DPCC to write to Medical Supdt.  and EE to chase up with hospital. Call on 14.07.2008.
	Letter issued.

EE(BMW)  talked to the official (s)

of the hospital .


	Trainee to visit and persuade MS of the Hospital to apply quickly. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	33.
	Jai Prakash Narayan ApexTrauma Centre, Ansari Nagar, Raj Nagar, New Delhi-29


	200
	SW-131


	 7-Sep-06
	 27.09.07
	1. HCU was inspected on 19-3-2007(C/50) and BMW Management found as per rule, but ETP was not in operation.

2. HCU had not submitted waste water test report 

3. Applied for Consent to Operate on 27.09.07. Noise monitoring report for DG set received from DPCC lab.

4. As decided in the meeting on 18.03.08, letter for deficiencies was issued.Reply  received.
5. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

6.Reply not  received.   


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.


	A common letter be sent to Jt. Secretary (Health), GOI with copy to D.G. (CPWD), from Chairman, DPCC  as per the general decision taken for Central Government Hospitals 

EE to chase up. Call on 14.07.2008.
	Common letter prepared & submitted  . To be issued after approval.

EE(BMW)  talked to the official (s)

of the hospital .


	Call on 27.08.2008

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	34.
	Hedgewar  Arogya Sansthan, Opposite CPCB, Karkardooma, east Arjun Nagar, Delhi-32
	200
	E-158


	 14-3-07
	19.12.07
	1. Authorization is valid up to 30-5-2010 (C/67).

2. SCN under Air Act was issued on 11-6-2007(C/65)  since  HCU had not applied for consent under Air Act.

3. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Pr Secy  (Health).

4.  Meeting taken by Pr. Secy. (Health) on 25.09.07, it was decided that MS of the Hospital should submit Consent application within 15 days and to inform DPCC for rectification measures taken w.r.t. deficiencies pointed out in the meeting. 

5. EE (BMW) talked to the official of the hospital as decided on 15.11.07. 

6.. Application for consent to operate received along with affidavit. The application reveals having two boilers (HSD fired) and two DG sets of 62.5 KVA,( without acoustic enclosure).Stack monitoring report  not  submitted. 

7.. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 21.04.08. Reply received.

8. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

9..Reply dated 09-06-08 received w.r.t letter dated 21-04-08.regarding doing the needful as directed.
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Reply received w.r.t. letter dated 21.4.2008.

EE(BMW)  talked to the official (s)

of the hospital


	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals.

EE to chase. Call on 14.07.2008  
	Common letter prepared & submitted  . To be issued after approval.

EE(BMW)  talked to the official (s)

of the hospital .


	EE(BMW) to chase up . Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	35.


	Delhi Government Hospital,  Sector-9, Dwarka, New Delhi


	500(Proposed Hospital)
	SW-135


	 22-Sep-05



	 Applied 

for CTE

	1. The construction of HCU not started.
2. Letters were issued on 23-3-2007 (C/9) and 11-6-2007(C/10) but HCU did not submit any reply to the above said correspondences.

3. It was decided in the meeting held on 1-8-2007, that  at that time  no action was  warranted on part of DPCC as the HCU  was  not in operation.

4.. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 26.05.08..

5. Reply dated 16-06-08  w.r.t. letter dated 26.5-08.received.

6. Applied for Consent to Establish .

7. Letter received from Directorate of Health Services referring that the matter is being looked after by PWD.

]


	EE(BMW)  talked to the official (s)

of the hospital, informed that Consent to Establish application shall be submitted soon.

Reply received w.r.t. letter dated 26.5.2008.


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	 Applied for Consent to Establish. 4 member team comprising of Dr.T.K.Joshi, EE(BMW),Dr. Chetna,  & Trainee to inspect. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	36.
	Hindu Rao Hospital Delhi – 110 007l.


	980
	N-001


	5-Apr-06
	Not Applied for Renewal
	1. HCU was inspected on 20-3-2007(C/207) during which BMW management found satisfactory but incinerator was not in operation.

2. SCN under Air Act was issued on 11-6-2007(C/210) but HCU did not apply for consent under Air Act.

3. HCU requested to extend the time limit for installation of ETP(C/211). 

4. As decided on 1-8-2007, D.O. letter was  issued on 17-8-2007 to Addl. Commissioner  (Health), MCD

5. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 & 01.10.07 to Addl. Commissioner, MCD./ Commissioner MCD., seeking consent application under Air Act. 

6. Letter dated 08.10.07 received and informed that matter regarding ETP  is under process and will be finalized at the earliest.

7. EE (BMW) talked to the official of the hospital as decided on 15.11.07. 

8. However Consent Application under Air Act not received so far.

9.  As decided in the meeting on 18.03.08, letter for deficiencies was issued on 21.04.08.

10. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.  11.Reply dated 24-06-08. w.r.t latter  dated 21-04-08 and 26-05-08. received informed  doing the needful as directed.
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d) ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital


	EE to chase up. Call on 14.07.2008.


	EE(BMW)  talked to the official (s)

of the hospital .


	EE(BMW) to chase up. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	37.
	Rao Tula Ram Memorial Hospital, Jafferpur, Delhi
	100


	SW-003


	7-Nov-06
	Not Applied
	1. Authorization is valid up to 7-3-2010(C/164).
2. SCN u/s 21/22 of Air Act was issued on  01-5-2007(C/165) and on 11-06-2007(C/173)

3. Reply was received with the remark that APCD has been installed with incinerator and stack report is also submitted and the installation of ETP is under process with PWD(C/172) .   

4. Reply received to SCN u/s 21/22 with the remark that they have applied for consent under air act but the same  has not been received(C/168).

5. Inspection  was  conducted on 9-7-2007 and BMW Management found as per rule. ( i/r at page 174- 175) 

6. Incinerator was not in operation as the incinerable waste was not there.

8. Earlier spoken to Medical Superintendent of the Hospital, and it was informed that the Matter is under process and the application for consent under Air Act will be submitted very shortly.

9.  Meeting taken by Pr. Secy. (Health) on 25.09.07, it was decided that MS of the Hospital should submit Consent application within 15 days. Not Applied for Consent though submitted required fee for DG set monitoring.

10. EE (BMW) talked to the official of the hospital as decided on 15.11.07. 

11. However Consent Application under Air Act not received so far.

12. The hospital was inspected by a three member team headed by Dr. T.K.Joshi, on 27.02.08 and the records for incinerator revealed that incinerator was not operated during the period 19.11.07 to 03.12.07 and for the period 22.01.08 to 12.02.08 and the reasons could not be explained for the non-operation of the incinerator. It was also revealed from the records maintained that temperature in the secondary chamber of the incinerator is for below the prescribed temperature. 

13. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 19.05.08.

14.Reply dated 12.06.08 enclosing  Copy of communication to PWD regarding NMR, stack report and non operation of incinerator submitted.

	. As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital.l Reply  received.


	EE to chase up. Call on 14.07.2008.  
	EE(BMW)  talked to the official (s)

of the hospital .


	EE(BMW) to chase up. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	38.
	Chacha Nehru Bal Chikatsalya, Geeta Colony, Delhi-110 031
	216
	E-179


	1-May-07
	Not Applied
	1.Earlier  Authorization was valid upto 22-3-2007(C/13).

 2. Meeting taken by Pr. Secy. (Health) on 25.09.07, it was decided that MS of the Hospital should submit Consent application within 15 days. 

3. Talked to the official of the hospital as decided on 15.11.07. 

4. However Consent Application under Air Act not received so far.

5. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 21.04.08.
6.Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

7.Reply dated 11-06-08. w.r.t latter  dated 21-04-08.and 26-05-8. received regarding doing the needful as directed 
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital. Reply  received

	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals.

EE to chase up. Call on 14.07.2008.  
	Common letter prepared & submitted  . To be issued after approval.

EE(BMW)  talked to the official (s)

of the hospital .


	Call on 27.08.2008.



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	39.
	Guru Gobind Singh Govt. Hospital, Raghubir Nagar, New Delhi-110 027
	100
	W-006


	13-Mar-07
	19-Dec--07


	1. Authorization was valid up to 16-4-2007(C/42).

2. Application received for consent however, noise monitoring report for DG Sets     not submitted.  Waste water test report received showing the parameters    within prescribed limits.

3.. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 21.04.08. 

4.. Reply received w.r.t. letter dated 21.4.2008. Balance fee of CTO not submitted and CTE not applied.
5.Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

6.Reply not received.



	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)of the hospital. Reply received w.r.t. letter dated 21.4.2008
	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals.

EE to chase up. Call on 14.07.2008.   
	Common letter prepared & submitted  . To be issued after approval.

EE(BMW)  talked to the official (s)

of the hospital .


	Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	40.
	Lady Harding Medical College and Associated Hospital, New Delhi


	1227
	ND-001


	9-May-07
	Applied
	1. HCU applied for authorization on 9-3-2007(C/555).

2. Authorization was valid up to 16-5-2007(C/359).

3. HCU applied for Consent to Operate  under Air Act.

4. Letter issued on 28.12.07 asking Stack Monitoring report of      Boilers as well as incinerator & for providing acoustic treatment/      enclosure for the 2 DG Sets of 160  KVA each , noise monitoring      report for the DG Sets & also for installation of ETP. Reports/      Reply to the said letter  received.

5.  As decided in the meeting on 18.03.08, letter for deficiencies was issued on 25.04.08.. 

6. Reply received w.r.t. letter dated 25.4.2008.
7. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Reply received w.r.t. letter dated 25.4.2008.

EE(BMW)  talked to the official (s)

of the hospital


	EE to chase up. EE to also ascertain what is the waste water generation and how it is disposed off at present. Based on this a letter may be sent to Joint Secretary, Ministry of Health with the copy to DG, CPWD to get the needful done. Call on 14.07.2008.
	EE talked to M.S. of Hospital. Quantum of waste water generation given in the study conducted by I.I.T Delhi, which has suggested for ETP. Waste water is discharged in municipal sewer. 
Letter to be issued after approval.

	A letter maybe drafted from Chairman, DPCC to Secretary, Ministry of Heath  directing him to apply for Consent to Establish  immediately and install Effluent Treatment Plant (ETP) without any further delay on account of 400 KLD of waste water generation from the Hospital . Ask him to apply for CGWA clearance also immediately. If the unit fails to respond DPCC will be constrained to take punitive action.  Copy to Chairman, CPCB, Principal LHMC, Secretary,Environment, Govt. of India. Other deficiencies noted may also be communicated. 

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	41.
	Central Jail
 Hospital, Tihar
	150
	W-005


	4-Aug-06(valid)
	Not Applied
	1. Authorization is valid up to 1-7-2009(C/124)  was issued with the condition that HCU will apply for consent under Air Act within two months time.

2. Meeting taken by Pr. Secy. (Health) on 25.09.07, it was decided that MS of the Hospital should submit Consent application within 15 days. However Consent Application under Air Act not received so far. 

3. Talked to the official of the hospital as decided on 15.11.07. 

4. However Consent Application under Air Act not received so far.

5.  As decided in the meeting on 18.03.08, letter for deficiencies was issued on 25.04.08. 

6. Reply received informing that the matter has been referred to PWD in respect to letters received from DPCC. List of Lab was sought which was  faxed to the hospital.

7 Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

8.Reply dated 27-05-08.w.r.t letter dated 25-04-08.& letters received on 08.07.08  w.r.t letter dated 26.05.08.mentioning that to communicate with Prison Head Quarters for the necessary action.

 
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	MS to write to DG Prisons, Copy to Pr. Secretary, Home .



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	42.
	ESI Hospital, Shree Maa Anandmayi Marg, Okhla phase-1, New Delhi- 110020
	150
	S-012


	22-Oct-07
	Not Applied
	1. Earlier Authorization was valid up to 2-11-2007(C/135). 

2. Applied for renewal of Authorization under BMW Rules on      22.10.07

3D.O. letter issued to Jt. Secy. (Labour) GOI with copy to DG ESI.     Reply received from JS.

4. Talked to the official of the hospital as decided on 15.11.07. 

5. However Consent Application under Air Act not received so far.

6. As decided in the meeting on 18.03.08, letter for deficiencies was issued.
7 Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

 8. Reply not received.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital

	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	Trainee to visit and persuade MS of the Hospital to apply quickly. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	43.
	ESI Hospital, Sector-15. Rohini
	100
	NW-010
	05-Oct-07
	20-Jul-05
	1. Authorization was valid up to 1-11-2007(C/91).

2. Applied for renewal of authorization on 05.10.07

3 D.O. letter issued to Jt. Secy. (Labour) GOI with copy to DG ESI. Reply received from JS. 

4. Talked to the official of the hospital as decided on 15.11.07. 

5.  Applied for Consent ( Renewal) under Air Act, As per receipt submitted.

6. As decided in the meeting on 18.03.08, letter for deficiencies was issued.
7.Letter dated 12-06-08 and 16-06-08.w.r.t letter dated 26-05-08.receiverd , asking for time upto 31-10-08, for  necessary installation. 

	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital Reply  received.

	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	Trainee to visit and persuade MS of the Hospital to apply quickly. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	44.
	Institute of Human Behaviour & Allied Sciences, Near GTB Hospital, Dilshad Garden
	190
	NE-003


	5-Aug-05(valid)
	15-Jan-08
	1. Authorization is valid up to 4-8-2008(C/109 of the concerned file). 

2. Applied for renewal of  Consent to Operate on 15.01.08.

3. Acoustic Enclosure provided for DG Set of 2x 625 KVA & for other DG Set, (180 KVA DG Set) it is informed that it is not in operation ( acoustic enclosure not provided). Noise Monitoring Report for DG Set not submitted.

4.. As decided in the meeting on 18.03.08, letter for deficiencies was issued.
5. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

6.Reply  not received.
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital

	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals.


	Common letter prepared & submitted  . To be issued after approval.
	Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	45..


	Palika Maternity Hospital, Lodhi Colony , New Delhi-3
	50
	S-018


	09-Aug-05


	Not Applied


	1. Authorization is valid up to 30-01-2010(C/128).

2. SCN u/s 21/22 of Air Act was issued on 11-6-2007(C/137) but HCU did not apply under Air Act.

3. As decided on 1-8-2007, D.O. letter was issued on 17-8-2007 to Chairperson, NDMC..

4. Letter issued seeking consent application under Air Act , HCU s has informed in its reply that there is no Boiler and DG Set in the Hospital and also informed that installed incinerator is not functional ( closed) 

5. Talked to the official of the hospital as decided on 15.11.07. 

6. As decided in the meeting on 18.03.08, letter for deficiencies was issued.

	EE(BMW)  talked to the official (s)

of the hospital


	A letter from Chairman, DPCC to Chairman, NDMC. Call on 14.07.2008.
	Letter issued.
	Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	46
	International Centre for Genetic Engineering & Bio Tech, ICGEB  Campus, P.O. Box  10504, Aruna Asaf Ali Marg, Delhi -67.
	Nil
	SW-054


	21- Mar- 05

and on 11.06.08 (for renewal)
	 Applied for CTE & CTO on 11.07.08
	1. This is a case of Research Centre (Veterinary) of Govt , which is engaged in research activities related with veterinary / Genetic Engineering & have applied for  authorization under BMW Rules. Provisional Authorization granted earlier was valid upto 05.11.2002. Application for renewal was received on 21.03.05.which was placed before the BMW Committee No. 3, in its meeting held on  18.10.07, and  it was decided by the said Committee  that being a case of research institute, put up on file for deciding which BMW Committee should deal this case . The matter was put in fil e  and as decided by MS, DPCC, this case has been  included in the cases to be dealt by BMW Committee No.1.  

2. The Institute has installed an incinerator for the disposal of BMW. and submitted stack monitoring report  dated 19.05.05. showing parameters within the prescribed limits. 

3.  Two  DG Sets of capacity 625 KVA each found installed without acoustic enclosure during the inspection carried out on 27.06.05 .

 4. As decided in the meeting on 18.03.08, letter for deficiencies was issued.

5. Applied fresh on 11.06.08 for renewal of authorization under BMW Rules. Applied for Consent to Establish & Operate on 11.07.08.
	EE(BMW)  talked to the official (s)

of the hospital. The HCU has submitted reply in response to the letter dated 02.05.2008 and has submitted balance fees.


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	Consent to Establish & Operate applied. 5 member team comprising of Dr.T.K. Joshi, EE(BMW),Dr. Chetna, Dr. Shardha Pant, and Trainee to inspect. Call on 27.08.2008. In the meantime, unit may be asked to submit  CGWA permission and install ETP. Unit may also be asked to do the remaining four  things. 



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	47
	Bhagwan Mahavir Hospital  , H – 4/5, Pitampura, Delhi -34.
	200
	NW-301


	19- Mar-07
	20-sep-07
	1. This is a case of Delhi GOVT. Hospital having 200 beds. 

2. Earlier authorization was granted under BMW Rules which was valid upto 19.04.07. 

3. The Hospital was inspected on 30.09.05 & two DG Sets of 750 KVA each were found with acoustic enclosure. Noise monitoring report of DG Sets not submitted. As per application DG Sets stack height is not adequate.

4. The BMW  is disposed through M/s Synergy  Waste Management Pvt. Ltd. 

5. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 24.04.08.
6. Reply received w.r.t. letter dated 24.4.2008.
7. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

8. Reply dated 10-06-08 regarding submission of  reports w.r.t 2 DG sets and waste water generated in the hospital was received.

9. Reply  dated 23-06-08.w.r.t latter dated .26-.05-8 was received regarding doing the needful as directed.
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital.

Reply received w.r.t. letter dated 24.4.2008


	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals.

EE to chase up. Call on 14.07.2008.   
	Common letter prepared & submitted  . To be issued after approval.

EE(BMW)  talked to the official (s)

of the hospital .


	Call on 27.08.2008

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	48
	Swami    Dayanand Hospital, Shahdara , Delhi-32
	230


	NE-002
	01-May-05
	10-Jul-05
Applied for CTE
	1. Authorization is valid up to 7-3-2010.

2. Consent to Operate is valid up to 30-5-2010.

3. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 21.04.08. Reply received vide letter dated 09.06.08 regarding submission of reports for DG Sets & waste water test report.

4. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

5.Reply dated 10-06-08,w.r .t letter dated 26-05-08.received  informing about doing the needful as directed .

6. Applied for Consent to Establish.



	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d) ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Reply received in response to letter dated 02.05.2008.

EE(BMW)  talked to the official (s)

of the hospital
	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	Applied for Consent to Establish .  4 member team comprising of Dr. T.K.Joshi, EE(BMW), Dr. Chetna and Trainee to inspect. Call on 27.08.2008

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	49

	MCD Chest Clinic and Hospital, Nehru Nagar, New Delhi- 65
	55
	S-236


	28-Dec-04
	Not Applied
	1. Authorization is valid till 30-10-2010(C/80).

2. SCN u/s 21/22 of Air Act was issued on 11-06-2007(C/82) since HCU had not applied under Air Act.

3. HCU submitted the reply on 26-7-2007(C/102) wherein it is mentioned that the DG set is out of order and not being used by them.

4. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 02.05.08.

5. Reply received w.r.t. letter dated 02.05.08. Required documents not submitted instead asked whether it is necessary to obtain consent under Air / Water Acts.

	EE(BMW)  talked to the official (s)

of the hospital


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	Trainee to visit and persuade MS of the Hospital to apply quickly. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	50
	Maharishi Balmiki Hospital, Pooth khurd , New Delhi-39
	100
	NW-011


	30-Jan-04
	26-Mar-07
	1. Authorization is valid up to 30-01-2010 (C/84). 

2..Consent to Operate  granted under Air Act as decided on 04.10.07& valid upto 03.10.2010.
3.. As decided in the meeting on 18.03.08, letter for deficiencies was issued.
4. Letter dated 26-05-08 was issued as per the decision taken on 06.05.08.

5. Copy of communication to EE(PWD) by the HCU submitted w.r.t the letters issued by DPCC vide letter dated 11.06.08.6. Another letter received from the Hospital on 10.07.08 stating the matter has been referred to PWD.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building. Copy of communication to EE(PWD) by the HCU submitted.EE(BMW)  talked to the official (s) of the hospital

	A common letter be sent to Pr. Secretary (Health) with copy to Pr. Secretary (PWD), Govt. NCTD, from Chairman, DPCC  as per the general decision taken for Delhi Government Hospitals.  
	Common letter prepared & submitted  . To be issued after approval.
	Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	51
	Dr. Shyama Prasad Mukherjee Chest Hospital, Patpar ganj, Delhi-91


	52
	E-004
	17-Aug-06
	Not Applied
	1. Authorization is valid up to 7-3-2010(C/56).

2. HCU reply to the SCN under Air Act with the undertaking that no DG set is in operation(C/58).

3. As decided in the meeting on 18.03.08, letter for deficiencies was issued on 26.05.08.  
4.Reply dated 12-06-08.w.r.t letter dated 26-05-08. received.Another letter received on 10.07.08.


	EE(BMW)  talked to the official (s)

of the hospital
	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	EE(BMW) to chase up. Call on 27.08.2008.

	52.
	Construction of 200 Bedded hospital at Kokiwala BaghAshokVihar, Phase-IV, Delhi-52. Correspondence Address - 

Exe.Engineer,Sector-6,Rohini, Delhi -85.
	200
	
	…….
	Applied for CTE.
	Information regarding Construction of 200 Bedded hospital at Kokiwala Bagh , Ashok Vihar, Phase-IV, Delhi-52 retrieved by CMC from the web site, was forwarded to BMW cell and the same is placed before the committee.  As per the retrieved information, project involves construction of general hospital on a plot area of 20105. 34 Sq.m and the total proposed builtup area is 54298.05 Sq.m. 
2.Reply dated 20-06-08.Regarding environmental clearance  received  .

3. Applied for Consent to Establish.
	Letter issued.
	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	Applied for Consent to Establish. 4 member team comprising of Dr. T.K.Joshi, EE(BMW), Dr. Chetna and Trainee to inspect. Call on 27.08.2008. Unit to also file  copy of Environmental Clearance. 


DECISIONS TAKEN BY BMW COMMITTEE NO.1 IN THE MEETING HELD ON 14.07.08 W.R.T AGENDA NO. 2 (74 CASES OF PVT.HOSPITALS/OPERATORS/DRUG MFG. / DRUG STOCKIST ETC.) (ANNEXURE  2)      
	   Sl.    NO.
	Name and Address  of the Unit 
	Authorization status
	Consent  Status
	Decision of the committee on 31-8-2007
	Action Taken  w.r.t Decision Taken on .31-8-2007 /  Remarks
	Decision of the committee  in the  Meeting  on 04-10-2007
	Action Taken w.r.t Decision Taken on 04-10.2007

	58.
	M/s Synergy Waste Management Pvt. Ltd.    Near Composite Plant ,  Sukhdev Vihar      Okhla , New Delhi-20.  


	 Applied for authorization on 22.06.06 for 3 years as per Rules. Authorization was granted on 07.11.06 for 1year 
	Applied for Consent on 27.06.06 with 3 years fee.  Consent to operate was  granted on 07.11.06 for 1year .
	1. SCN under rule 7 of BMW Rules be issued for the following: 1. waste should not be kept in open. 2. ‘On Govt. Duty’ on vehicles should not be display. 3. sludge dewatering device be provided with ETP.4. Manual mode on PLC should not be used. 5. Measures to control smell from BMW be taken. 6. Rota meter should be provided at PC &SC of incinerator.
	1.SCN has been issued on 03.09.2007

2. Inspection has been conducted on 27-9-2007.

 3. SCN u/s 5 of EP Act was issued by CPCB on 7-9-2007 after the inspection on 24-7-2007

4. Operator has submitted reply to both the notices mentioned above.

 5. The fact finding committee has been constituted by DHS for the complaints received from residents of Sukhdev Vihar and the representations received from the operators.

6. Letter issued to The Principal Secretary (Health) for allotment of alternative site.

7.Meeting of Committee constituted by Pr. Secy.(Health) GNCTD, was held on 24.10.07.

8. Authorization under BMW Rules & Consent to operate under Air Act granted to the Operator of CBMWT Facility was upto 06.11.2007.

9. Letter from CPCB dated: 05.10.07 to  CBMWT facility with directions for taking certain measures for the compliance of BMW Rules may also be perused.( Copy enclosed) 
	 The case was discussed in detail  & Show Cause Notice issued to the operator on 03.09.2007, Reply received from the Operator of the CBMWT and inspection carried out on 27.09.07, were also considered  and following decisions were taken :

(i) W.r.t deficiency “The Bio – Medical Waste should be kept in closed bins” mentioned in the said Notice,Reply is factually incorrect and the Committee has decided to issue Show Cause Notice for Closure of the Facility. 

(ii) Regarding  erasing of “ On Government Duty “ printed on the vehicles used for collecting BMW ,  the Committee accepts the reply.

(iii)  Regarding installation of Filter Press with the ETP for dewatering of sludge as mentioned in the said Notice, despite clear Notice the unit has not complied with the directions and given justifications which is not acceptable to the Committee. The Operator of the CBMWT Facility is once again directed to install Filter Press within three weeks and confirm through an Affidavit before next date of meeting of the Committee i.e on 15.11.2007.

(iv) Regarding “The manual mode of operation in the installed programmable Logic Control (PLC) based control system should be removed “  mentioned in the said Notice, Committee is not satisfied with the reply  and the Committee insists that Automatic System (PLC)  Should only be used as  mentioned in th CPCB Guidelines and an Affidavit should be filed by the Operator with in three weeks and he should comply with this direction before the next meeting of this Committee i.e. on 15.11.2007.To ensure that Operator of the said  CBMWT Facility, complies with this direction, the Operator of the Facility , will  submit a  Bank Guarantee of Rs. One Lakh ,  valid for Six month period , in favour of Delhi Pollution Control Committee, within three weeks along with the said Affidavit.

(v) Regarding “Necessary measures should be taken for controlling the smell generated from BMW within the facility “mentioned in the Notice, the Committee accepts the reply, however any discontinuance or irregularity in the action will result in filing of another Bank Guarantee of Rs. One Lakh valid for Six month period, in favour of DPCC, by the Operator of the said Facility.

(vi) Regarding “ Rota – meters and pressure gauges should be installed in the primary and secondary chamber of the Incinerator “ mentioned in the said Notice , the Operator of the said Facility has not filed factually correct reply since the Rota meter and pressure gauges not found installed during the inspection on 27.09.07. The Committee directs him to file an Affidavit after installation of Rota meters and Pressure Gauges, within three weeks.   
	Show Cause Notice u/s 5 of EPA issued on 12.10.07 for the decisions taken by the committee. Reply along with the affidavit received for the compliance of the decision taken by the committee. Informed that provided filter press, informed regarding never use of manual mode of operation in the installed PLC, and regarding installation of Rota meters and pressure gauges, lids provided to all BMW plastic containers and necessary measures taken to control the smell, display sign (on Govt. Duty have been erased, no segregation is done within the facility, records of BMW collection and   incineration / autoclaving are being maintained. Operator of the CBMWT requested for exemption from depositing the Bank Guarantee. As directed by Chairman DPCC letter issued on 07.11.07 informing that no exemption from Bank Guarantee is possible. Operator submitted the Bank Guarantee of Rs. One Lakh , valid for 6 months.

The Operator of the facility had requested for grant of authorization under BMW Rules since earlier granted authorization expired on 06.11.07.( Consent to operate also expired on 06.11.07.)


 Decision  Taken by the Committee  in the  Meeting  on 15-11-2007:   Since  a complaint against this unit has been processed & submitted to Hon’ble Lt. Governor , Delhi, and since  its Authorization under BMW Rules & Consent  under the Air / Water Act , lapsed on 06.11.07 , full yearly authorization or 3 yearly authorization / consent under the said Rules / Acts is not possible under the circumstances. An interim extension of the  Authorization under BMW Rules and  Consent to operate under the Air / Water Acts , upto 31.12.2007, is granted by which time the status of the complaint will be decided. Meanwhile Member Secretary, DPCC, will speak to  Medical Deptt./ Directorate of Health Services & get the report of the Committee  set up by them for deciding on shifting  his location.

Action  Taken Report w.r.t. meeting on 15.11.07:  (i) Authorization under BMW Rules and consent to operate under the Air & Water Acts extended upto 31.12.07. (ii)  Letter issued to the  Convenor of the Committee constituted for said operator seeking report of the committee. Report awaited.   

(III) The operator has submitted a list of 8 units w.r.t the letter issued seeking the list of the units (drug mfg units) from which the operator is collecting BMW waste however the units not applied for authorization.. 

        Decision Taken by BMW Committee No. 1 in the Meeting Held on 15.01.2008 : “Both, the decision of Hon’ble Lt. Governor and the inspection report are not yet available on file. These reports may be expedited and put up on file formally through Member Secretary, DPCC         and other members of the Committee to the Chairman. Since this may take 15 days, the authorization under BMW Rules and Consent to operate under Air & Water Acts may be extended for interim period of one month i.e. 31st January, 2008.”

       

M/s Synergy Waste Management Pvt. Ltd, Near  Composite Plant, Sukhdev Vihar, Okhla, Delhi-20. 

Action Taken w.r.t Meeting on 15.01.2008 :  

In view of the above decision taken by the said BMW Committee No. 1, the extension of the Authorization under BMW Rules and Consent under the Air / Water Acts up to 31.01.2008, has been issued on 25.01.2008. Report of the Independent Committee received and  put up in file . As directed  by the Chairman, DPCC, the same is placed before the BMW Committee No.1 for the decision. 

Decision Taken by BMW Committee No. 1 in the Meeting Held on 08.02.2008 : 

The report of the Committee constituted by Pr. Secretary (Health) to enquire into the case of M/s Synergy Waste Management Pvt. Ltd. was placed before BMW Committee No-I today. The report is clear that in the long run it would not be advisable to keep the operation of Bio Medical Waste treatment facility at the existing premises at Okhla. Several options of alternate space were discussed. According to Dr. T.K. Joshi, there are three places which can be inspected and a decision can be taken in one of them which is free from all possible health hazards for operating such a facility. These are (a) Deen Dayal Upadhyaya Hospital, Hari Nagar, New Delhi (b) Rao Tula Ram Memorial Hospital, Jafferpur, Delhi & (c) Maharishi Balmiki Hospital, Pooth Khurd, Delhi. 

The above three premises may be inspected by a team headed by Dr. T.K. Joshi, Mr. D.K. Singh and the management of Synergey Waste Management Pvt. Ltd. so that an amicable solution could be found out. The report will be submitted on or before 29.02.2008. The authorization & consent of M/s Synergy Waste Management Pvt. Ltd. may be extended upto 29.02.2008 in view of the above and in the extension letter; one of the deficiencies noted would be communicated.  

Action Taken w.r.t Meeting on 08.02.2008:
(i) Authorization under BMW Rules and Consent to Operate under the Air & Water Acts extended upto 29.02.08 vide letter issued on   22 .02.08 & one of the deficiencies noted has       been communicated.

(ii)A letter dated 29.02.08,  was received from the director of M/s Synergy Waste Management Pvt. Ltd. requesting for extension of authorization under BMW Rules  for one year. As directed by      Chairman, DPCC, a letter has been issued to the said operator informing that the extension of authorization under the said Bio-medical Waste Rules, for a year, is not possible.       
(iii) A team headed by Dr. T.K.Joshi inspected the following three sites on 27.02.08 ;  1. Deen Dayal Upadhyaya Hospital, Hari Nagar, Delhi-64  2. Rao Tula Ram Memorial Hospital, Jafferpur,        Delhi-      43.   3.Maharishi Balmiki Hospital, Pooth Khurd, Delhi-39 and report was submitted to Chairman DPCC in file. The team found that none of the above mentioned three sites of the       Hospitals are       suitable for the establishment of a Common Bio-Medical Waste Treatment Facility. As directed by the Chairman, DPCC, the matter is placed before the BMW Committee No.1.

(iv) A letter dated 29.02.08, has also been received from the director of M/s Synergy Waste Management Pvt. Ltd., requesting to provide a copy of the said report of the team.

Decision Taken by BMW Committee No. 1 in the Meeting Held on 18.03.2008 :

(i) While Directorate of Health Services (DHS) , Govt. of NCT Delhi and the Private     Operator (M/s Synergy Waste Management Pvt. Ltd, Near Composite  Plant, Sukhdev  

     Vihar, Okhla, Delhi- 20.) will follow up with DDA for allotment of land for    the Common Bio Medical  Waste Treatment Facility  , this matter will be raised in the    list of issues to be taken up by      Chairman, DPCC with Vice Chairman, DDA.

(ii) Authorization under BMW Rules and Consent to Operate under the Air & Water Acts extended upto 30.04.2008.

(iii)Operator must get the land organized by  himself or  through DDA.  

Action Taken w.r.t Meeting on 18.03.2008:

(i) Aforementioned decision taken by the BMW Committee No.1, was sent to CMC for inclusion in the list of issues to be taken up by  Chairman, DPCC with Vice Chairman, DDA.

(ii) Authorization under BMW Rules and Consent to Operate under the Air & Water Acts extended upto 30.04.2008 vide letter issued on 09.04.08 mentioning the aforementioned decision taken by the BMW Committee No.1 in the meeting held on       18.03.08. 

(iii) Copy of the said letter was also sent to Directorate of Health Services (DHS) , Govt. of NCT Delhi.

(iv) A letter dated  28.04.08  has  been received from the director of M/s Synergy Waste Management Pvt. Ltd., requesting for extension of  authorization. Vide another letter dated 28.04.08 the Director of the unit has stated the back ground / brief of       the allotment of the said site by DDA to DHS for the said facility and also stated that the said site was inspected by officials of DHS, CPCB,  DPCC & COEH prior to its establishment. The said site is on the allotted land by DDA to DHS for       carrying out the activities of treatment and disposal of BMW. It is also mentioned that in the surrounding area is being used for waste management activities e.g. Okhla STP, MCD compost plant, NDMC waste to power project etc. It is mentioned       that DHS and DDA are in a better position to explain about the site that was already given to the operator or suggest an alternate site for  the treatment and disposal of BMW. It is also mentioned by the operator that whatever directions were given to       the operator, the same was complied and also enclosed the copy of stack monitoring report and water analysis report dated 19.09.07. showing parameters within the prescribed limit. It is also mentioned that the operator has approached DHS for       looking for an alternate land also. Requested for looking the matter sympathetically and for grant of authorization under BMW Rules and Consent to Operate under Air and Water Act.

v. A representation has been received from the residents of Sukhdev Vihar, DDA flats regarding health hazards due to treatment of large quantity of BMW at the said plant of CBMWTF. Near the residential area of Sukhdev Vihar    

Decisions Taken by BMW Committee No. 1 in the Meeting Held on 06.05.2008 :

(i) For finding a suitable alternative site for this  Common BMW Treatment Facility, a letter may be written by Chairman, DPCC, to Vice Chairman, DDA, and Commissioner, MCD, since this unit will have to be trans-located soon.

(ii) Authorization under BMW Rules and Consent to Operate under the Air & Water Acts extended upto the   next BMW Committee meeting  on 13.06.2008.

Action Taken w.r.t Meeting on 06.05.2008: 

(i) Letter issued to, Vice Chairman, DDA, and Commissioner, MCD, for finding a suitable alternative site for this  Common BMW Treatment Facility .
(ii)Authorization under BMW Rules and Consent to Operate under the Air & Water Acts extended upto  13.06.2008 vide letter issued on  21.05.08.Representatiom from the operator  received regarding extension of Authorization.  

Decisions Taken by BMW Committee No. 1 in the Meeting Held on 13.06.2008 : Authorization  under BMW Rules and Consent to Operate under  the Air & Water Acts extended upto the next BMW Committee meeting  on 14.07.2008.

Action Taken w.r.t Meeting on 13.06.2008:  (i) Authorization under BMW Rules and Consent to Operate under the Air & Water Acts extended upto  14.07..2008 vide letter issued on  27.06.08.

  (ii)  A  letter  from CMO ( BMW) , Deptt of Health Govt. of NCT , Delhi  received informing that Deptt of Health & Family Welfare ,GNCT  Delhi, has already taken up the matter   with  the DDA & has applied for an alternative land for  the present CTF at Okhla. 

Decisions Taken by BMW Committee No. 1 in the Meeting Held on 14.07.2008 :

Ask the two operators that on what basis they are charging the fee and how are they increasing the fee overnight by 100 %. A formal clear justification of increasing the fee may be submitted that must be examined properly and file may be submitted administratively.   If the unit does not behave, no further extension of authorization will be granted.  Reply must come within 15 days and file to be put up administratively. 

         (J.K. Dadoo)                            ( K.Mahesh)                          ( Dr.T.K.Joshi)          ( Dr. Chetna Harjai)               ( D.K.Singh)                ( Sanjay Vatts )             ( Shyam Sunder )             
       Chairman,DPCC              Member  Secretary,DPCC              COEH ,MAMC     Scientist, DOE , GNCTD       EE(BMWM Cell)         AEE(BMWM Cell)      AEE (BMWM Cell)         

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	1
	Maharaja Agrasein Hospital, West Punjabi Bagh, New Delhi- 26


	350
	W-003
	01.06.07
	10.09.05 (Operate), 04.04.08 (Establish)
	1. The HCU was inspected on 28-9-2006(C/139-C/140) and BMW management found as per rule.                                                                                                            2. Acoustic enclosure and adequate stack height has been provided with the DG sets.                                                                                                                          3.  The HCU had not submit the noise monitoring report of DG sets and stack monitoring report of boiler.               

4.  Applied for renewal of authorization along with affidavit & copy of valid agreement with operator of facility on 01-06-07 .Previous authorization expired on 23-02-07(C/137). 

5. Reply to SCN received that a common stack is provided with two of the boilers. Letter was issued seeking require d documents Noise Report & Stack Monitoring report after the meeting on 15.11.07. 

6. HCU has 3 DG sets. One is non-functional & is in process to dispose it.

7. Earlier only one noise monitoring report was submitted by the Hospital . Later on after the meeting on 15.01.08, copy of another report for the remaining DG Set was provided by DPCC LAB. This report was not submitted by the Hospital. . Sack monitoring submitted.8. Applied for consent to establish on 04.04.08. 9. Letter issued seeking balance fee of Rs. 35,600/-

10. Complaint was received from Sh. R.A. Grover honorary Secretary, Punjabi Bagh Cooperative Society Ltd. regarding illegal huge oxygen mfg. plant installed on road no. 35 West Punjabi Bagh. The inspection w.r.t. said complaint was done by Sh. B.Kumar, SEE on 30.04.08 and as per the inspection report, the complaint was of Mr. Sethi of the said area against MRI center, 19/35, Punjabi Bagh which is operating illegal and oxygen Mfg. plant operating at Mahraja Agresain Hospital, Punjabi Bagh. On the said specified address M/s National MRI scan centre was found. The main entry was found locked from inside.  It was gathered that ICICI recovery people had come for recovery of loan due to which main gate was closed. On inspection of Maharaja Agrasain Hospital, Punjabi Bagh, admin. Officer informed that the hospital is having the a facility for storage of Oxygen for their patients. The storing capacity is 5000Kg and about 4000Kg Oxygen is refilled twice in a week through tankers from M/s Ionex Air P. Ltd. Greater Noida. The hospital has obtained & have valid licence from Chief Controller of Explosives, GOI. As directed  the case was put up before BMW Committee. Complaint of Mr. Sethi and others of the area addressed to Hon;ble LG has also been received from CM office.  

11. As decided in the meeting on 18.03.08, letter for deficiencies was issued. 12. Inspected on 10.06.08 following deficiencies were observed.

      (i) Proper segregation not observed.  (ii) BMW storage site found in bad condition, spillage observed, mixing  of yellow, blue & red bags found in the storage room.General waste  also found lying near the BMWstorage  room.

     (iii) Lack of awareness / training  regarding BMW management  of Nurses / Health Care workers.

Oxygen Storage tank provided for which license obtained.

12. As per the general decision taken on 06.05.08, letter issued on 26.05.08.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d) ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Inspected.
	A letter may be sent from MS, DPCC to Medical Supdt. indicating all the deficiencies and asking for correction of deficiencies and filing of an affidavit before 14.07.2008 without fail. If the hospital fails to do so, necessary action will be taken as per BMW Rules. 


	Letter issued.
	EE (BMW) to chase up on both letters and ensure compliance. Call on 27.08.2008.



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	2
	Tirath Ram Hospital, 2 ,R.B.L,Isher Das Sawhney Marg, Rajpur Road,New Delhi -54
	165
	N-003
	28.07.06
	11.01.07

11.4.08(CTE)


	1. The HCU was inspected on 15-11-2006 and BMW management found as per rule(C/192).                    

2. Letter was sent on 1-12-2006 to submit the condo nation fee and other documents(C/193).   Condo nation fee not submitted. Earlier submitted Effluent Report shows that oil & Grease and Bio Asssay Test are exceeding the prescribed norms.      

3. The HCU did not submit noise monitoring report of DG sets.

4. Inspected on 05.11.07. At isolated storage site general waste bags as well as bags containing BMW were found kept together though separate storage facility provided at the site. DG set 125KVA (with inbuilt acoustic enclosure) & other 2 DG Sets of 110 KVA AND 18 KVA found kept in a room with acoustic treated Door & roof.  

5. The deficiencies are noted by the HCU & will not occur in future.

6. In the received reply the hospital have stated that due to shortage of supply from supplier black bags were used. 

- BMW / general waste are being placed in their respected places so that no deficiency is observed in future.- The parameters of the water testing report submitted earlier are within the norms.

-. As per the decision taken by Committee on 15.11.07, Letter was issued. Reply received.  7.  As decided in the meeting on 18.03.08, letter for deficiencies was issued.

8. Applied  for Consent to Establish on 11.04.08


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d) ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Replied for the letter issued on 25.4.2008, Effluent analysis report submitted.


	Consent to Establish granted. Compliance of letter dated 26.05.2008 be obtained. 
	Consent to Establish issued. Letter issued seeking compliance w.r.t letter dated 26.05.08 
	EE(BMW) to chase up and ensure compliance. Call on 27.08.2008.

	3


	Shanti Mukund Hospital, 2, Institutional Area, Vikas Marg Extension, Delhi-92
	144
	E-003
	07.11.07(Renewal)
	09.03.07
	1. Earlier Authorization was valid upto   16.11.07. Applied for renewal  of authorization on 07.11.07 

1.  Applied for Consent to Operate on 09.03.07 however noise monitoring  report was not submitted. for the DG Sets.

2. Letter issued. Reply received referring earlier submitted Consent to Operate application. Noise report submitted from RITES Limited which is not an approved laboratory from DPCC and results do not indicate Insertion Loss. Not Applied for Consent to Establish.

3.Letter issued. Reply received referring earlier submitted Consent to Operate application. Noise report submitted from RITES Limited which is not an approved laboratory from DPCC and results do not indicate Insertion Loss .

Not Applied for Consent to Establish.

4. As decided in the meeting on 18.03.08, letter for deficiencies was issued.

5. Reply w.r.t letter issued on 25.4.2008 received

6.Reply dated 11-06-08,w.r.t.letter dated 26-05-08. received .


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Reply w.r.t letter issued on 25.4.2008 received.


	EE to ascertain the waste water generation and then comment whether ETP is required or not. Also EE must insist for rain water harvesting structure which does not require much space. 

EE to chase up for remaining documents. 


	Waste Water quantity  ascertained and submitted in file.

	Since the waste water generation is 33 KLD  directions may be issued to the hospital by MS DPCC, to install ETP, apply for CTE and to comply with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.. Call on 27.08.2008.




	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	4


	Max Balaji Hospital, 108-A ,  IP Extension, Patparganj, Delhi-92
	134
	E-186
	20.09.07(Renewal)
	 20.11.06(CO)

18.03.08

(CTE) & 31.03.08 (CTE)
	1.Earlier Authorization  was valid upto 29-9-2007(C/33). Applied for renewal on 20.09.07 without fee for authorization. Letter was issued seeking Affidavit in prescribed form with the application. Affidavit submitted. Fee submitted 

2.Applied for Consent to Operate on 20.11.06.                                                                     2. The HCU submitted the noise monitoring report(C/38-C/40)(for DG Sets , 500 KVA 2 No.) wherein the      insertion loss is within the prescribed standards.3.Letter issued on  15.02.08, seeking Application for Consent to Establish  . 

4. Applied for Consent to Establish 

5. As decided by the BMW Committee the HCU was inspected on 28.03.08 and (i) BMW management found as per the Rules 

(ii) DG Sets are having acoustic enclosure 

(iii) ETP provided for the treatment of the waste water generated from the       hospital 

6.  Letter issued as per the decision taken on 06.05.08.

7.  Test Report of the treated effluent   submitted.

8. CTE for increasing of bed strength has also been applied on 31.03.08.

9. Letter dated 26-05-08.was issued

10.Reply dated 02-06-08.was received w.r.t letter dated 26-05-08.about doing the needful as directed along with analysis report of water effluent.

11.Reply of letter dated 26.05.08 received regarding doing the needful as directed.



	Letter issued. 

As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Reply / Effluent Test report received.


	Consent to Establish granted.for existing building. For new building, unit be asked to submit information w.r.t. built up area and also response of letter dated 26.05.2008.
	Consent to Establish issued. Letter issued 
	Consent to Operate & authorization will be given only when the unit  complies with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Inform the unit accordingly. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	5
	Pushpawati Singhania Research Institute, Sheikh Sarai Ph-II , Press Enclave Marg, New Delhi-17
	114
	S-014
	02.06.06
	Not Applied 
	1. The HCU was inspected on 3-4-2006(C/65) and BMW management not found as per rule. 

2. SCN was issued on 24-5-2006(C/68) and HCU submitted the reply (C/69) with the remark that corrective measures have been taken. 

3. Not Applied for Consent under Air Act.                                         

4. Two LDO fired boilers are installed.

5. DG sets are with acoustic enclosures.

6. Inspected on 18.12.07. following are the observations,

Sharp Management was found not as per rule.

No proper containers for BMW were found.

General waste and BMW were found mixed at isolated       storage site.

No display board at isolated storage site.

No awareness among the Health care workers.

SCN was  issued. Reply  was not received. 

As decided in the meeting on 18.03.08, letter for deficiencies was issued. Reply received.  Yet to apply for Consent to operate & consent to Establish.

7.reply dated 12-06-08.w.r.t letter dated 02-05-08.informing about submitting the application for consent to establish and consent to operate within short time.



	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Reply received .


	Call on 14.07.2008 for compliance of letter dated 26.05.2008


	
	MS .DPCC to call MS of the Hospital and persuade him to apply. Call on 27.08.2008.



	6


	Saroj Hospital, 2,  Institutional Area, Sector 14 Extn. Rohini, Delhi -85


	111
	NW-006
	23.05.07
	11.04.07
	1. HCU was inspected on 15-6-2006(C/124) ,BMW management not found as per rule.  

2. SCN u/s 5 of EPA was issued on 19-7-2006(C/126).  

3. HCU submitted the reply on 28-7-2006(C/128) wherein it is mentioned that necessary measures has been taken for the compliance of BMW management.

4. Noise Monitoring Report for DG Set not submitted.

5. HCU was inspected. BMW management found as per Rules.

6. Consent under air act and authorization under BMW rules issued as per decision taken by the committee on 115.11.07.

Letter  was Issued. Applied for Consent to Establish on 17.03.08 and as decided by the Committee Consent to Establish issued .

7.Letter dated 26-05-08.was issued 

8.No reply received.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.


	Call on 14.07.2008 for compliance of letter dated 26.05.2008


	
	MS DPCC to call MS of the Hospital to comply with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	7
	Vidyasagar Institute of Mental  Health and Nuero Sciences, 1, Institutional Area, Nehru Nagar, New Delhi – 65
	110
	S-011
	06.11.07
	Not Applied for Renewal.
	1. Authorization expired on 18-4-2007 (C/118). 

2. HCU was inspected on 13-9-2005(C/119) and BMW management found as per rule, however isolated storage site for BMW waste not provided. 

3. A letter was issued on 23-11-2005(C/121) to provide the isolated storage site and HCU submitted the reply on 7-12-2005(C/123). 

4. HCU was again inspected on 28-3-2006(C/124) and various deficiencies were observed. 

5. SCN u/s 5 of EPA was issued on 1-5-2006(C/128) for the deficiencies observed during inspection on 28-3-2006. 6. HCU submitted the reply on 16-5-2006(C/133) wherein it is mentioned that necessary rectifications has been made. 7. Applied for Authorization under BMW Rules however not applied   for consent under Air Act.

8. The HCU was inspected & following are the observations:Autoclave waste is being treated by the hospital it self.BMW and general waste were found mixed together at the isolated storage site.Earlier Letter issued .   Application for  Consent to Establish  not submitted As decided in the meeting on 18.03.08, letter for deficiencies was issued.  Reply received along with late fees requesting a week time for the completion of other formalities i.e. application for consent to establish, noise monitoring report of DG sets and application for consent to operate.

9. Reply dated 12-06-08.w.r.t dated 29-05-08.was received along with copies of registrar ion certificate and noise monitoring report.
	 As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	MS  DPCC to talk to MS of the Hospital and persuade him to apply. Call on 27.08.2008.

	8
	Brahm Shakti Hospital & Research Centre, U-1/78, Budh Vihar, Rohini, Delhi – 41


	105
	NW-013
	25.10.04
	Not Applied

	1. Provisional Authorization expired on     22-8-2002(C/7).

2. Not Applied for Consent under Air     Act.

3. Inspected on 08.11.07. 

Sharp management not found satisfactory. At isolated storage site BMW found mixed with general waste. Biohazard symbol not provided at the isolated storage site.

DG sets of 380KVA & 200KVA found kept in a room with partially acoustic treated and without adequate stack height.

4. Reply received in respect of SCN dated 13.12.07stated that the deficiencies has been rectified as observed during the inspection, however with regards to acoustic treatment of the DG sets, quotations has been sought from the various agencies and also submitted that the application for authorization under BMW Rules shall be submitted but no information provided for the consent application under Air Act.

5.Letter Issued for  Consent to Establish application however the same has not been submitted..

Inspected


6. Letlter dated 26-05-08 was issued

7.Reply dated 13-06-08.received informing about rectifying the deficiencies pointed during inspection .
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Inspected.


	Time extended upto 14.07.2008 for submission of  CTE/CTO & Authorization application. No further extension will be given.
	Letter issued.
	EE(BMW) to chase up. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	9
	R.L.K.C  Hospital ( A Unit of Dr. R.L.Khera Charitable Trust )   Pandav nagar, near . Shadipur Depot, Delhi 08
	104
	W-341
	14.03.06
	08.02.07(CTO)& 26.06.08(CTE)


	1. The HCU was inspected on 13-11-2006(C/12) and BMW management found as per rule, however isolated storage site for BMW not provided.                                        

2. HCU has not provided the waste water test report.

3. The HCU was inspected & following are the observations:

Bio-medical Waste found as per rules.

 Bio-Hazard symbol not displayed at isolated storage site & the waste was found laying near the isolated storage site 

Acoustic enclosure has been provided with the D.G. sets(380 & 320 KVA) & adequate stack height provided 

Letter issued. Reply not received. Not Applied for Consent to Establish

4. A communication on 15.04.08 received informing bio-hazard symbol displayed. Charges for water monitoring report have been deposited. Photocopy of Noise monitoring report submitted by manufacturer/ authorized dealer which is simple letters not noise monitoring report.

4. As decided in the meeting on 18.03.08, letter for deficiencies was issued.

5. Letlter dated 26-05-08 was issued

6.Reply dated 13-06-08.w.r.t letter dated 26-05-08.about asking for time for doing the needful as directed was received .




	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .


	Time extended upto 14.07.2008 for submission of  CTE application. No further extension will be given.
	Letter issued 
	Consent to Establish applied. 4 member team comprising of Dr. T.K.Joshi,, EE(BMW ), Dr. Chetna &  Trainee to inspect. Call on 27.08.2008.

	
10
	City Hospital,B-1/1, N.E.A. Pusa Road, New Delhi-60
	102
	C-101
	26.05.08
	22.11.06

03.04.2008(CTE)
	1. HCU was inspected on 24-8-2006(C/17).  BMWM found as per rule. 2. HCU did not submit the noise monitoring report of DG set.3. The HCU did not submit the waste water test report.

4. The HCU was inspected & following are the observations:

Autoclavable waste was being sent to M/s Sir Ganga Ram Hospital and no authorization for transportation was applied.  The inspection team advised not to do so and the same waste send to operator of Combined Bio-medical Waste facility. 

A.C. Plant (2 Nos.) Diesel fired 80 Tones capacity each were found installed at roof top and no adequate stack height provided. 

Bio-Hazard symbol not displayed at isolated storage site & also size of the isolated storage site is very small.  

Acoustic enclosure has been provided with the D.G. set (380 KVA) & adequate stack height provided.

A diesel fired baby boiler was also installed at the roof top without adequate stake height.

The hospital is operating at the premises of Millennium hospital which have now closed at the premises (as reported by Sh Naveen Jain (M.S) , City Hospital) .. Letter issued. Reply not received. Not Applied for Consent to Establish.

6.  Letter issued on 21.04.08. Applied for authorization on 26.5.2008. .Applied for CTE  on 03.04.08
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .


	Consent to Establish granted. Call on 14.07.2008 for compliance of letter dated 26.05.2008.
	Consent to Establish issued.
	MS DPCC to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.  Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	
       
Status of the Case / Remarks
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	11
	Bensups Hospital, Near K.M. Chowk, Sector-12, Dwarka, Delhi - 75 


	100

     
	SW-147
	22.02.07
	22.02.07
	1. HCU has applied for Authorization (C/44) and consent under Air Act(C/38).

2. HCU has not submitted noise monitoring report.

3. HCU was inspected & following are the observations:

Records of BMW not maintained.

Bio-Hazard symbol not displayed at isolated storage site.

Fee for noise monitoring report is reportedly submitted with DPCC lab.

One DG set was found with acoustic and other one was      found without acoustic enclosure.

Letter issued.  Applied for Consent to Establish.  Submitted test report for the BIO- Assay  meeting the prescribed standards.

As decided in the meeting on 18.03.08, letter for deficiencies was issued.

Reply received and has informed that the HCU is registered for 60 beds and ETP will be installed in the hospital on extension of the bed strength from 60 to 100, affidavit in this regard has been submitted. 
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.


	Consent to Establish granted. EE to ascertain the waste water generation and then decide for ETP in the next meeting. Call on 14.07.2008.
	Consent to establish issued. Waste water generation ascertained & submitted in file.
	MS DPCC to call MS of the hospital and ask  to complete CTE application with ground water source details, CGWA clearance and waste water generation and treatment facility. If he does not respond properly, MS to issue directions accordingly. Call on 27.08.2008.

	12
	Delhi Heart and Lung Institute, 3-M.M II ,Panchkuian Road,N.Delhi-55
	100

	C-089
	04.09.06
	19.3.2008(CTE)

Applied for CTO on 15.05.2008
	1. Authorization expired on 27-10-2006(C/29). 

2. HCU was inspected on 2-8-2006(C/37) during which BMW Management found as per rule.  

3. HCU applied for renewal of authorization on 4-9-2006(C/45).  

4. HCU did not apply for consent under Air Act. Having DG Set of 500 KVA with acoustic enclosure.

5. Inspected on 05.11.07 & BMW management found as per rules.  

6. Letter issued. Reply not received..

7. As decided in the meeting on 18.03.08, letter for deficiencies was issued.

Applied for Consent to Establish.

8. Applied for CTO on 15.05.2008
9.Reply dated 16-06-08.received regarding during g the needful as directed in the letter dated 26-05-08


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d) ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .

 HCU has applied for CTE and CTO. 
	EE to chase up. Call on 14.07.2008.

	EE(BMW)  talked to the official (s)

of the hospital .
	Consent to Establish applied. 4 member team comprising of Dr. T.K.Joshi,, EE(BMW ), Dr. Chetna &  Trainee to inspect. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	13
	Devki Devi Foundation ( Max Devki Devi Heart & Vascular Institute ) 2, Press Enclave Road, Saket, New .Delhi -17.


	193
	S-275
	30.11.04
	26-9-06
	1. HCU was inspected on 22-9-2006(C/47) during which some deficiencies were observed. 

2. SCN u/s 5 of EPA(C/50) and SCN under BMW Rules(C/51) were issued on 27-11-2006. 

3. HCU submitted the reply on 7-12-2006(C/53) wherein it is mentioned that the necessary measures have been taken. 

4. The HCU has installed an ETP to treat the liquid BMW.

5. The HCU is Having DG Set of 1000 KVA with acoustic enclosure. 

6. The HCU applied for consent under Air Act on 26-09-06 with noise monitoring report.

7. 3 years .expired since the earlier application was received for Authorization under BMW Rules and the HCU submitted fresh authorization application . 

Applied for Consent to Establish.

8. Pointwise reply of letter dated 26.05.08 received regarding doing the needful as directed.

9. Inspected on 12.07.08.

10 After the inspection on 12.03.08 letter alongwith photograph of containers at the storage site submitted by the Hospital on 14.07.08.

\


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

File sent to Chairman, DPCC. To be inspected by Chairman.


	MS to inspect and report on 14.07.2008.



	Inspected on 12.03.08.
	MS DPCC to issue directions to MS of the hospital to get CGWA clearance and submit expeditiously. The adjacent  Super Specialty hospital which also belongs to Max Group  must get the Environmental Clearance  because its capital cost was more than Rs. 50 crores therefore comes under EIA notification 2004. MS to issue directions  immediately and include the name of this hospital in this list.  


	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	14
	Jessa Ram Hospital (A unit of R.B.Seth Jessa Ram & Bros Charitable Hospital)  WEA Karol Bagh,New Delhi -05
	100
	C-008
	12.03.07
	07.11.05 & 30.10.07

23.5.2008(CTE)
	1. The authorization expired on 11.6.06 (C/91).   

2. HCU was inspected on 4-8-06(C/95) during which segregation of BMW at general ward and nursing home not found as per rule.

3. SCN u/s 5 of EPA was issued on 10-11-06(C/109). 

4.HCU submitted the reply on 24.11.06(C/118) wherein it is mentioned that

 necessary measures have been taken. 

5. Consent to operate expired on 24.11.05.

6. As per Copy of Receipt enclosed, applied for renewal of consent to operate on 7-11-05(C/114).( Consent Application not available). Now HCU has submitted fresh consent application under Air Act on 30.10.2007.

7. HCU has not submitted waste water test report & submitted old noise monitoring reported dated 28.05.03.

8. The HCU was inspected & following are the observations:

Bio-medical Waste found as per rules. 

Sharp management found satisfactory.

Isolated storage site for BMW is provided.

Acoustic enclosure has been provided with the D.G. sets (125,200 & 500 KVA) & adequate stack height provided.

Letter issued. Reply not received. Applied for Consent to Establish

9. As decided in the meeting on 18.03.08, letter for deficiencies was issued.

10. Applied for Consent to Establish on 23.05.08

11.As per the general decision taken on 06.05.08, letter issued.

12.Reply dated 10-06-08. with reference to our letter dated 26-05-08 .informing about do ing the needful as directed .

13. 7Letlter dated 26-05-08 was issued

14.Reply dated 10-06-08.received w.r.t letter dated 26-05-08.about during the needful as directed.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d) ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Reply received w.r.t. letter dated 21.4.2008. 

EE(BMW)  talked to the official (s)

of the hospital .

Reply received
	Consent to Establish granted. Call on 14.07.2008 for compliance of letter dated 26.05.2008.
	Consent to establish issued.
	 4 member team comprising of Dr. T.K.Joshi,, EE(BMW ), Dr. Chetna &  Trainee to inspect. Call on 27.08.2008. 

Seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	15
	Shroff Charity Eye Hospital, 5027, Kedar Nath Road ,Daryganj, New Delhi-02
	56
	C-011
	26.05.06
	22.09.06(CO)

& 09.06.08 ( CTE)
	1. Authorization expired on  4-7-2006(C/94).  

2. HCU applied for renewal on     26.05.06 (C/117). 

3. HCU was inspected on 14-8-2006(C/122)     during which BMW management found as     per rule. 

4.HCU has applied under Air Act on 22-9-  2006(C/114) but noise monitoring report    of DG sets ( 100, 75,125 KVA) not     submitted.

5.Inspected on 05.11.07 Management was    found satisfactory, however Biohazard    symbol not provided at isolated storage    site. 125KVA & 380KVA DG sets kept In acoustic treated room with adequate    stack Height.

6. HCU replied that deficiencies have been rectified.

 7. As decided in the meeting on 18.03.08, letter for deficiencies was issued.  

8.Reply dated 18-06-08.along with waste water taste report received .


	EE(BMW)  talked to the official (s)

of the hospital .


	Consent to Establish granted.  Letter be issued similar to letter dated 26.05.2008 regarding solar water heating system etc.
	Consent to Establish issued .

 Letter issued.


	Seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	16
	MGS Hospital, West Punjabi Bagh , Rohtak Road, New Delhi,-26  
	100
	W-008
	21.01.08
	 08.02.08
	1. Authorization granted & Valid upto 07.02.08 

2. The HCE was inspected on 5-1-2007(C/65-C/66) and following deficiencies were observed: (a). Sharp Management not found satisfactory. (b). Segregation of BMW was being carried out at isolated storage site. (b). BMW collection bags not found labeled and tied.

3.  Applied for consent under Air Act.   

5. The HCU was inspected on 11.01.08 & following are the observations:

Bio-medical Waste found as per rules. 

Sharp management found satisfactory.

Isolated storage site for BMW provided.

Acoustic enclosure has been provided with the D.G. set (180 KVA) & adequate stack height provided.

6. As decided in the meeting on 18.03.08, letter for deficiencies was issued.

    Reply received. Applied for consent to Establish on 22.05.08


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .


	Consent to Establish granted. EE to check the waste water generation and also check the number of trees planted.
	Consent to establish issued. 

Waste Water generation checked from the application & no of trees enquired from the hospital 
	In view of 10 KLD ground water use . Seek CGWA clearance. CTE application shows waste water generation of 20 KLD ask the unit to install ETP and confirm by 27.08.2008. Call on 27.08.2008.



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	17
	Kalra Hospital, A- 5 & 6, Kirti Nagar, New Delhi-15
	100
	W-012


	04.06.07
	Valid upto 14.09.09
	1. Authorization expired on 28-6-2007(C/108). 

2. HCU applied for renewal of authorization on 04.06.07(C/118). 

3. Consent to Operate under Air Act is valid upto 14-9-2009(C/110). Having  DG Sets of 180 KVA &. 320 KVA( 2 NO.) , Not submitted Noise Monitoring Report as asked vide consent order issued on 20.11.06. 

.4. The HCU was inspected & following are the observations:

Bio-medical Waste found as per rules. 

Sharp management found satisfactory.

Isolated storage site for BMW provided, however needs further improvement by providing proper enclosure of the site of storage.

Acoustic enclosure has been provided with the D.G. sets (62.5 KVA, 180 KVA & 2X320 KVA) however  adequate stack height not provided. & 62.5 KVA D.G. Set not mentioned in the consent order as well as consent application.

A copy of noise monitoring report provided during the inspection but the same shows that only one D.G. set (180 KVA) found operational during the monitoring.   

5. As decided in the meeting on 18.03.08, letter for deficiencies was issued.

  6. .Letlter dated 26-05-08 was issued

7.Reply dated 11-06-08.w.r.t letter dated 26-05-08.informing about during the needful as directed received.

	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	Ask the unit to apply for CTE, comply with the  directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008. 4 member team comprising of Dr. Joshi, EE, Dr. Chetna,  Trainee to inspect after receipt of  CTE Application  to check whether deficiencies corrected. Call on 27.08.2008.




	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	18
	Max  Hospital ( A unit of Max Health Care Institute Ltd.) HB Twin Towers, A 2,3,&4, Netaji Subash Place, Wazirpur, Distt. Centre, Delhi-34
	92
	NW-017
	29.12.06(Renewal)
	17.01.08 (CO), 18.3.2008- CTE
	1. Earlier authorization was valid up to 16-12- 2006(C/50). Applied for renewal of authorization on 29.12.06.  

2. The HCU had not applied for consent under Air  Act.

3. Inspected on 08.11.07. At isolated storage site bags containing BMW and general waste kept in same room without proper separation. One of the Red bag containing BMW found kept inside black bag meant for general waste. Segregation of BMW particularly at labor room found not as per rule. Biohazard symbol not found displayed on the container & at the door of the isolated facility. Proper BMW carrying facility lacking. Three DG sets (2X320KVA & 1no. 180 KVA) found, work for acoustic enclosure for two DG sets (180KVA and 320KVA) was going on. Second 320 KVA DG set was with inbuilt acoustic enclosure, Adequate stack height for all the DG sets not provided. 

4.SCN issued for the above . Reply received regarding rectification measures taken.

5. Letter issued seeking Consent to Establish application, applied for Consent to Establish on 18.3.2008. Inspection conducted.

Waste water test repot for the treated effluent from the ETP has been asked from the HCU. 

As decided in the meeting on 18.03.08, letter for deficiencies was issued.

Test  report received .  


	EE(BMW)  talked to the official (s)

of the hospital . Test report received.


	Consent to Establish granted. EE to check the built up area for Environmental Clearance. Letter be issued similar to letter dated 26.05.2008 regarding solar water heating system etc.
	Consent to Establish issued. Letter issued. Regarding built up area etc. the matter was submitted in file. 
	Since the use of  ground water  is 40 KLD, ask the unit to file CGWA clearance. Since the waste water generation is 45 KLD ask for adequacy report of ETP. Call on 27.08.2008.




	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	19
	National Heart Institute, 49- 50, Community Centre, East of Kailash, New Delhi-65
	80
	S-069
	07.03.07
	Not Applied



	1. Provisional Authorization Expired on 30-10-    2004(C/39).

2. HCU did not apply for consent under Air Act.

3. Inspected & found that BMW management was as per rule.

4.  The HCU was advised to apply under Air Act.

Earlier Letter was issued.  Not Applied for Consent to Establish

As decided in the meeting on 18.03.08, letter for deficiencies was issued.   

5.No reply 


	EE(BMW)  talked to the official (s)

of the hospital .


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	MS  DPCC to issue directions to MS of the hospital to apply for Consent to Establish . Call on 27.08.2008.

	20
	Sitaram Bhartia Institute of Science & Research, B-16, Qutub Institutional Area, New Delhi – 16
	71
	S-051
	11.10.07
	11.10.07

29.04.08(CTE)
	1. The authorization expired on 6-5-2007(C/221 of the concerned file).     

2. The consent to operate expired on 2-9-2005(C/26 of the concerned file). 


2. HCU had submitted the applications for Renewal of authorization under BMW Rules and for consent under Air Act.

3. The HCU was inspected & BMW mgt found as per rule.

4. ETP to treat the liquid BMW is also installed.

Earlier Letter issued.  Not Applied for Consent to Establish

As decided in the meeting on 18.03.08, letter for deficiencies was issued.

Applied foe Consent  to Establish on 29.04.08.

5.Reply dated 20-05-08.was received .regarding submission of balance fee of 2years  for the authorization amount.

	EE(BMW)  talked to the official (s)

of the hospital .

Reply received in response to letter dated 02.05.2008. NMR , stack monitoring report of boiler and effluent analysis report (without parameters of BOD and Bio assay Test) submitted


	Consent to Establish granted.  Letter be issued similar to letter dated 26.05.2008 regarding solar water heating system etc.
	Consent to Establish issued.

Letter issued.
	Ask the unit to comply  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	21
	Deepak Memorial Hospital, 5, Institutional Area,  Vikas Marg Extn. 2 , Delhi-92


	60
	E-006
	19.02.07
	29.5.2008(CTE)

29.5.2008(CTO)
	1. Earlier Authorization Expired on  18-3-2007 (C/72). 

2. HCU did not apply for consent under Air Act. 

3. Inspected on 01.01.08. During the inspection The management of BMW w.r.t. segregation, colors coded bags were as per rule.

4. Isolated storage site provided but no display board/bio- hazard symbol displayed.

5. Having 4nos. of DG sets of capacity 82,5 KVA, 200KVA, 500 KVA and 25 KVA. 82,5 KVA DG Set  was without the acoustic enclosure and 25 KVA capacity DG Set was non operating condition. Stack heights for the DG sets were inadequate.      

6. Letter Issued based on the decision taken on 15.01.08. Reply not received.      

Earlier Letter Issued.   Applied for Consent to Establish

As decided in the meeting on 18.03.08, letter for deficiencies was issued

7.As per the general decision taken on 06.05.08, letter issued.

8.R eply  received . Letter dated 17-06-08. about the authorization under r  BMW rules 

9.Reply dated 17-06-08.w.r.t dated 25-04-08.regarding authorization under BMW rules received.


	EE(BMW)  talked to the official (s)

of the hospital . HCU has applied for CTE and CTO on 29.5.2008.


	Ask for affidavit for correction of deficiencies observed during the inspection. 
	Letter issued.
	CTE applied. Issue reminder for affidavit for correction of deficiencies. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	22
	Nazar Kanwar Surana Hospital(A Unit of Bram Health Care (P) LTD), 219/220, N.K. Surana Marg, Gulabi Bagh, Delhi - 07


	60
	N-095
	05.05.06
	Not Applied
	1. HCU applied for fresh authorization on 5-5-2006(C/7).

2. HCU did not apply for consent under Air Act. 

3. Inspected on 02.01.08. 

4. During the inspection the BMW was not as per rule;   

-No isolated storage site  provided

-Sharp management was found very poor, needle destroyer was found out of order.

- Although color coded bags placed in the closed containers were as per rule but the segregation was not as per rule at the causality & at nursing station where general waste was placed in yellow bag.

- DG set of capacity was found placed in acoustic enclosure with adequate stack height.

-advise to apply for consent.

5. Letter issued on 15.02.08 seeking application for Consent to Establish  & for correction of Deficiencies observed during the inspection. However  reply not received & not applied for consent to Establish. 

6 As decided in the meeting on 18.03.08, letter for deficiencies was issued.

7.Reply dated 12-06-08.w.r.t phone  call from Mr.singh on 11-06-08.regarding action taken report.


	EE(BMW)  talked to the official (s)

of the hospital . Reply received


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	MS DPCC to issue directions for applying for Consent to Establish and for correction of deficiencies. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	23
	Venu Eye Institute & Research Centre, 1/31, Institutional Area, Phase – 2 ,  Sheikh Sarai, New Delhi-17
	60
	S-017
	18.09.06
	16.03.07
	1. The authorization expired on 5-10-2006(C/75). 

2. Having 3 DG Sets. Two are provided with acoustic enclosure & one without acoustic. 

3. Inspected & BMW mgt found as per rule except that bio-hazard symbol at isolated storage site was not provided.

Letter issued. Reply  received informed regarding rectification of deficiencies . 

As decided in the meeting on 18.03.08, letter for deficiencies was issued.

4.Reply dated 12-06-08 w.r.t letter dated 29-04-08 regarding consent  to estliblish under air and water act was received 
	EE(BMW)  talked to the official (s)

of the hospital . Reply received


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	MS DPCC to issue directions for applying for Consent to Establish . Call on 27.08.2008.

	24
	Jeewan Hospital & Nursing Home Pvt. Ltd., Gali No.1  Jeewan Nagar, New Delhi-14
	60
	S-016
	04.01.08
	 04.01.08
	1. Provisional Authorization expired on  25-10-2005(C/31 of the concerned file).    

2. Earlier  HCU had not   ubmitted the application for authorization under BMW Rules and for consent  to operate under Air Act.

3. Inspected & following are the observations:

BMW mgt is not found as per rule.

Not applied for auth & consent.

Three D.G. sets are without acoustic enclosure.

No isolated storage site is provided.

4. After the inspection the unit has applied for Authorization & informed regarding rectification measures taken.SCN Issued. A letter received regarding deficiencies rectified.  Applied for Consent to Operate. under Air Act.As decided in the meeting on 18.03.08, letter for deficiencies was issued.

5.Reply dated 17-06-08.regarding renewal of authorization 
	EE(BMW)  talked to the official (s)

of the hospital .


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	MS DPCC  to issue directions for applying for Consent to Establish. Call on 27.08.2008.

	25
	Red Cross Maternity & Child care Hospital,  New Seemapuri, Delhi-95


	57
	NE-006
	09.04.07
	03.03.2008(CTE)
	1. Authorization expired on 14-5-2007 (C/31).   2. HCU applied for renewal of authorization on 9-4-2007(C/43).                                                                                  

2. HCU did not apply for consent under Air Act.   

3. Letter Issued. Applied for Consent to Establish.

inspected.

As decided in the meeting on 18.03.08, letter for deficiencies was issued.


	Inspected. Replied on 26.5.2008. The unit still has not submitted CTO application and NMR.
	Issue letter for correction of deficiencies. Call on 14.07.2008.
	Letter issued.
	Issue reminder for correction of deficiencies. Call on 27.08.2008.




	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	26
	Metro Hospital & Cancer Institute ( Earlier Anand Hospital,) 21, Community Centre, Preet Vihar, Delhi-92
	52
	E-007
	25.07.05
	  Applied .

(CTE on 01.07.08) 
	1. Provisional Authorization expired on 23.09.04. HCU applied for renewal of authorization on 25-7-2005(C/70). 

3. HCU was inspected on 13-7-2006(C/71-C/72) during which BMW management not found as per rule.

4. SCN u/s 5 of EPA(C/81) and SCN for refusal of authorization under BMW Rules(C/82) were issued on 10-11-2006 but HCU did not reply the same.

5. HCU did not apply for consent under Air Act  

6. From the same premises an application for authorization under BMW Rules has been received in the Name of Metro Hospital & Cancer Institute ( A Unit of Anand Health Care LTD.) on 06.08.2007( having 70 beds).

7 Inspected on 01.01.08. as informed the hospital have sold out to Metro Hospital & Cancer Institute since Jan.2006.

8. Segregation of BMW at the causality was not as per rule.

9. Isolated storage site not proper. The BMW kept in the Kaccha room constructed near new construction going on for the said hospital in the nearby plot..

10. The general waste  as well as BMW are being kept in the said room altoghether without proper separation. Resegregation of the waste was observed at the site,

11. DG set of 320 KVA was acoustically treated without having adequate stack height.  

Notice Issued to Metro Hospital and Cancer Institute which was inspected and existing in the premises of Anand Hospital. (Anand Hospital sold out to Metro Hospital & Cancer Institute).

As decided in the meeting on 18.03.08, letter for deficiencies was issued.

12.Reply dated 13-06-08.w.r.t letter dated 25-04-08.was   

received asking for a week time .

 13. Applied for Consent to establish and Consent to        Operate.


	EE(BMW)  talked to the official (s)

of the hospital .


	Time allowed till 14.07.2008.
	Applied for Consent to Establish & Operate.
	CTE applied. Ground water use  is 20 KLD, therefore, CGWA clearance is required. Since the consumption of water is 20 KLD, the unit may be asked to file correct waste water generation figure and based on the waste water figures, decision for ETP  may be taken. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	27
	Jeevan Anmol Hospital, Mayur Vihar Phase-I , Delhi-91
	51
	E-015
	23.03.04
	19.11.07(CT) 

12.06.08 (CTE)
	1. The HCU applied for authorization on  23-3-2004(C/47),  provisional authorization  was granted which expired on 23-3-2005(C/49) thereafter not applied for Authorization under BMW Rules.  

 2.  HCU was inspected on 13-10-2005 and BMW management found as per rule(C/54) except adequate stack height with DG sets. 

3. A letter was sent on 3-5-2006(C/55) wherein they were directed to install the adequate stack height and informed that stack has been increased.(C/58). 

4. The three year period of the authorization has been expired on 23.03.2007, however not applied afresh.. 

5. Application received for consent, however noise monitoring report for DG Sets not submitted.
6. Inspected on 01.01.08. During the inspection the management of BMW at the source of generation was found as per rule w.r.t. segregation, color coded bags.

7. Existing facility for storage of BMW at isolated storage site found not proper since it is kept in wooden cabinets at open along the wall near causality.

8. No bio-hazard symbol provided at the isolated storage site i.e on wooden cabinet.

9. 100KVA DG set found installed in acoustic enclosure and stack height is about 10’ from roof room i.e. adequate in height.

Letter  was Issued.  Not Applied for Consent to Establish.

As decided in the meeting on 18.03.08, letter for deficiencies was issued.applied for CTE on 12.06.08.



	EE(BMW)  talked to the official (s)

of the hospital .


	Consent to Establish granted.  Letter be issued similar to letter dated 26.05.2008 regarding solar water heating system etc.
	Consent to Establish issued.

Letter issued.
	Reminder to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	28
	Park Hospital, 12, Meera Enclave (Chowkhandi) Near Keshavpur Depot, Outer Ring Road, New Delhi-18


	100
	W-326
	24.07.07
	25.07.07(operate)

&  14.03.08( Establish) & 10.06.08 (Establish)
	1. HCU was inspected on 17-3-2005(C/13) during which it was observed that no isolated storage site for BMW provided.  2. A letter was sent on 17-4-05(C/15) but HCU did not reply. 

3. A complaint has also been received against the management of BMW(C/19) in April 2007. As per Letter from DHS Dated 22.08.07 inspection was done by DHS official and it was informed that complaint could not be established.(C/ 48)

4. HCU has applied for authorization on 24-7-2007(C/28) again and no authorization was issued for the application submitted in this office on 14-6-2004(C/12).  

5. Noise Monitoring Report for DG Set submitted showing meeting the norms for insertion loss.

6. The HCU was inspected & following are the observations:

Now Hospital has increase the capacity of beds upto 100 beds & not submitted waste water test report.

Bio-Medical Waste segregation through being done and color coding system followed however from perusal of BMW  records and also observing the conditions of BMW Containers, proper segregation is not being done and needs improvement in this regards.  

Isolated storage site for Bio-medical Waste not provided. It was informed that BMW from various floors is collected and given to Synergy Waste Management Pvt. Ltd. for the disposal. 

Sharp management found satisfactory. 

Hospital is having 2 D.G. Sets of 62.5 KVA & 20 KVA  ( with   acoustic enclosure,)  but adequate stack  height  not provided with D.G. Sets. Both D.G. Sets were kept outside the Hospital (backside of hospital.) in which 20 KVA D.G. Set not in use (as reported) & also same was not mentioned in the consent application by the Hospital. 

7. Letter issued asking the unit to apply consent to establish under the Air & water Act.

8. Applied for Consent to establish on 14.03.08 along with project report and required fee and affidavit. Informed regarding rectification of the deficiencies observed during the inspection. Fee submitted for testing of tha waste water Characteristics. Submitted Affidavit that  another DG Set (Old One ) with acoustic enclosure however not working/ Operation. 

9.  Letter for deficiencies issued on 21.04.08. Hospital submitted waste water analysis report from DPCC lab. Indicating the analyzed parameters are within the limit.

10. Letter issued as per the decision taken on 06.05.08. Reply received.

11. Again submitted consent to establish on 10.06.08.

12.Reply dated 30-05-08.with reference to letter dated 26-05-08.was received mentioning inability to put rain water harvesting system .

13. Reply received w.r.t letter issued after the meeting on 13.06.08 & informed that ETP will be installed. Regarding rain water harvesting it is informed that Building is of old period & at that time rain water harvesting was not mandatory. 


	Letter issued.

As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d) ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Reply received, NMR submitted.
	Insist for compliance of all the directions mentioned in letter dated 26.05.2008. Time allowed till 14.07.2008.
	Letter issued.
	It must be clarified to the hospital that without compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008 Consent to Establish  cannot be granted. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	29
	Bhatia Global Hospital  307-308, Ambica Vihar, New Delhi-87
	50
	W-007
	05.08.04
	 Applied (CTE on 23.06.08)
	1. Provisional Authorization Expired on 22-8-2002(C/9).  2. HCU applied for authorization on 5-8-2004(C/66) and three years has been expired on 4-8-2007. 

3. HCU did not apply for consent under Air Act.

4. The HCU was inspected & following are the observations:

Proper co- operation not provided to the inspecting team by the hospital Staff.. 

Proper segregation of BMW not observed. Waste including general waste found mixed with BMW and separate containers/bins not provided.

Proper training is required for medical staff regarding BMW Management. 

Sharp management found not satisfactory.

Isolated storage site for BMW is not provided. Plastic containers kept in open without following proper colour coding and bio-hazard symbol not provided.

Record for BMW not maintained properly.

Acoustic enclosure has been provided with the D.G. set (160 KVA) & adequate stack height provided.

5.  As decided in the meeting on 18.03.08, letter for deficiencies was issued.

6. Applied for Consent to Establish/ Operate .


	EE(BMW)  talked to the official (s)

of the hospital .


	EE to chase up. Call on 14.07.2008.


	EE(BMW)  talked to the official (s)

of the hospital .


	Since ground water  use is 17 KLD, CGWA clearance is required. Since waste water generation is 25 KLD, unit may be directed to install ETP expeditiously.

Call on 27.08.2008.



	30
	Millenium Hospital, B-1/1, Pusa Road, New Delhi -
	50
	C-009
	15.09.04
	Not Applied
	1. Authorization expired on 29-8-2004(C/50).   

2. HCU applied for renewal on 15-9-2004(C/67)  but the affidavit was not proper. 

3. Show cause notice was issued on 19-2-   2007(C/68). Reply not submitted.

4. Three years already lapsed on 14.09.07 since applied for authorization on 15.09.2004.

5 . The HCU was inspected & following are the observations:

Millennium Hospital is closed and now M/s City Hospital is operating in the same premises. (as reported by Shri Naveen Jain (MS)  City Hospital)

File Closed. No further action required.


	         

         -------------


	No further action.
	----------
	No action. 

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	31.
	Surya Hospital

388/11C ,East Azad Nagar, Delhi-51


	55
	E-013
	Applied for Renewal of authorization on 11.6.2008.
	 23.06.08( CTO & CTE.both)
	1. Earlier Authorization expired on 6-10-2006(C/70 ).

2. SCN  was issued on 23-3-2007(C/83) and 20-6-2007(C/84) since had  not applied  for authorization.

3. Inspected on 01.01.08& following were the main observations.    

-Having two nos. of DG sets of capacity 125KVA and 50 KVA. 125 KVA DG set was placed in acoustic ally treated room and 50 KVA DG set was without acoustic placed out side the acoustic room. Stack heights for the DG set are above the building roof about 6’.

- BMW Management was not as per rule. The sharp management was very poor, needle destroyers were found out of order, no puncture proof containers were being used.

- at the isolated storage site situated in other back lane building, the BMW were found mixed with the general waste. No color caded bags were found in use at isolated storage site. No bio-hazard symbol was found displayed.- Record of BMW not shown. 

Letter Issued. Reply received.  Informed regarding management of BMW as per instructions. Noise monitoring report submitted for 125 KVA DG Set & informed regarding removal of 50 KVA DG Set  

Applied for Consent to Establish & Consent to Operate on 23.06.08. As decided in the meeting on 18.03.08, letter for deficiencies was issued.  

6.Applied for authorization under BMW rules on 11-06-08. 


	EE(BMW)  talked to the official (s)

of the hospital . Applied for renewal of Authorization.


	EE to chase up. Call on 14.07.2008.


	EE(BMW)  talked to the official (s)

of the hospital .


	Since ground water  use  is 07 KLD, CGWA clearance is required. Since waste water generation is 7 KLD ETP is required and must be installed expeditiously. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	32.
	Kukreja Hospital & Heart Centre, C-1, Vishal Enclave, New Delhi-27


	103
	W-018
	18.01.08(rEnewal)
	27.11.07(operate)

& 13.03.08(Establish)
	1. The Authorization expired on 02-9-2007(C/42) thereafter applied for renewal. On 18.01.08

 2. Applied for Consent on 27.11.07 , however  noise monitoring report for DG Set not submitted. Submitted fee for noise monitoring.

3. The HCU was inspected & following are the observations:

Now Hospital has increased the capacity of beds upto 103 beds & not submitted waste water test report.

Proper segregation and storage of BMW not observed. 

Sharp management found satisfactory.

Isolated storage site for BMW is not proper i.e not covered, not displayed by bio-hazard symbols and general waste is also kept with BMW.

Acoustic enclosure has been provided with the 4 D.G. sets (2X125 KVA& 2X 62.5KVA) however adequate stack height not provided.

Recorded of BMW could not be shown since concerned  person was not available 

4. Letter issued. Reply received Applied for Consent to Establish. 

 Informed regarding noise monitoring conducted by DPCC. & also about   rectification of the deficiencies.  Test report asked for the waste water not   submitted. 

5.Reply dated 10-06-08.w.r.t letter dated 26-05-08.about doing the needful as directed was received.
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d) ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital . Reply received.


	Consent to Establish granted. Call on 14.07.2008 for compliance of letter dated 26.05.2008.
	Consent to Establish issued.
	Since 3 KLD use  of ground water, ask him to apply for CGWA. clearance Since waste water is 2 KLD, unit may be asked to install mini ETP and CTE form is required to filled properly. Call on 27.08.2008.

	33.
	Jivodaya Hospital, Ashok Vihar, Phase-1, Delhi-52


	65
	NW-014
	29.01.08
	04.02.08(CTO)

05.05.2008(CTE)
	1.Earlier  Authorization was  valid up to   20.03.2008 (C/58). Applied for renewal of authorization on 29.01.08

2. HCU had not applied for consent under Air Act.

3. Inspected on 02.01.08 and following main observations were made.

-the management of BMW was found as per rule w.r.t. sharps, color coded bags as per rule. Segregation of BMW was also found as per rule.

- Covered containers being used for the waste storage.

-Having 2nos of DG set with acoustic treated i.e. placed in acoustically treated room of capacity 125 KVA and 43 KVA. Stack height was found adequate in height. As informed that 43 KVA DG set is standby.

- Isolated storage site provided with bio Hazard symbol displayed.

- Advised to apply for consent under Air Act. 

4. Applied for Consent to Operate on 04.02.08. Old  Noise monitoring report    for DG Sets( 125 & 43 KVA) submitted along with the Consent Application.

5 .As decided in the meeting on 18.03.08, letter for deficiencies was issued.

6. Applied for Consent to Establish  on 05.05.08 

7.NO Reply

	EE(BMW)  talked to the official (s)

of the hospital.


	Consent to Establish granted.  Letter be issued similar to letter dated 26.05.2008 regarding solar water heating system etc.
	Consent to establish issued.

Letter issued.
	Seek compliance  with directions issued w.r.t decision taken on 13.06.08.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	34.
	Mai Kamliwali Hospital, J-block, Community Centre, Rajouri Garden, New Delhi-27
	50
	W-022
	 24.09.07
	Not Applied
	1. The Authorization was valid up to 28-10-2007(C/ 70 ). Applied for renewal of authorization on 24.09.07.

2. HCU did not apply for consent under Air Act.

3. The HCU was inspected & following are the observations:

Proper segregation and  colour coding not followed as per BMW Rules only black plastic bags is being used for all kind of BMW Waste.

Sharp management found satisfactory.

Isolated storage site for BMW is not provided and bio-hazard symbol not provided on the containers

Acoustic enclosure has not been provided with the D.G. set ( 62.5 KVA ) & adequate stack height not provided.

Record of BMW could not be provided during the inspection. 

4. Letter issued on 15.02.08. Reply received. Not Applied for Consent to Establish. Not informed regarding the rectification of the deficiencies observed during the inspection.

5.  As decided in the meeting on 18.03.08, letter for deficiencies was issued.

6.Reply dated 12-06-08.received Informing about  rectifying the deficiencies observed during inspection and asking about the procedure to be adopted to apply for consent to establish   under the Air /Water act

Another letter received referring the earlier submitted reply.


	EE(BMW)  talked to the official (s)

of the hospital. Reply received.


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	MS DPCC to issue directions to apply for Consent to Establish and to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008..

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	35.
	Shree Jeewan Hospital, 67/1, New Rohtak Road, Delhi -05
	52 nos.
	W-024
	29.06.05 & on 03.03.08
	03.03.08
	1. Authorization Expired on 3-4-2004(C/34).

2. The HCU applied for renewal on 29-6-    2005(C/63)& on 03.03.08

3. HCU was inspected on 22-3-2006(C/64) during         which BMW management not found as per rule. Hospital was again inspected on 27.09.2006 and BMW management found as per rule.

 4. HCU had not applied for consent under Air Act. Having DG Set of 75 KVA with acoustic enclosure. 

5. The HCU was inspected & following are the observations:

Proper segregation of BMW not observed. Plastic bins provided do not contain proper colored plastic begs for storage of BMW.

Sharp management found satisfactory.

Isolated storage site for BMW provided however storage bins not found properly maintained and BMW found kept without proper color coding/ without proper plastic bags in the bins. Condition inside storage facility also found poor.

Record of BMW not found maintained.

Acoustic enclosure has been provided with D.G. set (65 KVA) & adequate stack height is provided.

6. Letter issued 0n 15.02.08. Reply received.  Applied for Consent to  operate however not applied for Consent to Establish. Informed regarding rectification of the deficiencies. 7.  As decided in the meeting on 18.03.08, letter for deficiencies was issued.

7.Reply dated 29-04-08.w.r.t letter dated 21-04-8 regarding submission of  documents related to consent under air / water acts.


	EE(BMW)  talked to the official (s)

of the hospital .


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	MS DPCC to issue directions to apply for Consent to Establish and to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	36.
	Jaipur Golden Hospital, 2, Institutional Area , Sec-3, Rohini, Delhi-85
	256
	NW-003
	0.9.06.08
	23-Aug-05

 
	1. HCU applied for authorization on 15-9-2004 & THEREAFTER ON 09.06.08. 2. HCU was inspected on 5-10-2006(C/131) and BMW management found as per rule except liquid BMW as bio-assay parameter was found beyond the limit. 

3.SCN was issued for the deficiencies on 02.05.06 In response to the SCN issued, Hospital had informed regarding rectification measures taken. Inspection was carried out on 05.10.06(131/c)however deficiencies were observed..

 4. HCU applied under Air Act on 23-8-2005(C/177) without the noise monitoring report of DG sets. As per test report submitted by the HCU all parameters are within limit except bio-assay test.

5. As per the decision taken in the meeting held on 1-8-2007, a letter has been issued on 27-8-2007 to HCU to submit the fresh water analysis report within 30 days. In response to the said letter it was informed that NPC does not have facility to conduct Bio Assay Test.

6. The copy of the letter had also been sent to National Productivity Council to monitor the parameters at the earliest.

7. A reminder letter was sent to HCU to submit the water monitoring report before next meeting to be held on 3-10-2007.

8. A copy of this letter was sent to NPC also.
9. Letter issued on 13.12.07 to apply  a fresh for authorization under BMW Rules and to submit test report for  Bio-assay  test from I.P. University or I.I.T. Delhi .  Reply was  not received and as decided on 15.01.08, a letter was issued seeking application for Consent to Establish , however reply not received & not applied for Consent to Establish.

As decided in the meeting on 18.03.08, letter for deficiencies was issued.

Inspected. DG Set of 1010 KVA found installed without adequate stack height and no stack analysis report submitted. Bins for storage needs to be properly labeled.

Application for renewal of authorization filed on 09.06.2008

10.Latter dated 26-05-08 was issued 

11.Reply dated.11-06-08.w.r.t letter dated 26-05-08.regarding  doing the needful as directed.


	Letter issued.

As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building. Application for renewal of authorization filed on 09.06.2008.


	Ask the unit to apply for Consent to Establish and compliance of letter dated 26.05.2008.

Also EE to chase up. Call on 14.07.2008.
	Letter issued .
	MS DPCC to issue directions to apply for Consent to Establish and to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	37
	Sunder Lal Jain Charitable  Hospital, Ashok Vihar, Phase III, Delhi-52
	178
	NW-007
	4- Dec-06
	10-Jan-07
	1. HCU Applied for authorization on 4-12-2006(C/ 145).                                                                    2. HCU was inspected on 25-1-2007(C/148) and BMW management found as per Rule except liquid BMW as bio-assay parameter was found beyond the limit. 

3. HCU applied for consent under Air Act on 10-1-2007along with the noise monitoring report of DG sets.

 4. No waste water analysis report has been submitted by the HCU.  

5. As per the decision taken in the meeting held on 1-8-2007, a letter had been issued on 27-8-2007 to HCU to submit the fresh water analysis report within 30 days..

6. The copy of the letter was also sent to National Productivity Council to monitor the parameters at the earliest..

7. A reminder letter was sent to HCU to submit the water monitoring report before next meeting to be held on 3-10-2007.Hosp[ital had requested NPC to conduct monitoring of BIO Assay Test. NPC had informed that BIO Assay Testing Facility is not with them.

8. Again a letter was issued on 13.12.07 to submit Bio-assay test report from I.P. University or from I.I.T. Delhi .

9. Reply received but without the desired monitoring report, however the HCU submitted amount of Rs2000/- and stated “kindly arrange for collection of sample for waste water analysis report (Bio-assay test report) from our hospital premises.

10 As decided in the meeting on 15.01.08, letter was issued seeking application for Consent to Establish. However reply was  not received. Consent to Establish application not received. 
As decided on 18.03.08 letter issued .

Inspection conducted on 01.05.2008. Again letter issued on 26.05.08.

11. Reply received on 10.07.08 informed that quotations received for ETP..


	Letter issued.

As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	MS DPCC to issue directions to apply for Consent to Establish and to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	38
	Rajiv Gandhi Cancer Institute &Research Centre, Sector-VI, Rohini, New Delhi-85
	162
	NW-005
	28-Nov-06
	29-Dec-06

26.5.2008(CTE)
	1. The HCU was inspected on 9-5-2006(I/R at  C/135-C/136)  & SCN u/s 5 of EPA was issued on 26-6-2006(C/141) for the deficiencies observed during inspection and reply was submitted on 4-7-2006(C/142) wherein it is mentioned that necessary measures have been taken. 

2. The unit applied for renewal of authorization under BMW Rules on 28.11.06.(Earlier authorization expired on 03.07.06)

3. The Application for Consent to Operate(Renewal) was submitted on 29.12.06 (earlier granted Consent to Operate was valid upto 31.07.05) along with stack monitoring report of DG sets(C/177-C/1178) & for Boiler  wherein the analyzed parameters are within the prescribed standards.

 6. Waste water analysis report has not been submitted by the HCU.

5. SCN for refusal of authorization under Rule 7 of BMW Rules was issued for the deficiencies observed during inspection on 23-8-2007(I/R at page 183/c).
6. SCN issued. HCU replied that BMW training is given to the concerned staff.

7.  A reply on D.O. letter issued on 29.10.07 also received informing various remedial measures taken /being taken on energy efficiency and energy conservation include regular ISO 9000 and ISO 14000 audit are being conducted by the ISO certification authorities. 

8. Letter Issued based on decision taken on 15.01.08. Reply  received , Copy of Noise Monitoring report Dated 20.12.07( of DG Set 1250 KW) &   Common report Dated 15.11.06 ( of DG Sets 1250 KVA, 856.25 KVA & 800 KVA )submitted. 

9. Reply of letter dated 26.05.08 received.

As decided in the meeting on 18.03.08, letter for deficiencies was issued. 

9. Applied for Consent to Establish on 26.05.08

10. Letter dated 26-05-08 was issued

11.Reply dated 12-06-08. w.r.t letter dated 26-05-08.was received regarding doing the needful as directed.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

(f) Applied for CTE on 26.5.2008

EE(BMW)  talked to the official (s)

of the hospital .


	Consent to Establish granted. Call on 14.07.2008 for compliance of letter dated 26.05.2008.
	Consent to Establish issued.
	Reminder  to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008. and also seek permission from CGWA for ground water drawl. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	39.
	Indian Spinal Injuries Centre, Sector-C, Vasant Kunj, New Delhi-110 070
	115
	SW-004
	Applied
	29-Feb-08
	1HCU applied for authorization on 3-3-2004(C/165) 

2. The HCU was inspected on 22-3-2005(C/177) and BMW management found as per rule.  3.Letter was sent on 12-4-2005(C/178) to submit the documents and another reminder was sent on 20-5-2005(C/179) along with stack monitoring report(C/182-C/183) wherein the analyzed parameters found within the prescribed limit and water analysis report(C/180) wherein the analyzed parameters not found within the prescribed standards.

 4. The HCU was inspected on 1-8-2006(C/185-C/186) and following deficiencies were observed: (a). Proper isolated storage site for BMW not provided. (b). Bio-hazard symbol and display board not provided on isolated storage site. 5. SCN for refusal of authorization was issued on 5-12-2006(C/195) and HCU submitted the reply(C/197-C/198) along with the noise monitoring report wherein the insertion loss is not within the prescribed standards.

6HCU had not applied for renewal of authorization date as the time of earlier authorization had been expired on 2-3-2007.

7. Letter has been issued to apply for authorization under BMW Rules.

8. Application for authorization received.

9. Applied for consent to operate on 29.02.08. Noise report, boiler stack report & wastewater analysis report submitted.

Letter issued. Application for Consent to Establish not received.

Applied for consent to operate on 29.02.08. Noise report, boiler stack report & wastewater analysis report submitted.

As decided in the meeting on 18.03.08, letter for deficiencies was issued.

10. Letter dated 26-05-08.was issued

11.reply dated 11-06-08.w.r.t letter dated 02-05-08 regarding authorization under BMW rules and consent under air /water  acts was received .

12.Reply dated 11-06-08.w.r.t letter dated 26-05-08.was received informing about during the needful as directed.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .

Reply received
	EE to chase up. Call on 14.07.2008. 


	EE(BMW)  talked to the official (s)

of the hospital .


	Since ground water use is 19 KLD CGWA clearance is required. Waste water generation is 10 KLD, adequacy report of ETP may be filed. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	40
	Primus Ortho & Spine Hospital ( of Delhi Hospital Society ),  2, Chandergupt Marg, Chankayapuri, New Delhi-21
	100
	ND-024
	10.12.07
	03.10.07( CTE) & 03.12..07 (CTO ) 
	Applied for consent to establish on 03.10.07 for 100 bedded Hospital replacing existing 70 bedded Hospitals. Project report submitted and informed regarding one no. of 500 KVA DG Set with acoustic enclosure and with adequate stack height. For discharge of Kitchen waste water, Greece strap is proposed and mentioned that BMW shall be disposed through authorized agencies and measures shall be taken for BMW Management. Adequate effluent treatment plant, if required shall be provided to meet the prescribed standards. Date of commissioning is 20.10.07.  Trade effluent discharge as per affidavit submitted will be 10 KLD and domestic effluent discharge 49 KLD. As per application industrial / trade effluent is 16.5 KLD. Letter issued, Applied for Consent to Operate.& Authorization under BMW Rules however  specific reply not received w.r.t the letter issued & regarding ETP . It is mentioned in the affidavit submitted along with the Consent application that ETP (if, required) shall be provided to meet the prescribed standards. As per the Consent application operation of the unit started from 20th October 2007 and Hospital is also having a Boiler however Monitoring report for Boiler not submitted. Subsequently vide letter 14.01.08 the unit has informed that the unit is assessing the exact quantity of effluent and in process of getting the sample testing and also informed that ETP if required shall be installed after getting the report and a fresh affidavit for authorization under BMW Rules submitted. The affidavit submitted along with the application for consent to operate is not proper.  

As per BMW Committee meeting held on 18.03.08, the hospital has been inspected on 28.03.08 .During the inspection following deficiencies were  observed :

(i) Bio-Hazard symbols not provided on the containers

(ii) Isolated storage site not provided for the storage of Bio-Medical waste.

(iii)Nurses and other staff need proper training which is lacking at present.

(iv)Proper record keeping of the Bio- Medical waste not observed.

(v)Stack height with 25 KVA DG set with inbuilt acoustic enclosure  found inadequate.

(vi)Effluent Treatment Plant (ETP) for the waste water generated from the    Hospital not provided. As decided in the meeting on 18.03.08, letter for deficiencies was issued.

7. Letter dated 26-05-08 was issued

8.Reply dated 11-06-08.w.r.t letter dated 26-05-08.asking for time to install ETP till 31-03-09. was received.


	Letter issued. Reply received and has requested to grant time till 31.3.2009 for installation of ETP.

As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d) ETP (e) Plantation of trees along side of the periphery of the Hospital building.


	Consent to Establish granted. Time allowed for installation of ETP till 31.03.2009. However, compliance of letter dated 26.05.2008 to be submitted. Call on 14.07.2008.


	Consent to Establish issued. 

Letter issued.
	Reminder seeking compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	41.
	Batra Hospital & Medical Research Centre, 1, Tughlakabad Institutional Area,Mehrauli  Badarpur Road, Delhi
	495
	s-005


	26-Jul-06
	Not Applied
	1. The HCU was inspected on 26-7-2006(C/290) and BMW management found as per rule.                                                                                                                      2. The letter was issued on 27-11-2006(C/291) to submit the following: (a). Condo nation fee of     Rs.50100. (b). Application for consent under Air Act. (c) To increase the stack height of DG     sets. (d). Waste Water analysis report.                                                                                             3. The HCU submitted the reply(C/296) wherein it is mentioned necessary fee towards noise monitoring(C/294), stack monitoring of boiler(C/293) and effluent analysis report(C/292) has     been deposited in DPCC on 10-1-2007deposited and reports are awaited.                                                                                                                                    4. A letter has been issued to the hospital authorities to install the Effluent Treatment Plant within three months.5. Letter issued referring earlier references. 

6. Not applied for consent.

7. As decided in the meeting held on 1-8-2007, a copy of the letter was to be sent to Sh. Ashok Pradhan, Administrator of the Hospital.

8. Letter issued. Earlier HCU has submitted the reply that ETP has been installed and now it is functional.

9. HCU has also submitted the waste water test report for ETP.Letter issued. Reply received informed that all reports are submitted. Application for Consent to Establish not received.As decided in the meeting on 18.03.08, letter for deficiencies was issued.

10. Letter dated 26-05-08.was issued

11.No reply received.
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital .


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	MS DPCC to issue directions to MS of the Hospital  for applying for Consent to Establish. Call on 27.08.2008.

	42
	Holy Family hospital, Okhla Road,
	298
	S-006
	13.04.07
	19.01.07
	1. The authorization was valid up to 8-4-7and apply for renewal on 13-4-2007.                                                                                                             2. The HCU was inspected on 10-11-2006 and BMW management found as per rule and acoustic enclosure has been provided with the D.G. sets.                                                       3. The HCU did not submit the noise monitoring report.

As decided in the meeting on 18.03.08, letter for deficiencies was issued.

4.Reply dated 10-06-08.w.r.t. letter dated 26-05-08.received informing about doing the needful as directed .



	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

EE(BMW)  talked to the official (s)

of the hospital . Reply received


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	MS DPCC to issue directions to MS of the hospital for applying for Consent to Establish  and for  compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	43
	Sir Ganga Ram Hospital, Rajender Nagar, New Delhi - 110 008
	500
	C-005
	07.07.06
	13.11.06
	. The HCU was inspected on 2-8-2006 (C/201-202) and BMW management found as per rule.     However some deficiencies were observed in ETP.                                                                                                         2. SCN u/s 5 of EPA was issued on 6-10-2006 (C/208) with the remarks (a).Although the ETP     was in operation, but sludge bulking in the lamina clarifier was observed, which indicated that ETP is not working satisfactory. (b). The condition of Filter Press indicated that the same was not being used, which show that the de-sludging process is not being undertaken.                                                                                                                                                    3. HCU submitted the reply wherein it was mentioned that ETP was working satisfactorily (C/209) and also submitted the water monitoring report(C/236) wherein the analyzed     parameters found within the prescribed limit.    

4. HCU also submitted the Stack Monitoring report of boiler (C/235), Stack Monitoring report of D.G. set(C/266 -C/ 271), and Noise Monitoring report of D.G. sets (C/225-C/228) wherein the analyzed parameters found with the prescribed limit.5. Authorization under BMW Rules and Consent to operate is valid up to 30-5-2010.  

6.Reply dated 04-06-08 w.r.t letter dated 26-05-8.informing about doing the needful as directed.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.

Reply received.


	Ask the unit to apply for Consent to Establish.

Also EE to chase up. Call on 14.07.2008.
	Letter issued.
	MS DPCC to write to MS of the Hospital to apply for Consent to Establish and to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	44
	I.P Medical Corp. Ltd.Sarita  Vihar , Mathura Road , New Delhi-44


	661
	S-003


	05.06.06
	19.02.07

11.06.2008(CTE)
	1. The authorization was valid till 30-7-2006(C/149).

2. The HCU was inspected on 10-11-2006(C/182) and BMW management found as per rule.

3. The Effluent Treatment Plant is yet to be installed.

4. The HCU submitted the water analysis report from Shri Ram Laboratories(C/185) which is not the approved laboratory and also the analysed parameters i.e. BOD is not within the prescribed standards.

5. The HCU submitted the reply on 17-11-2006(C/186-C/187) wherein it mentioned where they requested for advice for installation of ETP.

6.The HCU has also submitted the stack monitoring report(C/191) and the noise monitoring report of DG Sets(C/192-C/194) wherein the analyzed parameters and insertion loss found within the prescribed standards.

7. Reply has been received with the remarks that the work has been finalized(C/213).

8. Letter issued. Reply submitted and the likely date of completion of ETP mentioned is 31.03.08 along with details of ETP. 9.Another letter received informing that more time is required for completion of ETP.

10.As decided in the meeting on 18.03.08, letter for deficiencies was issued. Letter also issued  after the decision on06.05.08. Reply received.

11.Inspected by a team alongwith Dr. T.K.Joshi , on 11.07.08. During inspection BMW management found satisfactory however improvement required w.r.t providing proper containers at the storage site. ETP found under construction & it was informed that it will be completed in a months time.
	Letter issued. Reply received w.r.t. letter dated 02.05.2008. CTE applied.

As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.. Reply received


	Inspect.
	Inspected  on 11.07.08
	Inform the deficiencies   to the unit. Case of CTE application will be decided once ETP is installed. Call on 27.08.2008.

	45
	Fortis  Lt. Rajan Dhall Charitable Trust, Secto-B, Aruna Asaf Ali arg, Vasant Kunj


	158
	SW-149
	1-May-06
	1-Sep-06
	1. HCU applied for authorization on 1-5-2006(C17).

2. HCU was inspected on 22-8-2006(C18) and BMW management found as per rule.

3. HCU applied under Air Act n 1-9-2006.

4. Waste Water monitoring report submitted.

5. As per the decision taken in the meeting held on 1-8-2007, consent under Air Act and authorization under BMW rule has been issued

6. .Letter dated 26-05-08 was issued .

7.NO reply.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.


	Ask the unit to apply for Consent to Establish.

Also EE to chase up. Call on 14.07.2008.
	Letter issued.
	MS DPCC to direct MS  of the hospital  to apply for Consent to Establish and to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	46
	Moolchand Hospital, Lajpat Nagar-III , New Delhi-24
	150
	S-008
	7/Jun/05
	23-Jun/04
	1. HCU was inspected on 15-9-2005(C/147) and BMW management found as per rule. 2. HCU apply for consent under air act on 23-6-2004(C/32).                                                       3. Acoustic enclosure not provided with the DG sets.

4. As per decision taken in the meeting held on 1-8-07, HCU has been inspected on 14-8-2007(C/194) and BMW Management found as per rule.5. As per decision taken on 31.08.07, Consent under Air Act and Authorization under BMW Rules issued.
6.No reply received.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.


	Ask the unit to apply for Consent to Establish.

Also EE to chase up. Call on 14.07.2008.
	Letter issued.
	MS DPCC to direct MS  of the hospital  to apply for Consent to Establish and to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	47
	Rockland  Hospital,B-33-34, Qutab institutional Area, New Delhi-16


	130
	S-276
	28-Mar-06
	27-Dec-06


	1.The application for authorization was completed on 28-3-2006 by submitting the balance fee and provisional authorization was valid upto 12-4-2005(C/9) .                                                                                                   2. The HCU was inspected on 22-9-2006(C/30) and BMW management found as per rule and acoustic enclosure has been provided with the D.G. sets.   

3. As per the decision taken in the meeting held on 1-8-2007, consent under Air Act and authorization under BMW rule has been issued

4.. Letter dated 26-05-08 was issued

5.NO reply received.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.


	Ask the unit to apply for Consent to Establish.

Also EE to chase up. Call on 14.07.2008.
	Letter issued.
	MS DPCC to direct MS  of the hospital  to apply for Consent to Establish and to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 



	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	48
	Sant Parmanand Hospital, 18, Civil Lines, Sham Nath MargDelhi-6


	120
	N-004
	18-Apr-07
	14-Jun-06
	1. HCU was inspected on 15-11-2006(C/104) and BMW management found as per rule.

2. HCU applied for consent under on 14-6-2004 along with the noise monitoring report of DG set.

3. .Waste water analysis report has been submitted.

4. As per the decision taken in the meeting held on 1-8-2007, consent under Air Act and authorization under BMW rule has been issued

5. Letter dated 26-05-08 was issued

6.Letter received on 14.07.08 requesting for CTE application.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.


	Ask the unit to apply for Consent to Establish.

Also EE to chase up. Call on 14.07.2008.
	Letter issued.
	MS DPCC to direct MS  of the hospital  to apply for Consent to Establish and to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	49
	Mata Chanan Devi Hospital, C-1, Janak Puri,New Delhi 


	210
	W-004
	28.04.06

( Auth Valid upto 04.05.09)
	28.04.06
	1.HCU submitted the noise monitoring report(  Dated 23.05.06)(C/313) wherein the  insertion loss is within the prescribed standards.                                                                            

2. Consent issued under Air Act as per the decision taken on 04.10.07.

3. Letter dated 26-05-08 was issued

4.letter received on 14.07.08 w.r.t letter dated 26.05.08,   informing that needful is being done. 


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.


	Ask the unit to apply for Consent to Establish.

Also EE to chase up. Call on 14.07.2008.
	Letter issued.
	MS DPCC to direct MS  of the hospital  to apply for Consent to Establish and to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	50
	Sri Balaji Action Medical Institute , FC-34, A-4, Paschim Vihar, New Delhi- 63


	200
	W-327
	21.06.07


	22.06.07
	1.HCU applied for renewal of authorization on 21-06-07(C/115). Previous authorization expired on 08-07-07(C/88).                      

2. Applied for renewal of consent on 22-06-07(C/32). Previous consent was expired on 08-07-07(C/42).               

3. Noise monitoring report submitted on 29-3-2006(C/79) wherein the insertion loss found within the prescribed standards.

4. Consent issued under Air Act. &Authorization issued under BMW Rules, as per the decision taken on 04.10.07.

5. Letter dated 26-05-08 was issued

6. Letter received on 14.07.08 w.r.t letter dated 26.05.08, informing that needful is being done. 


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building. 


	Ask the unit to apply for Consent to Establish.

Also EE to chase up. Call on 14.07.2008.
	Letter issued.
	MS DPCC to direct MS  of the hospital  to apply for Consent to Establish and to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	51
	Jeewan Mala Hospital(P)Ltd., 67/1, New Rohtak Road.New Delhi -05


	104
	C-012
	04.07.06
	08.01.07
	. The HCU was inspected on 27-9-2006(C/80)  and BMW management found as per rule.  The HCU was again inspected on 09.07.2007 since complaints were received against the Hospital and BMW management was found  as per rule ( (  C/134).                                                                                                                      2. Acoustic enclosure and adequate stack height with the D.G. set of 75 KVA has been provided.                           

3. Noise Monitoring Report (dated19.10.06) was submitted along with the Consent application. Insertion loss meeting the norms.

4. Consent issued under Air Act. & Authorization issued under BMW Rules as per the decision taken on 04.10.07.

5. Letter dated 26-05-08 was issued

6.No reply received.


	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.


	Ask the unit to apply for Consent to Establish.

Also EE to chase up. Call on 14.07.2008.
	Letter issued.
	MS DPCC to direct MS  of the hospital  to apply for Consent to Establish and to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	52
	G.M.Modi Hospital and Research Centre for Medical Science, Mandir Marg, Saket , New Delhi -17
	100
	S-010
	29.06.07
	13.08.07



	1. Authorization expired on 28-2-2007(C/134-C/135). 

2. HCU has applied for consent to operate under Air Act and authorization under BMW Rules along with noise monitoring report. Insertion Loss within the limit.

3. Consent issued under Air Act. &Authorization issued under BMW Rules as per the decision taken on 04.10.07.

4.Letter dated 26-05-08 was issued .

5.Reply w.r.t letter dated 26.05.08  received.
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.
	Ask the unit to apply for Consent to Establish.

Also EE to chase up. Call on 14.07.2008.
	Letter issued.
	MS DPCC to direct MS  of the hospital  to apply for Consent to Establish and to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	53
	Jeewan Mala Hospital Pvt. Ltd., 66- A/2, New Rohtak Road, New Delhi-05
	50
	C-091
	03.07.06
	08.01.07
	1. HCU was inspected on 27-9-2006(C/39) and BMW management found as per rule.

2. HCU submitted the application for consent under Air act on 8-1-2007(C/53) along with noise monitoring report (C48).

3. Consent under Air Act and Authorization under BMW Rules issued on 25.09.07.

4.No reply received .
	------------
	Ask the unit to apply for Consent to Establish Also EE to chase up. Call on 14.07.08
	Letter issued .
	MS DPCC to direct MS  of the hospital  to apply for Consent to Establish and to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	54
	Jeewan Nursing Home & Hospital, 2-B, Pusa Road, New Delhi-05 
	100
	C-016
	11.07.07
	O7.07.06
	1. Previous Authorization under BMW Rules expired on 28.07.07. Consent under Air Act granted for three years from the date of submission of the application dated 07.07.06. but HCU has not submitted noise monitoring report of the DG sets in compliance of consent condition no. 4.

2. Letter Issued Reply Received however not applied for Consent to Establish. & not submitted the noise monitoring report for the DG sets.

3.  Letter for deficiencies issued on 21.04.08. Reply waited.

4. Inspected on 29.04.08. During the inspection the management of the BMW     was found as per rule w.r.t. segregation, color coded bags being used as     per rule. (i)  Isolated storage site has been provided & the waste being stored in the separate containers for insuperable & Autoclavable waste at the storage site.(ii) Having two DG sets of capacity 62.5KVA & 82.5KVA with acoustic       enclosure and the stack (combined) found of adequate height.

 (iii) Health care workers were found aware of regarding the management of        BMW 

5.Letter dated 26-05-08 was issued 

6.Reply dated 12-06-08,was received along with noise monitoring report waste water analysis .


	Letter issued. 

As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.


	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	MS DPCC to direct MS  of the hospital  to apply for Consent to Establish and to seek compliance  with directions issued vide letter dated 26.05.08 w.r.t decisions taken on 06.05.2008.Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	55
	Dr. B.L.Kapur Memorial Hospital , 5, Pusa Road, Delhi  08
	500
	C-
	………


	13.03.08(Establish)
	1. This is a 500 bedded Hospital for which Consent to Establish application has been received on 13.03.08 . Date of Commencement Mentioned is April 2008. Plot Area is 20240 SQ Meter , Built up Area is 101247 Sq meter. Total  Water Consumption  -  574 KLD( 292  KLD Domestic,  125 Boiler etc. ,  13 KLD Gardening ). In the project report water use is also mentioned for  Dialysis purpose i.e. 144 KLD.  Effluent – 263 KLD(Domestic) &  10 KLD ( Cooling& Boiler Blow Down and Softening Plant ) .  STP proposed for the treatment of 300 KLD  Waste Water ( with  Screen /Grit Chamber, Equalization Tank, Aeration Tank( diffused aeration) Clarifier ( Lime / Ferrous Sulphate coagulant ) followed by chlorination( hypochlorite soln).For sludge handling aerobic digester cum thickner & centrifuse or filter press will be provided and solidified sludge cakes shall be used as manure in horticulture. Activated carbon filter will be proded for the filtration and water will be used for cooling towers of AC and DG system and for horticulture within the site. 122 KLD  is proposed to be discharged & 138 KLD is proposed to be reused/ re-cycled after treatment.   Boilers shall also be provided ( 4 Nos)    .DG Sets -  1610 KVA ( 2 No)) & 500 KVA ( 1 No.)  I DG Set  capacities given in the affidavit are not  matching with the capacities given in the application. No trade effluent  generation and discharge is mentioned in the affidavit whereas in the application effluent generation & discharge is mentioned.  It is mentioned that adequate STP will be provided to meet the prescribed standards. There are discrepancies in the figure of water reuse given in the Project report & Consent application. For DG Sets it is mentioned that  integral  acoustic enclosure will be provided and shall meet the prescribed  norms.   Regarding BMW  & MSW  these  will be managed as per BMW Rules & MSW Rules. Rain water Harvesting shall also be done by taking suitable measures.  For this project Environmental Clearance is also required from MOEF since built up area proposed is 101247 sq meter which is more that 20000 sq meter .However information not given in this regard.  

2.  As decided in the meeting on 18.03.08, letter for deficiencies was issued on 21.04.08.

3.Reply dated 06-06-08. w r t.letter dated 21-04-08.received informing about doing the needful as directed .

4.Letter dated 13-06-08 .regarding redevelopment of the hospital received.
5. Environmental Clearance given by MOEF  vide letter dated 13.06.08.

6. Inspected by a team along with Dr.T.K.Joshi , on  11.07.08. Construction of the Hospital was going on & it was informed that the work is expected to be completed in October 2008. 


	EE(BMW)  talked to the official (s)

of the hospital .


	Inspect.
	Inspected on 11.07.08.
	Deficiencies be informed to the unit. Since the waste water is 263 KLD, unit may be directed to install ETP expeditiously and also issue letter  based on the decisions taken in the meeting on  06.05.2008.& 13.06.08.

 

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	56. 


	Yashraj Bio-Technology Ltd., C-34.Mulund (West), Mumbai-80
	NA
	
	19-10-06
	Not Applicable
	1. Letter to Maharastra Pollution Control Board by MS, DPCC, requesting to inform about the status of authorization under BMW Rules.

2. For inspection G.B. Pant Hospital was visited on23-3-207 and the bottles in which the BMW fluid being carried out were seen which are having Biohazard symbol and level however Inspection of the vehicle and arrangement used for the transportation of bio-fluid could not be verified as the no one was came to carry the fluid from the transporter during the inspection.

3. Reply has been received from Maharastra State Pollution Control Board along with Valid Consent to Operate and authorization under BMW Rules.

4. A letter was issued to call the representative of the company the presentation before the committee in the next meeting.

As decided in the meeting held on 1-8-2007, representative of the company was asked to submit the required documents to this office and the same has been submitted to this office.

. A letter was issued to send the photographs about the handling of BMW fluids during the transportation. Letter has been issued.

Representation has been received referring earlier submitted photographs and presentation made before the committee on 1-8-2007

Letter issued referring to our earlier letter and seeking the required photograph.

Letter issued.  Reply received along with photographs of handling of BMW.

Reply received stated that they have placed the order for the directed masks and also stated measures taken to ensure for no pilferage during the transportation.

Another copy of the reply addressed to Hon’ble Chairperson received. 

Letter issued. Reply received submitted photograph of person using the desired mask, during collection of BMW & the same mask would be used during collection in Delhi. Copy of Purchase Order/ Work Order /Tax Invoice also enclosed. 

Authorization as per decision taken in the BMW meeting held on 06.05.08 has been issued.  


	Authorization  issued. File sent to Account section for the return of the remaining fee for two years.
	No action.
	---------------------
	No action. 

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.


	57. 

 
	Metro Bio-Care services (P) Limited,
	NA
	
	Having valid Authorization
	Having valid Consent
	1. To de1.The inspection has been conducted by Dr. T.K. Joshi along with DPCC officers.

2.The inspection team has pointed out some deficiencies and as per decision a letter was issued on 25-5-2007 to the operator to rectify the deficiencies within three months.

3. The operator submitted the reply wherein it is mentioned that they have rectified the deficiencies.

4. As the operator has installed new incinerator as per direction of CPCB, the facility is to be inspected by Dr. T.K. Joshi, along with officials of DPCC.

5. The operator of the facility has submitted the reply after taking all the measures regarding the common bio-medical waste treatment facility.

6. As per directions issued by CPCB u/s 5 of EPA on 03.10.07, CPCB has asked for extension of earlier submitted Bank Guarantee by the operator of the facility till 31.03.08 and directed to initiate necessary actions to ensure (a) Efficient working of droplet Separators for control of moisture in flue gas (b) Emission parameters are always met with standards prescribed in the BMW Rules.

7. As decided in the meeting held on 1-8-2007, the HCU was inspected on 23-8-2007 and the inspection report in detailed is placed(C/519) in the file.

8. SCN under rule 7 of BMW Rules was issued for : Sludge dewatering device be provided with ETP.2. Manual mode on PLC should not be used. 3. Rota meter should be provided at PC &SC of incinerator.

9. Reply Received along with an affidavit stating that Filter Press has been provided; PLC is being used on auto mode and will not be used on manual mode & Rota meter has been installed with the Primary & Secondary Chamber of the Incinerator.

10. Reply received, operator has informed regarding compliance with the  directions given by CPCB.

11. A Copy of  letter of CPCB  dated 25.02.08 has been received seeking undertaking in form of Affidavit with following declarations by 10.03.08 ;

 (i) The currently installed locally fabricated shredder in the facility shall be replaced with a new effective shredder as per CPCB Guidelines by 30.04.08.

(ii) The location and Specification of Port Hole, platform & Ladder etc. shall be as per Emission Regulations, Part -3, (COINDS / 20/ 1984-85), published by CPCB.

12. Operator submitted the affidavit sought by CPCB.

13. As decided by the committee an Inspected was carried out on 27.03.08 and PLC has been provided for the operation of incinerator on auto mode feeding system and the same was found operational. The temp. in the primary & secondary chamber has been checked & were found in the prescribed range.  

- Incinerator with wet scrubbing system was found in working condition & was in operation.

- Roto meter found installed in primary and secondary chamber.

- For improving the working of droplet separator for control of moisture in flue gas, addition duct space provided.

- Filter press has been installed for the sludge dewatering.

- Port hole, platform & ladder improvement measures have been taken.

- The operator is having one shredder of (25 Kg/hr), affidavit have been submitted by operator to CPCB, for new shredder installation as per CPCB guidelines by 30.04.08.   

14. The unit has informed regarding issuing the identity card to collection staff & proper dress has been provided to collection staff. New weighing machines have been provided to ensure proper weighing of BMW. 

15.  CPCB has released the bank guarantee submitted by the unit.  


	----------
	No action.
	------------------------
	No action. 

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.


	59. 
	Panacea Biotec  Ltd. , A-224,   PH – I ,  Okhla Industrial Area, Delhi -20.
	R& D activities for Vaccines
	S -291
	13.11..07
	22.02.06
	1. This is a case of  unit engaged in  research & development of Vaccines and operating since  Nov. 2004.  The unit applied for Consent to operate under Air& Water Act, on 22.02.06.  2. The unit was inspected by the officials of PGRC  on 27.04.07. & the matter was placed before CMC (Orange)in its meeting  held on  09.10.07. 3.The unit is having a DG Set of 380 KVA with acoustic enclosure and also have a oil fired Boiler for which information was not provided in the consent application.  The unit had concealed information and not provided adequate stack height., it was decided that the unit shall apply for Consent to Establish and submit a Bank Guarantee of Rs. 50,000 . The unit has applied for Consent to Establish under the Air & Water Acts, on 27.11.07 and also submitted Bank Guarantee of Rs. 50,000. valid upto 21.11.08.  4. The unit submitted test report for the waste water generated from the unit showing that the  parameters are within the prescribed limit. 5.Stack monitoring report for the Oil fired Boiler not submitted.

6. The unit applied for the Authorization under the BMW Rules on 13.11.07 and informed that unit is engaged in formulation and the products manufactured are  tablets , capsules, liquid orals and gel and also informed that BMW generated is disposed through M/s Synergy Waste Management Pvt. Ltd.

 7. The team of PGRC Officials & Dr. T.K.Joshi could not inspect the unit on 06.11.07 as  Board meeting of the said unit was going on. 

8.  As per the Hazardous Waste ( M& H) Rules ,1989, as amended to date, the activities/ processes of the unit are covered under the said Rules.

As decided by the BMW Committee ,Notices were  issued to 7 units based on the information given by M/s Synergy Waste Management Pvt. Ltd. (out of 7 units 6 have been inspected and information/status given separately). Regarding this Unit  Panacea Bio-tec. Ltd. ,, inspection was done on 31.03.08 & following are the main observations :

(i) The main working area could not be inspected due to non vaccination of the visiting Officers. Information gathered from the persons available at the site. This unit is engaged in the R& D activities for vaccines. 

(ii) Blenders and SS containers are used in the activities of the unit and waste water is generated from the washing of Blenders/ Vessels for which ETP has not been provided. No equalization tank provided for the homogeneous mixing of the effluent for the proper characterization of the waste water. 

(iii) A small common storage facility is there  at premises no  A -242 , OIA PH I  for both the premises (  A – 224, OIA PH I & A -242, OIA PH I ) of the Panacea Bio Tech Ltd. The said common storage site is lacking with requirements of BMW Rules( Colour Coding , Sharp Waste Management , Containers , record keeping etc.)

(iv)The Unit is having DG Set of 380 KVA with Acoustic Enclosure & a oil fired boiler.

Fresh waste water analysis report after the equalization of the waste water & proper segregation of the BMW  was advised during the inspection.

V. Reply dated 03-06-08.w.r.t letter dated.26-05-08.regarding installation of ETP was  received. 
	Letter issued. Reply received.
	Ask the unit to submit affidavit for correction of deficiencies observed during the inspection and installation of ETP.
	Letter issued.
	Ask the unit to indicate how 1.4 KLD waste water is being treated and whether ETP is installed. Call on 27.08.2008.



	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	60. 
	Panacea Biotec  Ltd. , A- 239-242,   PH – I ,  Okhla Industrial Area, Delhi -20.
	Mfg of Vaccines
	S -292
	13.11..07
	20.01.06

( Renewal) 
	1. This is a case of  manufacturing of  Vaccines and operating since  1989.   Earlier granted Consent was valid  upto 19.02.06 .The unit applied for Consent to operate (renewal) under Air& Water Act, on 20.01.06.  The unit has submitted two set of application form for consent (renewal)  dated 12.07.06&  20.01.06 and contradictory statements were made in the applications. 2. The unit was inspected by the officials of PGRC  on  25.09.07. & the matter was placed before CMC (Orange)in its meeting  held on  09.10.07. & following decision was taken”  The unit has been submitting consent applications with confusing address on three locations. The unit has not applied foir Consent to Establish and only applied for Consent to Operate. Let him file an application alongwith an affidavit of correct address. Since the unit is involved in mfg of Vaccines for which inspection would require the services of specialist, PGRC team may take Dr. T. KJoshi, specialist of  BMW  Committee for this purpose and report on 14.11.07.”

3. The team inspected the unit on 06.11.07 & it was observed that the unit generates BMW for which unit had not applied for authorization under BMW Rules though having agreement with M/S Synergy Waste Management Pvt. Ltd. ,  for the disposal of the BMW. .The unit is having two  DG Set of 500 KVA  each with acoustic enclosure and also have  oil fired Boiler (as per report submitted.)  

4. Later on the unit has applied for Consent to Establish under the Air & Water Acts, on 27.11.07   5.Stack monitoring report for the Oil fired Boiler,  submitted showing parameters within the prescribed limit. . Trade Effluent is  generated from the unit  & as per the earlier report submitted , parameters are within the prescribed limit. 

6. The unit applied for the Authorization under the BMW Rules on 13.11.07 and informed that unit is engaged in formulation and the products manufactured are  tablets , capsules, liquid orals and gel and also informed that BMW generated is disposed through M/s Synergy Waste Management Pvt. Ltd. 

7.  As per the Hazardous Waste ( M& H) Rules ,1989, as amended to date, the activities/ processes of the unit are covered under the said Rules. 

8. Files obtained from PGRC.  

9. Applied for the authorization.

As decided by the BMW Committee ,Notices were  issued to 7 units based on the information given by M/s Synergy Waste Management Pvt. Ltd. (out of 7 units 6 have been inspected and information/status given separately). Regarding this Unit  Panacea Bio-tec. Ltd. ,, inspection was done on 31.03.08 & following are the main points / observations :

(i) The main working hall could not be inspected as vaccination is required ,the required information was gathered from the persons present during the inspection

(ii) This is the vaccines mfg unit & in the process/ activities, blenders / mixers are used for mixing of raw materials / chemicals / solutions etc for making vaccines mainly Polio vaccines. Waste water is generated from the washing of the blenders & SS containers for which ETP not provided. No Equalization tank provided which is required to know the characteristics of representative sample.

(iii) Regarding BMW , both solid and liquid waste was reportedly given to M/s Synergy Waste Management Pvt. Ltd however M/ s  Synergy has denied for liquid waste collection. Proper Isolated storage site not provided for BMW.

(iv) Sharp management not found as per rule.

(v) Color coding of BMW bags was not found as per Rule.

(vi) BMW record keeping  not proper. 

 (vii) The unit is having DG Sets ( 2 No 500 KVA each) with Acoustic Enclosure & also have 2 oil fired boilers.

Fresh waste water analysis report after the equalization of the waste water & proper segregation of the BMW  was advised during the inspection.

VIII.Reply dated 10-06-08.w.r.t  letter dated 26-05-08.regarding asking for 3month time  for   installation of ETP was received. 

Another letter received on 14.07.08 regarding request for outsourcing of liquid waste for the treatment.

  
	Letter issued. Reply received w.r.t. letter dated 26.5.2008.
	Ask the unit to submit affidavit for correction of deficiencies observed during the inspection and installation of ETP.
	Letter issued.
	Since waste water generation is 4.5 KLD out of total water consumption of 13.5 KLD, unit may be directed to install ETP and file affidavit for correction of deficiencies. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	61 
	Panacea Biotec  Ltd. , B- 1/ E-12, Mohan Co-operative Industrial Estate, Delhi -44..
	----
	S - 293
	13.11..07
	28.10.05(Renewal) 
	1. This is a case of  unit engaged in   MFG OF Tablets , Liquid orals, Ointment / Gel  ( mfg. of pharmaceuticals)  and operating since  1989.  The unit applied for Consent to operate under Air& Water Act, on 28.10.05(Renewal).  Previous Consent was valid upto 20.11.05.  2. The unit was inspected by the officials of PGRC  on 25.09.07. & the matter was placed before CMC (Orange)in its meeting  held on  09.10.07. and it was decided that  Prof  .T.K. Joshi,  will  inspect the unit and report on 14.11.07. 3.The unit is having two  DG Set of 380 KVA & 725 KVA with acoustic enclosure and LPG Bhatti.  4.The unit submitted test report for the waste water generated from the unit showing  that the  parameters are within the prescribed limit. . Later on the unit applied for Consent to Establish under the Air & Water Acts, on 27.11.07

5.  Inspection done on 06.11.07 & it was found that unit generates BMW However had not applied for the authorization under BMW Rules, through disposing BMW  through M/s Synergy Waste Management Pvt. Ltd.  Isolated storage site for BMW not provided.   6. The unit applied for the Authorization under the BMW Rules on 13.11.07 and informed that unit is engaged in mfg of  tablets , capsules, liquid orals and gel and also informed that BMW generated is disposed through M/s Synergy Waste Management Pvt. Ltd. 

7. As per the Hazardous Waste ( M& H) Rules ,1989, as amended to date,     the activities/ processes of the unit are covered under the said Rules.

 8. Applied for the authorization.   As decided by the BMW Committee ,Notices were  issued to 7 units based on the information given by M/s Synergy Waste Management Pvt. Ltd. (out of 7 units 6 have been inspected and information/status given separately).  Regarding this Unit  Panacea Biotec  Ltd. The unit was inspected by the team on 03.03.08. Waste Water / Liquid waste is generated for which no ETP / Equalization tank provided .Other Unit M/s Panacea Bio – Pharmaceuticals Research at First Floor a R & D Laboratory is also operating which has not applied for authorization under BMW Rules. Liquid BMW from this Laboratory is given to M/S Synergy Waste Management Pvt. Ltd .however the said Operator has informed contrary to this. 
As decided in the meeting on 18.03.08, letter for deficiencies was issued. Reply dated 03-06-08 regarding installation of ETP was received.


	Reply received.  
	Ask the unit to submit affidavit for correction of deficiencies observed during the inspection and installation of ETP.
	Letter issued.
	Since ground water  use  is 6 KLD, CGWA clearance is required. Since waste water generation is 4 KLD, unit may be directed to install ETP and submit affidavit for correction of deficiencies. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	62 
	Shriram Institute for Industial Research , 19, University Road, Delhi -07.
	----
	N- 069
	28- Feb- 07
	Not Applied.
	This is a case of research institute which is engaged in research related with animals and generates BMW .2. Earlier the Institute was having incinerator for the disposal of BMW. Presently the unit ,as per the information provided alongwith the application , is disposing its BMW through M/s Metro Bio Care.

3. The Institute had applied for the authorization under the BMW Rules, on 29.06.2001 & again on 28.02.07  which was placed before the BMW Committteee No. 3, in its meeting held on  18.10.07, and  it was decided by the said Committee  that being a case of research institute, put up on file for deciding which BMW Committee should deal this case . The matter was put in file  and as decided by MS, DPCC, this case has been  included in the cases to be dealt by BMW Committee No.1.  

4. Letter Issued Reply  Received  however not applied for Consent to Establish.

To be Inspected.

5. Inspected on 29.04.08. During the inspection following deficiencies observed:

i). In the histopathology lab the management of the BMW  not as per rules w.r.t. colour coded bags,  Bio-Hazard symbol not provided/ not displayed on the  storage freezer/ room

ii) Having three nos. of DG sets of capacity 1x 320 KVA installed in the acoustic enclosure with adequate stack. 1x250 KVA DG set was found without acoustic enclosure & reportedly not in use & third DG set is of 75 KVA also found without acoustic enclosure & reportedly not in use.  

Letter issued based on the decision taken on 06.05.08. Reply received asking time for filing application for Consent to Operate/ Establish.

8.Reply dated 06-06-08.w.r. t.  letter dated 26-05-08.regarding taking necessary steps to meet BMW guidelines was received.


	Letter issued. Reply received. Asked time for filing application for consent to operate/Establish.  
	EE to chase up. Call on 14.07.2008.
	EE(BMW)  talked to the official (s)

of the hospital .


	MS DPCC to direct MS of the  Institute to file Consent to  Establish application . Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	63
	Neeman Medical International ( Asia) Ltd. , Max House, Ground Floor, 1, Dr. Jha Marg, Okhla, Delhi -20
	Storage &  Distribution of Clinical trial material.
	S-301
	16.04.08
	------
	Show Cause Notice as decided in the Meeting on 15.01.08 was issued to the Unit on 22.02.08.  Applied for authorization under BMW Rules ON 16.04.08

Inspection was done on 30.04.08 & following are the main observations :

(i) Separate Storage room provided for the storage of discarded medicines / drugs however discarded medicines /drugs also found stored outside the room and without proper labeling of Bio – Hazard Symbol

(ii) Log Book for the expired / discarded medicines could not be shown 

(iii) About 65 Containers ( Card Board Boxes) of 20 – 30 kg each of discarded medicines found in the storage room.

(iv) The unit has agreement with M/s Synergy Waste Management Pvt. Ltd for the disposal of discarded medicines / drugs.

V.Reply dated 05-06-08.w.r.t letter dated 26-05-08.regarding rectification of deficiencies .(Proper Bio hazard symbol display ,storage room for discarded medicines ,log book maintenance .)was received.


	Letter issued. Reply received.
	Ask the unit to submit affidavit for correction of deficiencies observed during the inspection. Call on 14.07.2008.
	Letter issued.
	Issue reminder seeking affidavit  for correction of deficiencies. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	64


	Ranbaxy Laboratories Ltd., J- 3/B-1 Extension. Mohan Co-oprative Industrial Estate, Badarpur, Delhi -44.

	Closed
	….
	…….
	……..
	Show Cause Notice as decided in the Meeting on 15.01.08 was issued to the Unit on 22.02.08. Premises was inspected on 03.03.08 and unit not found  existing . Unit Closed & Shifted.    


	-------------
	No action.


	--------------------
	No action. 

	65.
	LG Life Sciences India Pvt. Ltd., LG House, AB-3, Safderjung Enclave,Delhi-29
	Drug Stockist & Marketing/ Importer
	SW-163
	12.03.08 
	 Not Applied
	Show Cause Notice as decided in the Meeting on 15.01.08 was issued to the Unit on 22.02.08. Reply  received.  Applied for authorization under BMW Rules on 12.03.08. 

Inspection was done on 30.04.08 & following are the main observations :

(i) The site / Premises is the Central Office of the Unit which imports medicines/ drugs from the Korea & distributes in India . Discarded / expiry medicines / drugs are collected back & disposed through this office.

(ii) Separate Storage room not provided for the storage of discarded medicines / drugs & the same was kept in common room.

(iii) Log Book for the expired / discarded medicines need to be maintained. 

(iv) Bio – Hazard sybol not provided on the discarded medicines box.

(v) The unit has agreement with M/s Synergy Waste Management Pvt. Ltd for the disposal of discarded medicines / drugs.

(vi) The unit is having 3 DG Sets of 50 KVA( 2 No.) & 25 KVA ( One No) with acoustic enclosure.

VII.Reply dated 13-06-08.regarding rectification of the deficiencies found during inspection (Separate storage room for discarded medicines with proper  Bio Hazard Symbol) was received.       


	Letter issued. 
	Ask the unit to submit affidavit for correction of deficiencies observed during the inspection. Call on 14.07.2008.
	Letter issued.
	Issue reminder seeking affidavit  for correction of deficiencies. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	66.
	Imperial Marketing Services (Johnson & Johnson Ltd.), 9/43, Kirti Nagar,  Delhi-15
	Storage & Distribution of Medicines & Drugs 
	…..
	12.05.08
	---------
	1.Show Cause Notice as decided in the Meeting on 15.01.08 was issued to the Unit on 22.02.08 since not applied for authorization.. Reply received however had not applied for authorization under BMW Rules .

2.Inspected on 29.04.08. Following are the main observations :  

(i) It is a ware house which is also centre for the storage  & distribution of medicines & drugs of Johnson & Johnson Ltd.  

(ii) About 1000 kg of expired drugs was found stored for disposal.

(iii)As per certificate dated: 03.01.08 given by the operator of a facility that      686Kg of solid waste & 1225 liters of liquid waste has been destroyed.

(iv) The unit has agreement with M/s Synergy Waste Management Pvt. Ltd.       for the disposal of the discarded medicines / drugs

(iv ) Having 3 nos. of DG set of capacity 2x125 KVA & 1x160 KVA & the stack height provided with DG sets are adequate. (Acoustic enclosure provided). 

3. As per the decision taken on 06.05.08, a letter was issued. Reply received informed regarding rectification measures taken ( provided Bio- Hazard symbol on the storage site.). Applied for authorization under BMW Rules.


	Letter issued. 

EE(BMW)  talked to the official (s)

of the unit.

Reply received .
	Ask the unit to submit affidavit for correction of deficiencies observed during the inspection. Call on 14.07.2008.
	Letter issued.
	Issue reminder seeking affidavit  for correction of deficiencies. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	67.
	Keimed Limited, E-18, B-1 Extn, Mohan Co-operative Industrial Estate, Mathura Road,  Delhi-44
	Drug Stockist/ Marketing 
	S - 
	 31.03.08 
	-----
	Show Cause Notice as decided in the Meeting on 15.01.08 was issued to the Unit on 22.02.08. Premises were inspected on 03.03.08 and unit  found engaged in Storage of Drugs / Pharmaceuticals and its marketing . It was informed that only one time ( on 09.10.07) a consignment of discarded drugs of 125 kg was given to M/s Synergy Waste Management Pvt. LTD. For its disposal.  It was also informed that unit is sending back the discarded medicines to the manufactures, however in case of such eventuality the unit shall dispose the BMW to one of the approved Common BMW Operators. Reply not received. Not Applied for authorization under BMW Rules.

SCN issued. Premises were inspected on 03.03.08 and unit found engaged in Storage of Drugs / Pharmaceuticals and its marketing . It was informed that only one time ( on 09.10.07) a consignment of discarded drugs of 125 kg was given to M/s Synergy Waste Management Pvt. LTD. For its disposal.  It was also informed that unit is sending back the discarded medicines to the manufactures, however in case of such eventuality the unit shall dispose the BMW to one of the approved Common BMW Operators. Reply not received. Not Applied for authorization under BMW Rules.As decided in the meeting on 18.03.08, letter for deficiencies was issued.
Reply dated  .12-06-08.w.r.t latter dated 06-05-08.regarding confirmation about taking corrective measure as required by B MW committee.
	EE(BMW)  talked to the official (s)

of the Unit. Reply Received.


	Ask the unit to submit affidavit for correction of deficiencies observed during the inspection. Call on 14.07.2008.
	Letter issued.
	Issue reminder seeking affidavit  for correction of deficiencies. Call on 27.08.2008.

	68.
	Apollo Hospitals Enterprises Limited (Ahel Unit Apollo Pharmacy), IMCL Complex, Sarita Vihar, Delhi-Mathura Road,  Delhi-76
	Stocking & Selling of medicines / Drugs
	S-299
	 31.03.08
	-----
	Show Cause Notice as decided in the Meeting on 15.01.08 was issued to the Unit on 22.02.08. Applied for authorization under BMW Rules on  0.08.

Inspection was done on 30.04.08 & following are the main observations :

(i) This site is the Centre for the NCR for distribution of the medicines/ drugs of Apollo Pharmacy. 

(ii) Separate Storage room / Isolated storage site  not provided for the storage of discarded/ expired medicines / drugs. 

(iii) Labeling of Bio – Hazard Symbol not provided.

(ii) Proper records/ Log Book not maintained for discarded medicines / drugs.

(iv) The unit has agreement with M/s Synergy Waste Management Pvt. Ltd for the disposal of discarded medicines / drugs.   

(V).No reply received.


	Letter issued .
	Ask the unit to correct deficiencies and submit affidavit for correction of deficiencies observed during the inspection. Call on 14.07.2008.
	Letter issued.
	Issue reminder seeking affidavit  for correction of deficiencies. Call on 27.08.2008.

	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	69
	Becton Dickinson India P.Ltd., 2, Community Centre , 3RD Floor, Anand House , Saket w Delhi -17) ( Head Office at 6th Floor Signature Tower-B South City, 
	…..
	…..
	19.03.08 
	Not applied
	Show Cause Notice as decided in the Meeting on 15.01.08 was issued to the Unit on 22.02.08. Reply not received. Not Applied for authorization under BMW Rules / Consent to Establish.

Applied for authorization. on 19-03-08.

Inspected.


	Inspected.
	Inspect the storage site at Mandoli. 
	To be inspected.
	4 member team  comprising of Dr. T.K. Joshi, EE(BMW), Dr. Chetna &  Trainee to inspect. Call on 27.08.2008.


	Sl No.
	Name and Address of HCU
	Bed (No.)
	Dist. No.
	Authorization Application Date
	Consent Application Date
	 Status of the Case / Remarks 
	Action Taken w.r.t. Meeting on 06.05.08. 
	Decision Taken  on 13.06.08.
	Action Taken w.r.t. Meeting on 13.06.08.
	Decision Taken  on 14.07.08.

	70


	M/s Foundation International Charitable Trust Society,

306, Kohat Enclave, Pitampura, Delhi -34
	…….
	
	……….
	Not Applied for CTE 
	The project figures in the list of 18 projects provided by MoEFvide letter dated 16.04.08. As directed by Chairman DPCC Notice issued on 30.04.08 for applying for consent to establish and to submit environment clearance from MoEF 

2. Decision taken on 06.05.08 :  

  EE (BMW) to follow up. 

Ask the unit to file following five things :

(i)Consent to Establish

(ii)Environmental Clearance

(iii)Affidavit indicating date of start of construction and completion of construction.

(iv) Approved architectural drawing

(v) Completion Certificate.

 Chairman,DPCC, to inspect.


	Letter  issued. 

To be inspected by Chairman, DPCC.
	Issue letter seeking :

1. Affidavit indicating date of start of construction and date of completion. 2. Completion certificate. 3. Approved architectural drawing. 4. Details of water drawl. 5. Permission for water drawl. 6. Details of  waste water discharge   7. Details of D.G. Sets.8. Plot area. 9. Builtup Area. 10. Application for Consent to Establish. 11.Copy of Environmental Clearance.Inspection to be carried out alongwith Dr. Joshi 


	Letter issued.
	MS ,DPCC  to direct the unit to apply for Consent to Establish  & also seek copy of  Environmental Clearance . Unit to  submit the required data  as asked based on the decision taken on 13.06.08. Call on 27.08.2008.




	Sl No.
	Name and Address of  HCU
	Bed (No.)
	Dist. No.
	Authorization Application 

Date
	Consent Application 

Date
	Status of the Case / Remarks
	Action Taken w.r.t Meeting on 06.05.08
	Decision Taken on 13.06.08
	
	

	71
	Oscar Bio Tech Pvt. Ltd. (Multi Super Specialty Hospital, A- Bl;ock, Shalimar Bagh, Delhi-52) office address D-5, !st floor,Okhla Industrial Area, Phase-1, Delhi-20 
	550
	
	……..
	Applied for CTE 20.12.05. 
	The unit has applied for consent to establish on 20.12.05 for 550 beded hospital at A-Block Shalimar Bagh. Plot area as per affidavit submitted is 29664 Sq. m and built up area will be 5515 .29 sq.m. Proposed date of commissioning as per application was 01.12.07.  water consumption total 830 KLD(Domestic 40KLD, sanitation 265KLD, cooling 495KLD, horticulture 20KLD & others 10 KLD). ETP with design capacity of 250KLD is proposed with secondary and tertiary treatment. Treated wastewater will be reused for cooling and horticultural purpose.  DG sets- 1000KVA & 750 KVA proposed with acoustic enclosure.  It is mentioned that unit will comply with BMW Rules.

As per the decision taken by CMC in its meeting taken on 18.02.08, a letter was issued to the unit on 07.03.08 asking EIA clearance which it appears to have received on 20.04.07.

2.Reply dated 21-05-08 regarding  approval for consent to establish for the construction of hospital along with original affidavit was received. 

3. Decision taken on 06.05.08 :

Environmental Clearance (EC) filed. Ask the unit to file item-wise compliance of the EC conditions during the construction and the general conditions. Unit be also asked to commit on affidavit that it will follow the  conditions in the operation phase. Response to be filed by BMW Cell in the meeting on 13.06.08. Check from the website of MOEF whether there is any adverse order in this case. Ask  to file following  :

(i)Affidavit indicating date of start of construction and completion of construction.

(ii) Approved architectural drawing

(iii) Completion Certificate

Chairman, DPCC, to inspect.


	Letter issued.  Reply received, 

To be inspected by Chairman, DPCC.
	Issue letter directing to submit :

 1. Details of water drawl. 2. Permission for water drawl. 3. Details of  waste water discharge   4. Details of D.G. Sets.5. Plot area. 6. Builtup Area. 

Inspection to be carried out along with    Dr. T.K.Joshi.
	Letter issued
	Call for personal hearing on 27.08.2008 at 3.00 PM. By that time unit must comply with all the documentary evidence including CGWA clearance, ETP installation and item wise compliance of EC conditions. Call on 27.08.2008.

.

	Sl No.
	Name and Address of  HCU
	Bed (No.)
	Dist. No.
	Authorization Application 

Date
	Consent Application 

Date
	Status of the Case / Remarks
	Action Taken w.r.t Meeting on 06.05.08
	Decision Taken on 13.06.08
	
	

	72
	Society of Unique Hospital & Research Institute ( Multi Super Specialty Hospital & Research Institute at   Sector-19 Dwarka, Delhi) office address BD-73, Pitam Pura, Delhi-88
	400
	
	…………
	14.7.2006 
	The unit has applied for consent to establish on 14.07.06 for 400beded hospital at Sector-19 Dwarka, Delhi. Plot area as per affidavit submitted is 31502 Sq. m and built up area will be 29819.917 sq.m. Proposed date of commissioning as per application was 01.10.07.  water consumption total 340 KLD(Domestic 180KLD, cooling 140KLD, others 20 KLD). ETP with design capacity of 150KLD is proposed with secondary and tertiary treatment. Treated wastewater will be reused for cooling and horticultural purpose.  DG sets- 3 nos of 750 KVA capacity each proposed with acoustic enclosure. 3nos. oil fired boilers (1500Kg/hours. It is mentioned that unit will comply with BMW Rules.

Environmental Clearance given by MoEF vide letter dated 16.05.07. As per the decision taken by CMC in its meeting taken on 18.02.08, a letter was issued to the unit on 11.03.08 asking to file an affidavit for compliance of EIA clearance conditions. However no reply received in this regard.

Decision Taken on 06.05.08 :

Environmental Clearance (EC) obtained. Ask the unit to file item-wise compliance of the EC conditions during the construction and the general conditions. Unit be also asked to commit on affidavit that it will follow the  conditions in the operation phase. Response to be filed by BMW Cell in the meeting on 13.06.08. Check from the website of MOEF whether there is any adverse order in this case.. Ask  to file following  :

(i)Affidavit indicating date of start of construction and completion of construction.

(ii) Approved architectural drawing

(iii) Completion Certificate

Chairman,DPCC, to inspect.
	Letter issued. 

To be inspected by Chairman, DPCC.
	Issue letter directing to submit the documents/details sought earlier and submit :

1. Affidavit indicating date of start of construction and date of completion. 2.  Details of water drawl. 3. Permission for water drawl. 4. Details of  waste water discharge   5. Details of D.G. Sets 6. Plot area. 7. Builtup Area.

Inspection to be carried out alongwith Dr. T.K.Joshi


	Letter issued.
	Ask the unit to file the CGWA clearance for ground water. Regarding  waste water  i.e. 144 KLD, direct the unit to install the ETP and also file the required documents as per the decision taken on  13.06.2008. Call on 27.08.2008.



	Sl No.
	Name and Address of  HCU
	Bed (No.)
	Dist. No.
	Authorization Application 

Date
	Consent Application 

Date
	Status of the Case / Remarks
	Action Taken w.r.t Meeting on 06.05.08
	Decision Taken on 13.06.08
	
	

	73
	Delhi Biochemical Research Laboratory, 4874, Ansari Road, 24 Daryaganj, Delhi-2
	0
	C-034
	20- Mar- 07
	Not Applied
	Case of Research institute. As decided by the Chairman DPCC, all Research Institute to be taken up by  BMW Committee no.1.

Decision taken on 06.05.08:

Ask the unit to apply for Consent to Establish under the Air & Water Acts.

Not applied for Consent to  Establish & Operate
	Letter  issued.
	Inspect.
	To be inspected.
	4 member team  comprising of Dr. T.K. Joshi, EE (bmw), Dr.Chetna,  Trainee  to l inspect. Call on 27.08.2008.

	74
	St. Stephen's Hospital 

Tis Hazari, Delhi-54


	595


	N-002


	13-Jun-06

(valid up to 

5-Jul-09)


	Consent granted
	1. Authorization and Consent Granted
	As per the general decision taken on 06.05.08, letter issued for installation of (a) Solar water heating system (b) Rain water harvesting system (c) Replacement of ordinary Bulbs with CFL (d)  ETP (e) Plantation of trees along side of the periphery of the Hospital building.
	Ask the unit to apply for Consent to Establish and compliance of letter dated 26.05.2008.
	Letter issued.
	MS , DPCC  to direct MS of the hospital to file application for Consent to Establish  and to seek  compliance  w.r.t letter issued to the Hospital  on 26.05.2008. Call on 27.08.2008.


Annexure 3

Decisions taken w.r.t Agenda No. 3 in the Meeting of BMW Committee No.1, Held on 14.07.08
Agenda  No. 3  :  Action Taken Report  w.r.t Annexure  III of  Minutes of  Meeting of BMW Committee                              No.1 Held on  13.06.08, for the Meeting on  14.07.08  (Cases of 510 Health Care                               Units  wherein Show Cause Notices  and  reminders were issued earlier to apply                              for authorization under BMW Rules). 

Decision Taken By the   BMW Committee-1, in the Meeting Held  on   15.01.08 :  

(i) Regarding 6 Reminder Notices issued ( 5 from the list of 93 cases and  1 from the list of 22 cases) mentioned above since the units have informed that they are treating less than 1000 patients per month no further action is required.

(ii) Letter / representation received from M/s Agarwal Nursing Home, F-81, Street no. 4, Virender Nagar, Janakpuri, New Delhi-58,  to be put on file .

(iii) The Committee confirmed the decision of Member Secretary regarding 67 cases to be ascertained from DHS for their registration details.

Action Taken Report w.r.t. BMW Committee-1, in the Meeting Held on 15.01.08 : 
(i) Letter / representation received from M/s Agarwal Nursing Home, F-81, Street no. 4, Virender Nagar, Janakpuri, New Delhi-58 submitted on file.

(ii) Letter issued to DHS seeking present status of the 67 cases. Response awaited.

Decisions Taken By the   BMW Committee No.1, in the Meeting Held  on   18.03.08 :
(i)Regarding  Letter / representation received from M/s Agarwal Nursing Home, F-81, Street no. 4, Virender      Nagar, Janakpuri, New Delhi-58, ----  No Action in this case. 

(ii)Regarding  letter issued to DHS seeking present status of the 67 cases ,  DHS may be reminded by Member      Secretary , DPCC , to submit details. 
Action Taken Report w.r.t. BMW Committee-1, in the Meeting Held on  18.03.08 :
(i) Regarding  Letter / representation received from M/s Agarwal Nursing Home, F-81, Street no. 4, Virender      Nagar, Janakpuri, New Delhi-58, ----  No Action was required as per the decision taken by the Committee. 

(ii) Reminder Letter issued to DHS seeking present status of the 67 cases & to submit details.  Reply awaited.

Decisions Taken in the Meeting of BMW Committee No. 1, on 06.05.08 : 

    Both EE and MS to chase up with DHS and get the required details by 13.06.2008.
Action Taken Report w.r.t. BMW Committee-1, in the Meeting Held on  06.05.08 :

Another letter issued to the Director, DHS, by the Member Secretary. DPCC, requesting present status of the 67 cases & to submit details.  Also talked to Director DHS over phone in this regard & as informed reply will be submitted soon. Reply  awaited.

Decisions Taken in the Meeting of BMW Committee No. 1, on 13.06.08 : 

                                Issue  reminder  letter.   Matter to be taken up on   14.07.2008.

Action Taken Report w.r.t. BMW Committee-1, in the Meeting Held on  13.06.08 :

                               Reminder letter issued. Reply received from  DHS.

Decisions Taken in the Meeting of BMW Committee No. 1, on 14.07.08 : 

                                              Put up on file for administrative decision. 

         
              (J.K. Dadoo)          ( K Mahesh )          ( Dr.T.K.Joshi)    (Dr. Chetna Harjai)           ( D.K.Singh )           (Sanjay Vats )          ( Shyam Sunder )  

           Chairman,DPCC        M.S.,DPCC         COEH, MAMC     Scientist, Env.Deptt,          EE ( BMW)            AEE ( BMW)              AEE ( BMW) 

Annexure 4

Decisions taken w.r.t Agenda No. 4  in the Meeting of BMW Committee No.1, Held on  14.07.08
Agenda No.4: Action Taken Report w.r.t Annexure V  of  Minutes of Meeting of BMW Committee No.1, Held on                  13.06.08 for the Meeting on 14.07.08 ( Issue Regarding letters issued for acoustic enclosure, noise                    monitoring report for DG sets, affidavit for compliance, in respect of the 160 Health Care Units /                    Nursing Homes)  

A representation has been received from DMA Nursing Home & Medical Establishment Forum regarding the Show Cause Notices u/s 21 of the Air Act , issued to Nursing Homes by DPCC. 159 Show Cause Notices u/s 21 of the Air Act were issued to  Health Care Units /Nursing Home which had not applied for consent to DPCC (The HCU was required to apply for consent, if having DG Set or Boiler and if not an affidavit was sought in this regard )  based on the decision taken by the BMW Committee No. 2 in its meeting held on 31.07.07.  

On the said Representation, Chairman, DPCC, had directed that they will file an affidavit stating they will put acoustic enclosures within 3 months. Let them do so & then put up in CMC (BMW) on 15.11.07.

Decision Taken by the BMW Committee No.1, in the Meeting on 15.11.2007: 

A letter be issued to DMA Nursing Home & Medical Establishment Forum informing that Nursing Homes having DG Set(s) are required to provide proper acoustic enclosure for DG Set(s) / acoustic treatment of the room where DG Set( s)  is installed to meet the prescribed norms for DG Set and also required to provide adequate stack height  with the DG Set(s) . Three months time given for compliance of the above and also for submission of Noise Monitoring report ( after providing Acoustic Enclosure / Acoustic treatment of the room) from any of the Empanelled laboratories by DPCC. They will also submit an Affidavit regarding compliance of the above within 3 months.

Similar letter be issued in case of other Health Care units mentioned above (which have been issued Show Cause Notice u/s 21 of Air Act.).   

Action taken w.r.t. decision taken on 15.11.07: 

Letter issued to DMA Nursing Home & Medical Establishment Forum.  Reply received from DMA and informed that they have written to their members to comply with section 21/22 of Air Act at the earliest and install a proper acoustic enclosure for DG Set (s) , acoustic treatment of the room where DG Set(s) is installed to meet the prescribed norms for DG Set and get them approved by the laboratories empanelled by DPCC.  An Affidavit has also been submitted by the President of the said DMA Nursing Home & Medical Establishment Forum, in this regard. It is informed in the Affidavit that above requirement shall be fulfilled on or before 27.02.2008.

Letters issued to the aforementioned Health Care units including 38 Nursing Homes.

Decision Taken on 15.01.08

In view of the affidavit filed by the President of the DMA Nursing Home & Medical Establishment Forum, the case of the DG sets of Nursing Homes in BMW  Cell  be taken in March, 2008. By that time BMW Cell, may prepare list of Nursing Homes which have not confirmed regarding providing acoustic enclosure and noise monitoring.

Action taken w.r.t. decision taken on 15.11.07 & 15.01.08 

Status of the Health Care Establishments including 38 Nursing Homes which were issued letters after the decision taken on 15.11.07 is summarized below; 

(i) .Letters issued to HCUs



: 160

(ii). No response / no reply



: 121
(iii). Compliance affidavit submitted (w/o NMR)
:     1

(iv).  Noise Monitoring Report (NMR) received 
: 15 (in 1case old NMR and in 1 case consent to                                                                                                     operate + NMR)

(v). Letter received regarding no DG set

 :   7

(vi). Letter / Misc. Representation received

 : 11
(vii). Application submitted for Consent to Operate
 :   5

Contd….2


2
Decision Taken By the   BMW Committee No.1, in the Meeting Held  on   18.03.08 :
Member Secretary, DPCC,  to call the  Office Bearer of the  DMA Nursing Home & Medical Establishment Forum and ask them to give compliance report by 31.03.2008.

Action taken w.r.t. decision taken on  18.03.08 :

Member Secretary, DPCC,  called  the  Office Bearer of the  DMA Nursing Home & Medical Establishment Forum on  26.03.08 and ask them to give compliance report by 31.03.2008. Another  representation  dated 20.03.08 received from the said Forum regarding request for exclusion of the Nursing Homes from the provisions of the Air & Water Acts . As per the decision taken by the BMW Committee No 2, in its meeting held on 05.02.08 letters were issued seeking application for Consent to Establish under Air & Water Acts within one month.. It was informed to the Office Bearers of the Forum that similar decision has also been taken by the BMW Committee No.1 & provisions of the Air and Water Acts and relevant sections of theses Acts were shown to the President of the Forum. Minutes of the said meeting was also sent to the Forum Vide letter dated 28.03.08.The Forum has submitted the status vide letter dated 15.04.08 and further updated status vide letter dated 30.04.08. 

Decisions Taken in the Meeting of BMW Committee No. 1, on 06.05.08 : 
The DMA Nursing Home & Medical Establishment Forum  may be called for a meeting in the chamber of Chairman, DPCCC,  on 19.05.2008 at 3.00 PM. Complete updated status to  be provided to the Chairman , DPCC, two days in advance. 

Action taken w.r.t. decision taken on  06.05.08 :

 The office bearers of  DMA Nursing Home & Medical Establishment Forum were called for  meeting on 19.05.2008. The office bearers of the said forum could not attend the said meeting due to their preoccupation. As directed by Chairman DPCC, a letter was issued to the forum on 26.05.08 seeking compliance report in respect of all the Health Care Units/Nursing Homes registered with the forum. Forum has submitted status in respect of 749 HCU’s. The status is based on the telephonic enquiry by the forum. Summarized statement by the forum was placed before the Committee.

Decisions Taken in the Meeting of BMW Committee No. 1, on 13.06.08 : 

Issue Public Notice  to  all Health Care Establishments in  NCT Delhi, for submission of  an affidavit duly attested by the Notary Public, including statements (i) that  adequate  acoustic enclosure for DG Set(s) has been provided  or acoustic treatment of the room where DG Set( s)  is installed has been done to meet the prescribed norms by Ministry of Environment & Forest ,Govt. of India , for DG Sets  (ii) that adequate stack height has been provided as per the norms prescribed by Ministry of Environment & Forest ,Govt. of India , for DG Sets (iii)that Noise Monitoring report for the D.G.Set(s) from the empanelled  laboratory by Delhi Pollution Control Committee has been submitted to DPCC.  (iv) that  the Health Care Establishment is complying with the norms notified by the  Ministry of Environment & Forest ,Govt. of India , for DG Sets . 

Action taken w.r.t. decision taken on  13.06.08 :

                                              Public Notice issued  on 06.07.08 in Times of India & on 05.07.08 in Punjab Kesari.

Decisions Taken in the Meeting of BMW Committee No. 1, on 14.07.08 : 

                             Put up on file for administrative decision. 

                 (J.K. Dadoo)                            ( K Mahesh )                          ( Dr.T.K.Joshi) 

               Chairman,DPCC                         M.S.,DPCC                          COEH, MAMC      

Annexure 5

Decisions taken w.r.t Agenda No. 5 in the Meeting of BMW Committee No.1, Held on  14.07.08
Agenda  5:  Action Taken Report w.r.t Annexure 5 of Minutes of Meeting of BMW Committee No.1Held on

                    13.06.08(Decision Taken earlier on the List of Drug Manufacturing  Units,  List of Approved Testi                                   ng Laboratories, Blood Banks                  

 As per the decision taken by the BMW Committee No.1,  in the meeting held on 15.11.2007, a letter was issued to the Drugs Controller of GNCT, Delhi on 26.12.07 and the drug Controller was requested to provide the list of all registered drug mfg. units, R& D Laboratories etc. . Lists were collected personally from the Office of Drugs Controller, GNCT Delhi and following are the brief of the units mentioned in the lists ;

1.  No.of Licensed Drugs Manufacturing Units     :     92 (including 8 units of Homeopathic Medicines

2.  No. of  Approved Testing Laboratories             :     9

3.  No. of Licensed  Blood  Banks                        :   54 [Under Central Govt  -  8 ,  Under Govt. of Delhi              -   8

                                                                                         Under  MCD             -  3,  UnderVoluntary Organisation  - 3 

                                                                                        Under Pvt. Hospitals  - 25, Pvt. Blood Banks                --      7




                                            
            
Total            :    155

Decision taken by the BMW Committee No. 1, in the Meeting Held on 15.01.08 :  

The BMW Rules are clear that laboratories including research laboratories, drug manufacturing units and licensed blood banks should take authorization under BMW Rules. Therefore Committee decided that all the 9 testing laboratories and 3 Blood Banks of voluntary organizations and 7 Pvt. Blood Banks may be asked to seek authorization under BMW Rules, quoting relevant sections. As regard, licensed drug manufacturing units, only those units having R & D facilities / laboratories should be issued Show Cause Notice to apply for authorization quoting relevant sections, giving 3 months time to apply for authorization under BMW Rules. 

Action taken report w.r.t. decision taken on 15.01.08: 

(i)Show Cause Notice to apply for authorization under BMW Rules, giving 3 months time to apply for     authorization, issued to 87 units, out of above mentioned 92 units. Remaining 5 units had already     applied for authorization.

(ii)Letters issued to 8 testing laboratories out of 9 laboratories mentioned above, seeking application for      authorization under BMW Rules, giving 3months time. Remaining 1laboratory has already applied for      authorization.

(iii)Letters issued to 9 Blood Banks out of 10 Blood Banks mentioned above, seeking application for       authorization under BMW Rules, giving 3months time. Remaining 1 Blood Bank has applied for       authorization.

Decision Taken By the   BMW Committee No.1, in the Meeting Held  on   18.03.08 :  

Agenda Item No. 6 will be taken up in the month of  May, 2008.

Action taken report w.r.t. decision taken on  18.03.08: 

The matter is placed before the Committee .It is pertinent to mention here that letters for (i) to (iii) above were issued in the 3 rd / 4rth week of February , 2008 and 3 months time was given for applying for authorization under BMW Rules which is yet to be expired.

Decisions Taken in the Meeting of BMW Committee No. 1, on 06.05.08 :  

 To be taken up in the meeting on  13.06.2008 .  M.S. and EE to follow up.

Action taken report w.r.t. decision taken on  06.05.08: 

 The matter  was placed before the Committee and status was briefed. 
Decisions Taken in the Meeting of BMW Committee No. 1, on 13.06.08 :  

Issue a Public Notice  seeking application for authorization under the Bio- Medical Waste ( Management and Handling) Rules, 1998, as amended to date, from  all Drug/Pharmaceuticals   Manufacturing Units,  Pathological /Drug  Testing  Laboratories, Blood Banks,  referring the  provisions of the said rules regarding authorization.. 
Action taken report w.r.t. decision taken on  13.06.08: 

Public Notice issued in Hindustan Times on 02.07.08..

Decisions Taken in the Meeting of BMW Committee No. 1, on 14.07.08 :  

              Put up on file for administrative decision. 

  
(J.K. Dadoo)    ( K Mahesh )   ( Dr.T.K.Joshi)    (Dr. Chetna Harjai)      ( D.K.Singh )  (Sanjay Vats ) ( Shyam Sunder) Chairman,DPCC     M.S.,DPCC         COEH, MAMC       Scientist, Env.Deptt,          EE ( BMW)      AEE ( BMW)           AEE ( BMW) 

         

Annexure 6   

 Decision taken w.r.t Agenda No. 6 in the Meeting of BMW Committee No.1, Held on 14.07.08
Agenda-6 Action Taken Report w.r.t Annexure 6 of Minutes of Meeting of BMW Committee                   No.1 Held  on  13.06.08  (i) Regarding  Study on the Lead (ii)Regarding  Study on                   the effect of  Mercury waste
 (i) Action Taken Report w.r.t  Study on the Lead
      Earlier in meeting on 08.02.08 , It was decided that a study  has to be done of the      quantum of  lead used in Delhi and is likely adverse impact on the citizen of Delhi. Such      study will reveal  the appropriate strategy for handling and containing the   effect of lead on      the health of the  city.  Based on study further necessary action   will be taken. Information      sought by Dr.T.K.Joshi  was sent.

   
(ii) Action Taken  Report w.r.t Study on the Effect of Mercury Waste 

      In the meeting on 08.02.08 , it was decided that a formal study on  the effect of Mercury       Waste on  the citizens of Delhi will be done since as informed by Dr.T.K.Joshi,  no such      study in Delhi has been carried out earlier. Dr. T.K. Joshi will submit a proposal. The      proposal will also look at the appropriate technologies for disposal of Mercury waste in the          city.Information sought by Dr  T.K.Joshi  was  sent .

      

      Decision Taken in the Meeting of BMW Committee No. 1, on 06.05.08 

      I. Dr. T.K. Joshi to submit the proposals for both the studies (i) Study on the lead & (ii)          Study onthe Effect of Mercury Waste , within the month of May, 2008.

      Action Taken : Letters issued to Dr. T.K. Joshi for the proposal for both the studies (i)       Study on the lead &  (ii) Study on the Effect of Mercury Waste.

                               

     Separate  proposals for  both the studies, received from Dr. T.K.Joshi , were placed before      the Committee 

      Decision Taken in the Meeting of BMW Committee No. 1, on 13.06.08

     Both the proposals  received from Dr. T.K.Joshi  may be examined by Dr. Chetna Harjai,      Scientist , Deptt.of  Environment and put up  by 14.07.2008.

    Action  Taken  w.r.t decision taken  on 13.06.08
     Copy of both the Proposals were given to Dr. Chetna Harjai in the meeting on 13.06.08. Her      comments are awaited. 

      Decision Taken in the Meeting of BMW Committee No. 1, on 14.07.08
                        Put up on file for administrative decision. 

Annexure 7

Decision taken w.r.t Agenda No. 7 in the Meeting of BMW Committee No.1, Held on  14.07.08
         

Agenda -7 Action Taken Report w.r.t Annexure 7 of  Minutes of  Meeting of BMW  Committee                    No.1 Held on  13.06.08 (Management of Sharp Waste).

         A Seminar/ Advocacy Meeting was organized by Centre  for Environment Education (CEE) on 17.01.08  for imparting Training & Awareness on Bio- Medical Waste Management to Nursing Homes and Clinics in Delhi. Some of the representatives of Nursing Homes who were present in the Seminar  mentioned that Sharp Waste Equipment is not readily available in the market.  Chairman, DPCC had desired that , DPCC may take a view in this matter in the meeting of BMW Committee and send an appropriate letter through the Nursing Homes Association indicating the names of the quality – empanelled suppliers of such equipments.

         This Agenda was  placed before the Committee in the meeting held on 18.03.08 for decision on the aforesaid issue.

        Decision Taken by the BMW Committee No. 1  in its Meeting Held on 18.03.2008 :   

         According to the BMW Rules , sharps should be placed in  puncture proof  & leak proof containers. Instead of using conventional sharp boxes which are expensive and supplies are not regular, the simple plastic containers available in the market  may be used for storing sharps.

        Action Taken :Letter issued to the President of the  DMA Nursing Home & Medical                               Establishment Forum informing the above decision taken by the Committee.

Decisions Taken in the Meeting of BMW Committee No. 1, on 06.05.08 

         Dr. T.K.Joshi expressed  concern over the management of Sharp Waste & volunteered to draft directions to all the Hospitals & Nursing Homes for this purpose..            

        Action Taken : 



Letter issued to Dr. T.K.Joshi. Draft directions for management of sharp waste received & was placed before the Committee.




Decisions Taken in the Meeting of BMW Committee No. 1, on 13.06.08

Public Notice  on the Management of Sharp Waste to be issued  in two National Dailies, one in Hindi & one in English in 80 cc .  

Action taken w.r.t decision taken in the  meeting  on 13.06.08

Public Notice  on the Management of Sharp Waste prepared on the basis of the draft directions received from Dr. T.K.Joshi  and file is under process.


Decision Taken in the Meeting of BMW Committee No. 1, on 14.07.08

                                                            Complied. 
Annexure  8         

     Decisions Taken w.r.t Agenda No.8 in the Meeting of BMW Committee No. 1, on  14.07.08
 

Agenda-8  News Paper Item “Bio – medical waste plagues NCR” published in                   Times of India (Delhi Edition) on  5th May, 2008 regarding Training                   through  ASSOCHAM

The News Paper Item “Bio – medical waste plagues NCR”  published in Times of India (Delhi Edition) on  5th May, 2008 ( Copy enclosed) was also  taken as agenda item  as per the  directions of the  Chairman DPCC & this  was taken as Agenda No.10.

 Decisions Taken in the Meeting of BMW Committee No. 1, on 06.05.08 

For the news item on BMW, Member Secretary, DPCC, will talk to ASSOCHAM and offer the services of DPCC experts including Dr. T.K. Joshi, for arranging the training programme and for acquainting them with the operation of ETP & for disposing Bio – Medical Waste.To confirm in the next meeting of the BMW Committee on 13.06.08.

Action Taken Report:     Member Secretary,  DPCC talked to the Secretary General Sh. D.S. Rawat on the above matter and further action is to be taken by ASSOCHAM.

 Decisions Taken in the Meeting of BMW Committee No. 1, on 13.06.08 

                       Await the response of ASSOCHAM. 

 Action Taken  w.r.t decion taken in the  meeting  on 13.06.08 

                          Response of ASSOCHAM awaited.
 Decisions Taken in the Meeting of BMW Committee No. 1, on 14.07.08 
                                     Put up on file for administrative decision. 
     Annexure 9

Decision Taken w.r.t Agenda No. 9 , in the Meeting of BMW Committee No. 1 , held  on 14.07.08
AGENDA -9 : Surveillance / Monitoring of Health Care Establishment in                                Delhi.

During discussions with the representatives of the Audit Party (Accountant General (Audit), Delhi Office), in the meeting with the Chairman, DPCC, held on 27.05.2008, it was pointed out that regular monitoring of the Health Care Facilities/ Bio-Medical Waste Treatment Facilities (Incinerator/Autoclave etc.) is required which is lacking at present. As directed by Chairman, DPCC, the matter is placed before the Committee for decision.

     Decision Taken in the Meeting of BMW Committee No. 1, on 13.06.08 

The matter to be taken up in the next meeting on 14.07.08.

      Action  Taken w.r.t decision taken in the meeting  on 13.06.08 

 The matter is placed before the Committee .
     
  Decision Taken in the Meeting of BMW Committee No. 1, on 14.07.08 
                    Put up on file for administrative decision. 

   

Annexure  10

     Decision Taken   w.r.t Agenda No.10 , in the Meeting of BMW Committee No. 1, on      14.07.08 
AGENDA-10:  Case  of M/s Jagat Diagnostic Pvt. Ltd. B -82 , G.T.K. Road                           Industrial Area,  Delhi-33

Case of M/s Jagat Diagnostic Pvt, Ltd.B-82 ,G.T.K. Road Industrial Area, Delhi-33. was placed before the   CMC (Orange) in its  meeting held on 23.05.08. As per the decision taken by  the said Committee the case has been sent to BMW Cell  by CMC . 

The said unit is engaged in manufacturing of Blood Lancet, Dispo Swabs. As per the affidavit submitted by the unit.  The unit has applied for renewal of Consent under the Air & Water Acts on 23.02.07for the said activity .Earlier the Consent to Operate was issued to the unit on 04.02.04 ( valid upto 06.01.07) for the activity of   Blood Lancet , Dispo Swabs & ESR tubes with PVC  moulding.

Perusal of the application of the unit indicates that there is no generation of the BMW from the activities of the unit.

    

      Decision Taken in the Meeting of BMW Committee No. 1, on 13.06.08 

                                         Inspection of the unit.

      Action taken w.r.t. decision taken in the meeting on 13.06.08 

To be inspected.
     
      Decision Taken in the Meeting of BMW Committee No. 1, on 14.07.08 

Team comprising of Dr.T.K. Joshi, EE(BMW), Dr. Chetna Harjai  and   Trainee(BMW) to  inspect the unit. Call on 27.08.2008.
Annexure  11

     Decision Taken  w.r.t Agenda No. 11 ,in the Meeting of BMW Committee No. 1, on      14.07.08 
Agenda–11 Complaint  against Ayurveda Kendra , B- 5/ 99 , Safderjang Enclave , New                       Delhi -29. 
 A Complaint  against Ayurveda Kendra , B- 5/ 99 , Safderjang Enclave , New  Delhi -29.,  was received from Mr. N.K.Khanna of Safderjang Enclave & the said Ayurveda Kendra was inspected by the Official of PGRC of DPCC and the matter was also placed before the CMC in its meetings on 18.06.08 & 04.07.08 .As per the inspection report the said Ayurveda Kendra is engaged in Ayurvedic treatment & premises is used for Ayurvedic Clinic/Hospital & Bio –Medical waste is generated . 

CMC in its meeting on 18.06.08 has taken following decision in this case;

“  Based on the inspection report , it appears that it is an Ayurvedic hospital requiring authorization under BMW Rules . BMW Committee – I may inspect and report in the next BMW meeting on 14.07.08.”

In view of the above decision taken the matter is placed before the Committee.

      Decision Taken in the Meeting of BMW Committee No. 1, on 14.07.08 

The unit may be asked to apply for authorization under BMW Rules and also confirm installation of oil & grease trap. Call on 27.08.2008.

Annexure  12

     Decision Taken  w.r.t Agenda No. 12 ,in the Meeting of BMW Committee No. 1, on      14.07.08 
Agenda  12 :   Service Charges for Bio  Medical Waste Management by the
                       Operators of  Common Bio Medical Waste Treatment Facilities                        in Delhi.                         

Both the  Operators of  Common Bio Medical Waste Treatment Facilities in Delhi , authorized by Delhi Pollution Control Committee , are charging fee as service charges for providing Bio-Medical Waste  Management services to the Health Care Facilities in Delhi, including Govt. Hospitals( collection, transportation , treatment & disposal of BMW). It is learnt that the service charges are being enhanced by the operators often.  

1. M/s Synergy Waste Management Pvt. Limited, near Composite Plant,     Sukhdev  Vihar, Okhla, Delhi-20 

2. M/s Metro Bio-Care Services Pvt. Ltd., 55 Railway Road,  Samaipur, Delhi- 42. 

  In order to regulate and ensure that there is no exorbitant fee charged, the matter is placed before the BMW   Committee No. 1.  

 Decision Taken in the Meeting of BMW Committee No. 1, on 14.07.08 

Ask the two operators that on what basis they are charging the fee and how are they increasing the fee overnight by 100 %. A formal clear justification of increasing the fee may be submitted that must be examined properly and file may be submitted administratively.   If the unit does not behave ,  no further extension of authorization will be granted.  Reply must come within 15 days and file to be put up administratively. 
  

