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Minutes of the meeting of the 19" Meeting of the Commiittee constituted for deciding the

consent under the Air and Water Acts for Planning, Co-ordination & MSWM Cell held
on 10" June 2011.

1. The following lines appearing in the beginning of the minutes of 19" meeting of

CMC(MSW) held on 10" June 2011, in the case of Timarpur Okhla Waste

Management Company Limited (TOWMCL) at Okhla, are deleted as the same are
not applicable to this unit.

e CTO issued on 20.01.2010, valid up to 20.01.2012.
® NOC of AAI received from the unit on 22.01.2010.

o Authorization under MSW Rules issued on 04.02.2010, valid up to
03.02.2012.

2. The decision at point (3) of CMC (orange) w.r.t. cases of MSW Cell dated 20.4.2010
may read as Y

e The Hon’ble CM, Delhi has laid down foundation stone of the project on
28.06.2010.

The above error has occurred inadvertantly. Other facts mentioned in the minutes remain

unchanged.
@‘\\"%\\ \%
¢ 3 (B.Ku(ar)
4 Addl. Director
\W MSW Cell

P.S. to Chairman, DPCC- for kind information of Chairman please.
Member Secretary, DPCC

Prof. S.K. Gupta, Member (Acdm Institution)
Dr. Anil Kumar, Member (Env. Deptt.)

Addl. Director, MSWM Cell, DPCC

SEE, MSWM Cell, DPCC

EEs MSWM Cell, DPCC

N wop e

In-charge, Computer Cell, DPCC — soft copy of minutes is also enclosed for placing the
aforementioned minutes of the committee on the Website of DPCC.




Minutes of the 19th meeting of the CMC (MSW) held on 10.06.2011 in the Conference room of Chairman, DPCC.
The following officers attended the meeting on 10th June, 2010:

1. Sh. Keshav Chandra, Chairman, DPCC

2. Dr. A.K Ambasht, Member Secretary, DPCC

3. Prof S.K Gupta, Member (Acdm Institution)

4. Dr. Anil Kumar, Member (Env. Dept)

5. Sh. B. Kumar, Addl. Director, DPCC

6. SEE (MSWM Cell)

7. EEs of MSWM Cell

The 19th meeting of the Committee constituted for deciding the Consent under the Air and Water Acts, for CETPs, STPs, WTPs, MSW Projects & Power Plants cases was held on 10th June, 2011 and decision taken in the meeting with respect to following agendas are recorded in the enclosed sheets:

Cases of STPs:- Decisions taken with respect to STPs are annexed as Annexure -1.
Cases of Water Treatment Plants- Decisions taken with respect to Water Treatment Plants are annexed as Annexure- 2.
Cases of CETPs:- All the cases of CETPs were discussed and the decisions taken with respect to these cases are annexed as Annexure-3. 

Cases of Power Plants: - Decisions taken with respect to Power Plants are annexed as Annexure-4.
Cases of Municipal Solid Waste Management Project and Slaughter House:-Decisions taken with respect to all Municipal Solid Waste Management Projects and Slaughter House are annexed as Annexure- 5.
Cases regarding pending issues of the Local Area Environment Committee: - Decisions taken with respect to pending issues of the Local Area Environment Committee are annexed as Annexure- 6.
Table Agenda items: Two cases were taken as table agendas and decisions taken are annexed as Annexure- 7.
Meeting ended with thanks to the Chair.
*****

Annexure – 1

Dr. Sen Nursing home Nallah STP  (2.2 MGD)

Consent Status 
Consent to operate (Renewal) was issued on 08.02.10 valid upto 12.05.11

Applied for renewal of consent to operate on 19.04.2011.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue letter to CEO, DJB enclosing monthly monitoring reports for taking necessary action to comply with the norms, wherever the quality is not meeting the norms. 
Action taken/ Status after the meeting held on 09.08.2010:

1. A D.O letter with enclosed copy of monthly monitoring reports to CEO, Delhi Jal Board from Member Secretary, DPCC was issued on 10.09.2010.

2. A copy of letter, sent to DGM (Operation), PPCl in response to our letter dated 10.09.2010, by Executive Engineer (SDW) V was received on 13.10.2010 in which; EE has asked PPCL to look into the matter.
3. After examining the monthly analysis report for the months of August, September, October, November 2010 it was found that, parameters are  meeting the prescribed standards for the month of November
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

No action.
Action taken/ Status after the meeting held on 11.01.2011:

1. The unit has applied for renewal Consent to operate  on 19.04.2011
2.  A surprise inspection and sampling of effluent  was carried out  by      DPCC laboratory on 12.05.2011 after 10:00 PM After examining       the  analysis report dated 12.05.2011 it was found that parameters       are meeting the prescribed standards.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Grant renewal of consent to operate.


Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Delhi Gate Nallah STP, (10 MLD)

Consent Status
Consent to operate (Renewal) issued on 07.05.10 valid upto 02.02.2013
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

 No Action.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

No action.
Action taken/ Status after the meeting held on 11.01.2011:

A surprise inspection and sampling of effluent  was carried out  by DPCC laboratory on 12.05.2011 after 10:00 PM After examining the analysis report dated 12.05.2011 it was found that parameters are meeting the prescribed standards.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

No action.
Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

KONDLI STP , Ph-I (10 MGD)
Consent Status
Renewal of Consent to operate issued on 08.02.2010 and valid upto 16.08.2012.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue letter to CEO, DJB enclosing monthly monitoring reports for taking necessary action to comply with the norms, wherever the quality is not meeting the norms. 

Action taken/ Status after the meeting held on 09.08.2010:

1. A D.O letter with enclosed copy of monthly monitoring reports to CEO, Delhi Jal Board from Member Secretary, DPCC was issued on 10.09.2010.

2. After examining the monthly analysis report for the months August, September, October, November 2010 it was found that, parameters are meeting the prescribed standards for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

No action.
Action taken/Status after the meeting held on 11.01.2011:

1. After examining the monthly analysis report for the month of April 2011 it was found that, parameters are meeting the prescribed standards for the month.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

No action.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

KONDLI STP, Ph-II  (10 MGD)

Consent Status 
Consent to Operate issued on 08.02.2010 and valid upto 16.08.2012. 
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

No Action.

Action taken/ Status after the meeting held on 09.08.2010:

 1. After examining the monthly analysis report for the months of August, September, October, November 2010 it was found that parameters are meeting the prescribed standards for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011 :

No action.
Action taken/ Status after the meeting held on 11.01.2011:

1.A surprise inspection and sampling of effluent  was carried out  by DPCC laboratory on 03.05.2011 after 10:00 PM and during the inspection a bypass arrangement was observed, Accordingly a SCN for revocation /refusal of consent and SCN for direction under section 33(A) of water Act 1974 were issued on 31.05.2011.Reply is awaited.

2. After examining the analysis report dated 03.05.2011 it was found that parameters are not meeting the prescribed standards.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Decision, to issue SCN for refusal of consent and SCN of directions u/s 33(A) of Water Act, 1974, taken on file ratified.

Put up administratively after the receipt of the reply or after the expiry of time within which the reply should be filed.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

KONDLI STP, Ph-III , (10 MGD)

Consent Status
Renewal of Consent issued on 20.08.2008 & valid upto 02.12.2010.

Applied for renewal of consent to operate on 01.12.2010
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

No Action.
Action taken/ Status after the meeting held on 09.08.2010:

1. After examining the monthly analysis report for the months of August, September, October, November 2010 it was found that, parameters are not meeting the prescribed standards w.r.t TSS, BOD & Phosphate for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit to rectify the deficiencies, if any, to comply with the norms laid down.
Action taken/ Status after the meeting held on 11.01.2011:

     1.  DJB has applied for renewal of consent on 01.12.2010.

2. A surprise inspection and sampling of effluent  was carried out  by DPCC laboratory on 03.05.2011 after 10:00 PM and during the inspection a bypass arrangement was observed, Accordingly a SCN for revocation /refusal of consent and SCN for direction under section 33(A) of water Act 1974 were issued on 31.05.2011.Reply is awaited.

3.  After examining the analysis report dated 03.05.2011 it was found that parameters are not meeting the prescribed standards.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Decision, to issue SCN for refusal of consent and SCN of directions u/s 33(A) of Water Act, 1974, taken on file ratified.

Put up administratively after the receipt of the reply or after the expiry of time within which the reply should be filed.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

 Nehru Vihar, Oxidation Pond SFTP (13.5 MGD)

Consent Status 
Consent to operate (renewal) issued on 28.01.2011 and valid up to 19.09.2013.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

No Action.
Action taken/ Status after the meeting held on 09.08.2010:

1. After examining the monthly analysis report for the months of August,     September, October, November 2010 it was found that, parameters are    meeting the prescribed standards for the month of November
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011 :

Issue renewal of consent.
Action taken/ Status after the meeting held on 11.01.2011:

   1. In compliance of CMC (MSW) consent to operate (renewable) issued on        28.01.2011.

4. After examining the monthly analysis report for the month March  it was found that parameters are meeting the prescribed standards but  it  was found non operational in the month of April. 
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

No action.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Keshopur STP 60 MGD (40+20)

Consent Status 
Renewal of Consent to operate issued on 08.02.10 and valid upto 06.01.11. 
Not applied for renewal of consent to operate.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

 No Action.

Action taken/ Status after the meeting held on 09.08.2010:

1.After examining the monthly analysis report for the months of August, September, October, November 2010 it was found that, plant was found non-operational due to maintenance for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011 :

Ask the unit to submit application for consent under air and water act.
Action taken/ Status after the meeting held on 11.01.2011:

    1. In compliance of CMC (MSW) a letter seeking application for consent under air and water act was issued on 02.02.2011. DJB has not submitted an application for consent till date.
2.  After examining the monthly analysis report for the month April 2011 it was found that, plant was found non-operational due to maintenance for the month.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Issue reminder to DJB to submit application for CTO(R).

Chairman
M. S.
  Member    Prof. S.K Gupta          AD    SEE            EE    
DPCC      DPCC      Env. Deptt.   Member (Acd. Inst) (MSW)     MSWM Cell

Mehrauli  STP (5 MGD)

Consent Status

Consent to operate (renewable) issued on 28.01.2011 & valid upto 12.10.2013. 

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue reminder seeking application for renewal of consent to operate. 

Action taken/ Status after the meeting held on 09.08.2010:

A reminder letter was issued to STP seeking application for renewal of consent to operate on 03.09.2010.

After examining the monthly analysis report for the month of August, September, October, November 2010 was found that, parameters are meeting the prescribed standards for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011 :

Issue renewal of consent.
Action taken/ Status after the meeting held on 11.01.2011:

1.  In compliance of CMC (MSW) consent to operate (renewal) was issued on      28.01.2011.

2. After examining the monthly analysis report for the month of April 2011 it was found that parameters are meeting the prescribed standards .

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

No action.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Yamuna Vihar Phase –I STP (10 MGD)
Consent Status 
Renewal of Consent issued on 28.01.2011 valid upto 09.11.2013.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

No Action.
Action taken/ Status after the meeting held on 09.08.2010:

1. After examining the monthly analysis report for the months of August,        September, October, November 2010 it was found that, parameters are    meeting the prescribed standards for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011 :

Issue renewal of consent.
Action taken/ Status after the meeting held on 11.01.2011:

1.In compliance of CMC(MSW) decision consent to operate(renewable)    issued on 28.01.2011.

2.A surprise inspection and sampling of effluent  was carried out  by DPCC        laboratory on 12.05.2011 after 10:00 PM After examining the analysis      report dated 12.05.2011 it was found that parameters are meeting the prescribed standards.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

No action.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Yamuna Vihar Phase –II STP  (10 MGD)
Consent Status 
Renewal of consent issued on 08.02.10 valid up to 13.12.2012.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

No Action.
Action taken/ Status after the meeting held on 09.08.2010:

1.After examining the monthly analysis report for the months of August,        September, October, November 2010 it was found that, parameters are     meeting the prescribed standards for the month of November
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011 :

No action.
Action taken/ Status after the meeting held on 11.01.2011:

1.A surprise inspection was carried out  by DPCC laboratory on 12.05.2011 after 10:00 PM but no effluent was coming to the plant from sewage pump station ,therefore sampling could not be done. After examining the monthly analysis report for the month of April 2011 it was found that parameters are meeting the prescribed standards
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

No action.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Rithala STP– Ph-I, (40 MGD)
Consent Status 
Renewal of Consent to Operate was issued on 08.02.10 valid upto 30.06.12. 
 Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

No Action.
Action taken/ Status after the meeting held on 09.08.2010:

1. After examining the monthly analysis report for the months of August,
     September, October, November 2010 it was found that, parameters are        meeting the prescribed standards for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

No action.
Action taken/ Status after the meeting held on 11.01.2011:

1.A surprise inspection and sampling of effluent  was carried out  by DPCC laboratory on 03.05.2011 after 10:00 PM and during the inspection STP was found functional but treatment is not done adequately .Accordingly a SCN for revocation /refusal of consent and SCN for direction under water Act 1974 were issued on 31.05.2011.Reply is awaited.

2. After examining the analysis report dated 03.05.2011 it was found that parameters are not meeting the prescribed standards.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Decision, to issue SCN for refusal of consent and SCN of directions u/s 33(A) of Water Act, 1974, taken on file ratified.

Put up administratively after the receipt of the reply or after the expiry of time within which the reply should be filed.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Rithala  STP– Ph-II, ( 40 MGD)

 Consent Status 
Consent to operate (renewable) issued on 28.01.2011 and is valid upto 
 13- 12-2013.
Decision of  Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue reminder seeking application for renewal of consent to operate.
Action taken/ Status after the meeting held on 09.08.2010:

1. A reminder letter was issued to STP seeking application for renewal of consent to operate on 03.09.2010

2. After examining the monthly analysis report for the months of August, September, October, November 2010 it was found that, parameters are  meeting the prescribed standards for the month of November.
3. Applied for renewal of consent to operate on 14.12.2010 
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011 :

Issue renewal of consent.
Action taken/ Status after the meeting held on 11.01.2011:

1.In compliance of CMC(MSW) decision consent to operate(renewal) issued       on 28.01.2011 and is valid upto 13-12-2013.
2. A surprise inspection and sampling of effluent  was carried out  by DPCC laboratory on 03.05.2011 after 10:00 PM After examining the analysis report dated 03.05.2011 it was found that parameters are meeting the prescribed standards.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

No action.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Papankalan STP ( 20 MGD)
Consent Status 
Renewal of consent to operate issued on 10.02.2011 valid upto 26.12.2013.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

No Action.
Action taken/ Status after the meeting held on 09.08.2010:

1. After examining the monthly analysis report for the months of August, September, October, November 2010 it was found that, parameters are meeting the prescribed standards for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Issue renewal of consent.
Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC(MSW) decision renewal of consent to operate      issued on 28.01.2011.

2. After examining the monthly analysis report for the month April it was found that parameters are meeting the prescribed standards.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

No action.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Najafgarh STP, ( 5 MGD)
Consent Status 
Renewal of consent to operate issued on 10.02.2011 valid upto 26.12.2013.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

No Action.
Action taken/ Status after the meeting held on 09.08.2010:

1. After examining the monthly analysis report for the months of August, September, October, November 2010 it was found that, parameters meeting the prescribed standards for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Issue renewal of consent.  
Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC(MSW) decision consent to operate(renewal) issued   on 10.02.2011.

2. After examining the monthly analysis report for the month of April it was    found that parameters are meeting the prescribed standards.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

No action.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Nilothi STP (40 MGD)

Consent Status
Consent issued on 08.02.2010 valid upto 25.11.2010.
Applied for renewal of consent to operate on 15.04.2011.  
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

No Action.
Action taken/ Status after the meeting held on 09.08.2010:

1. A letter was received by EE (SDW) VI on 25.10.2010 in which they have enquired about the exact amount of fee for renewal of consent.

2. In response to this a letter a letter was sent to the EE (SDW) VI on 29.10.2010 along with the fee structure.

3. After examining the monthly analysis report for the months of August, September, October, 2010 it was found that, parameters are meeting the prescribed standards for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011 :

Ask the unit for submission of application for consent under air and water act.
Action taken/ Status after the meeting held on 11.01.2011:

1. A letter asking the unit for submission of application for consent under air    and water act issued on 02.02.2011.
2. The unit has applied for renewal of consent to operate on 15.04.2011.
3. After examining the monthly analysis report for the month April it was     found that parameters are meeting the prescribed standards.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Grant renewal of consent to operate.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Rohini STP (15 MGD)
Consent Status 

Consent to Operate issued on 08.02.2010 valid upto 30.04.2010

Applied for renewal of consent to operate on 13.04.2011
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue a DO letter to CEO (DJB) to look into the matter as plant is non-operational.
Action taken/ Status after the meeting held on 09.08.2010:

1. A D.O letter to CEO, Delhi Jal Board from Member Secretary, DPCC was issued on 10.09.2010. No reply received from the DJB.
2. After examining the monthly analysis report for the months of August, September, October, November 2010 it was found that, plant was non-operational due to no flow for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit for submission of application for consent under air and water act.
Action taken/ Status after the meeting held on 11.01.2011:
1. In compliance of CMC (MSW) decision a letter asking the unit for submission of application for consent under air and water act issued on 02.02.2011. DJB has applied for renewal of consent on 13.04.2011. 

2. After examining the monthly analysis report for the months of April 2011 it has found that sampling could not be done due to no flow at the time of Monitoring.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Send a DO letter urging DJB to take waste water flowing in the adjacent drain for treatment, as the plant is heavily underutilized.
Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Coronation Pillar STP (40 MGD)

Consent Status
Renewal of Consent to operate issued on 08.02.2010 valid upto 11.03.2012. 

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

No Action.
Action taken/ Status after the meeting held on 09.08.2010:

1. After examining the monthly analysis report for the months of August, September, October, November 2010  it was found that, phase I and III  were non operational due to under maintenance and parameters of Phase II are  meeting the prescribed for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

No action.
Action taken/ Status after the meeting held on 11.01.2011:

1.A surprise inspection and sampling of effluent  was carried out  by DPCC laboratory on 12.05.2011 after 10:00 PM and during the inspection a bypass arrangement was observed, Accordingly a SCN for revocation /refusal of consent and SCN for direction under water Act 1974 were issued on 31.05.2011.Reply is awaited.

2. After examining the analysis report dated 12.05.2011 it was found that      parameters are not meeting the prescribed standards.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Decision, to issue SCN for refusal of consent and SCN of directions u/s 33(A) of Water Act, 1974, taken on file ratified.

Put up administratively after the receipt of the reply or after the expiry of time within which the reply should be filed.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Vasant Kunj STP (5.2 MGD)

Consent Status 

Renewal of Consent to operate issued on 08.02.10 valid up to 28.01.11. 
Not  applied for renewal of consent to operate.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue letter to CEO, DJB enclosing monthly monitoring reports for taking necessary action to comply with the norms, wherever the quality is not meeting the norms. 
Action taken/ Status after the meeting held on 09.08.2010:

A D.O letter with enclosed copy of monthly monitoring reports to CEO,   Delhi Jal Board from Member Secretary, DPCC was issued on     10.09.2010. No reply received from the DJB.
After examining the monthly analysis report for the months of August, September, October, November 2010 it was found that, parameters are meeting the prescribed standards for the month of November.
 Not applied for renewal of consent to operate.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit to apply for renewal of consent.

Action taken/ Status after the meeting held on 11.01.2011:

1.A letter asking the unit for submission of application for consent under air and water act  issued on 02.02.2011. However DJB has not applied for conent till date.
2.After examining the monthly analysis report for the month of April it was    found that parameters are meeting the prescribed standards. 
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:
Issue reminder to DJB seeking application for CTO(R).

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Narela STP (10 MGD)

Consent Status
Applied for renewal of consent on 3.01.2008, valid upto 13.01.2011.
Not applied for renewal of consent.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

No Action.
Action taken/ Status after the meeting held on 09.08.2010:
1. After examining the monthly analysis report for the months of August, September, October, November 2010 it was found that, parameters are meeting the prescribed standards for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

No action.
Action taken/ Status after the meeting held on 11.01.2011:

1. DJB has not applied for renewal of consent after its expiry on 13.01.2011 till date. 

2. After examining the monthly analysis report for the month April 2011 it was found that parameters are meeting the prescribed standards
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Issue reminder to DJB seeking application for CTO (R).

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

OKHLA STP , [Phase- I, II, III & IV, (12+30+37+45), Total 124 MGD)

Consent Status :

Consent is renewed for all the four plants on 03.06.2008 & valid upto 09.03.2011.

Applied for renewal of consent for all the four plants on 7.02.2011.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue letter to CEO, DJB enclosing monthly monitoring reports for taking necessary action to comply with the norms, wherever the quality is not meeting the norms. 
Action taken/ Status after the meeting held on 09.08.2010:

 D.O letter with enclosed copy of monthly monitoring reports to CEO, Delhi Jal Board from Member Secretary, DPCC was issued on 10.09.2010.

After examining the monthly analysis report for the months of August, September, October, November 2010 it was found that, Plant III was non-operational and parameters of plant II are not  meeting the prescribed standards w.r.t TSS (54mg/L) and Phosphate (6.4 mg/L)for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit to rectify the deficiencies, if any, to comply with the norms laid down.
Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of decision Letter for rectification of deficiencies was issued on 01.02.2011.

2. A surprise inspection and sampling of effluent  was carried out  by DPCC laboratory on 03.05.2011 after 10:00 PM and during the inspection a bypass arrangement was observed, Accordingly a SCN for revocation /refusal of consent and SCN for direction under section 33(A) of water Act 1974 were issued on 31.05.2011.Reply is awaited.

3. After examining the analysis report dated 03.05.2011 it was found that parameters are not  meeting the prescribed standards.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Decision, to issue SCN for refusal of consent and SCN of directions u/s 33(A) of Water Act, 1974, taken on file ratified.

Put up administratively after the receipt of the reply or after the expiry of time within which the reply should be filed.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Okhla STP,Phase-V (16 MGD)

Consent Status:
Renewal of Consent issued on 28.01.2011 & valid upto 06.12.2013.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue letter to CEO, DJB enclosing monthly monitoring reports for taking necessary action to comply with the norms, wherever the quality is not meeting the norms. 
Action taken/ Status after the meeting held on 09.08.2010:

1. A D.O letter with enclosed copy of monthly monitoring reports to CEO, Delhi Jal Board from Member Secretary, DPCC was issued on 10.09.2010.

2. After examining the monthly analysis report for the months of August, September, October, November 2010 it was found that, parameters are  meeting the prescribed standards for the month of November
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Issue renewal of consent.
\

Action taken/ Status after the meeting held on 11.01.2011:

1.In compliance of CMC(MSW) decision renewal of  consent issued on 28.01.2011.
2. After examining the monthly analysis report for the month April  2011 it was found that, parameters are  meeting the prescribed standards 
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

No action.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

STP at C-DOT Campus, Chattarpur, Mehrauli, New Delhi-30.(125 KLD)

Consent Status :
Renewal of Consent issued on 03.06.2008 valid upto 10.03.2011.
Not applied for renewal of consent.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

No Action.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit to submit treated effluent quality report once in six months.

Action Taken Report:

1. In compliance of CMC(MSW) decision a letter seeking submission of treated effluent quality report once in six months was issued on 02.02.2011.Reply awaited. 

2. The unit has not applied for renewal of consent after its expiry on 10.03.2011 till date.  
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:
Issue letter to the unit seeking application for CTO (R).

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Bakkarwala STP, (3 MLD)
Consent Status 
Consent to operate (renewable) issued on 28.01.2011 valid upto 01.02.2013

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue a reminder seeking application for renewal of consent to operate.
Action taken/ Status after the meeting held on 09.08.2010:

1. A reminder letter was issued seeking application for renewal of consent to operate on 03.09.2010.

2. A D.O letter with enclosed copy of monthly monitoring reports to CEO, Delhi Jal Board from Member Secretary, DPCC was issued on 10.09.2010.

3. In response to our letter dated 10.09.2010, a letter was received from Executive Engineer, DD-I, Delhi Urban Shelter Improvement Board, stating that STP Bakkarwala have been transferred to Delhi Jal Board and any further correspondence may be taken up with DJB.

4. In response to our letter dated 10.09.2010, a letter was received from Executive Engineer, (SDW)-VIII , wherein it was mentioned that at the time of sampling the blower was un-operative due to electric fault. The same was rectified and the quality of the treated effluent is within limits.

5. After examining the monthly analysis report for the months of August, September, October, November 2010 it was found that, parameters are meeting the prescribed standards for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:
Issue consent.
Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC decision consent issued on 28.01.2011 valid upto 01.02.2013

2. After examining the monthly analysis report for the month of April 2011 it was found that, parameters are meeting the prescribed standards.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

No action.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Molar Band STP (3 MLD)
Consent Status 

Consent to Operate issued on 28.01.2011 valid upto 2.09.2013.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue a reminder seeking application for renewal of consent to operate.
Action taken/ Status after the meeting held on 09.08.2010:

1. A reminder letter was issued to STP seeking application for renewal of consent to operate on 03.09.2010. DJB applied for consent.

2. A D.O letter with enclosed copy of monthly monitoring reports to CEO, Delhi Jal Board from Member Secretary, DPCC was issued on 10.09.2010.

3. After examining the monthly analysis report for the months of August, September, October, November 2010  it was found that, plant was non operational for the month of November.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Issue  Consent.
Action taken/ Status after the meeting held on 11.01.2011:

1. Consent to operate was issued 28.01.2011 valid up to 02.09.2013.

2. After examining the monthly analysis report for the month of April      2011 it was found that, parameters are meeting the prescribed     standards.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

No action.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

                            

Holambi Kalan STP, (2 MLD)
Consent Status 
Consent to Operate issued on 14.05.04 valid upto 08.10.06.

Not applied for renewal of consent to operate.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue a reminder seeking application for renewal of consent to operate.
Action taken/ Status after the meeting held on 09.08.2010:

1. A reminder letter was issued to STP seeking application for renewal of      consent to operate on 03.09.2010
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011 :

Ask the unit for submission of application for consent under air and water act.
Action taken/ Status after the meeting held on 11.01.2011:

1. A letter seeking submission of application for consent under air and water act was sent on 02.02.2011.

2. DJB has not submitted application for consent till date.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Call for personal hearing before MS, DPCC. Officers from both DJB and JJ Department be called.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Tikri Khurd STP (2 MLD)
Consent Status 

Consent to Operate expired on 12.06.06. 
Not applied for renewal of consent to operate.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue a reminder seeking application for renewal of consent to operate.
Action taken/ Status after the meeting held on 09.08.2010:

1. A reminder letter was issued to STP seeking application for renewal of consent to operate on 03.09.2010.

2. Not applied for renewal for consent to operate.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit for submission of application for consent under air and water act.
Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC decision a letter was issued on 02.02.2011     asking submission of application for consent under air and water.     However, DJB has not applied for consent till date.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Call for personal hearing before MS, DPCC. Officers from both DJB and JJ Department be called.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Ghitorni STP,  (5 MGD)
Consent Status 

Not applied for consent.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue a reminder seeking application for consent to operate.
Action taken/ Status after the meeting held on 09.08.2010:

1. A reminder letter was issued to STP seeking application for consent to operate on 03.09.2010

2. Executive Engineer (SDW)V, Delhi Jal Board, submitted a reply to our letter, on 24.09.2010, stating that the STP is neither commissioned as yet nor it is in operation at present as no sewerage has been connected so far with the STP.

3. Not applied for consent.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit for submission of application for consent under air and water act.
Action taken/ Status after the meeting held on 11.01.2011:

1. A letter seeking submission of application for consent under air and water act was sent on 02.02.2011. However, DJB has not applied for consent till date.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Defer for next meeting, as the plant is not receiving any waste water for treatment.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

STP at National Bureau of Plant Genetic Resources ICAR, Pusa Campus,  (80 KLD)
Consent Status 

Consent to Operate expired on 07.06.07. 
Not applied for renewal of consent.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
Issue a reminder seeking application for renewal of consent to operate and send list of empanelled consultants to improve STP’s performance.

Action taken/ Status after the meeting held on 09.08.2010:

1. A reminder letter was issued to STP seeking application for renewal of consent to operate on 03.09.2010.

2. A copy of letter sent to Executive Engineer (Elect.)  by Sr. Admn. Officer, NBPGR, Pusa Campus was received by this office on 27.09.2010, in response of our letter asking CPWD to look into the matter regarding consent to operate as STP is under AMRO with CPWD.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit for submission of application for consent under air and water act and to submit treated effluent quality report once in six months.
Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC(MSW) decision a letter seeking submission of application for consent under air and water act and treated effluent quality report once in six months was issued on 02.02.2011.

2. In response to our letter Senior Administrative officer has submitted a letter wherein it has requested to provide details of repair works for proper running of the STP,so that it meets their standard requirements. It is also requested to suggest regarding “Consent to operate STP under the Water Act,1974 & the Air Act,1981”.
3. Not applied for renewal of consent.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Call for personal hearing before MS, DPCC. 

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Annexure - 2
Haiderpur Water Treatment Plant
Consent status:

· Consent to Establish issued on 08.02.10 valid upto 07.02.2011.

· Consent to Operate issued on 08.02.10 valid upto 12.02.2011.
· Applied for renewal of consent on 08.02.2011.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

No action. Inspect the plant to ascertain final discharge, after recycling, to drain/sewer. 

WTP was inspected by team of DPCC officials on 07.01.2011 and observations made are as under: 

· Unit has installed the recycling plant of 16 MGD.

· Left out or back wash water from the treatment units is being recycled.   
· Plant is having zero discharge concept. 
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011 :

Ask the unit to submit application for renewal of consent under air and water act.
Action Taken Report:

1. In compliance of CMC Decision a letter seeking submission of application for renewal of consent under air and water act on 07.02.2011.

2. In response DJB has submitted application for renewal of consent under air and water act was on 08.02.2011.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011 :

Grant renewal of consent to operate.

Call a meeting of DJB officers before MS to discuss treatment system and recycling of filter backwash water.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Nangloi Water Treatment Plant

Consent status:

· Consent to Establish issued on 03.11.08 valid upto 09.10.2009.
· Not applied for consent to operate. 

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue reminder seeking application for consent to operate.

Action taken/ Status after the meeting held on 09.08.2011:

1. Reminder letter seeking application for Consent to Operate under Air and Water Acts issued on 03.09.2010. 
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit to submit application for renewal of consent under air and water act and Inspect the plant to ascertain the status of recycling of back wash water.
Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC decision, a letter dated 04.02.2011 seeking submission of application for renewal of consent under air and water act. However, a deficiency memo for completion of application was issued on 15.03.2011 from Enquiry Counter. The unit has not submitted application till date.
2. As decided an inspection of the WTP was conducted to ascertain the status of recycling of back wash water. And during the inspection it was found the waste water generated by back washing of 16 no. filter beds is being recycled after taking back into raw water. 

3. There is no provision for treatment of waste water /sludge generated from the clarifier. Moreover, there is no provision for solidification of sludge and muddy sludge/ waste water and same is being discharge into drain at present. 

4. Water treatment Plant (40 MGD) found in operation. Raw water is being treated through 4 nos clarifiers and 16 nos filter beds. By using poly aluminum chloride and alum. 

5.   Pre and Post Chlorination are done by using a solution of required strength of chlorine gas with water.

6. There are three under ground reservoir for storing clear water and two  clear water pumping stations, in old pump house there are  7 nos. pump sets of capacity 10 MGD each and 3 nos  pump sets of capacity 7.5 MGD and  in new pump house there are  8 nos  pump sets of capacity 17.5 MGD.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011 :

Issue reminder seeking application for renewal of consent to operate.
Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Wazirabad Water Treatment Plant

Consent status:

· Consent to Establish issued on 08.02.10 valid upto 07.02.2011.
· Consent to operate issued on 09.02.2011 valid upto 30.09.2013

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue reminder seeking application for consent to operate. Inspect the plant to ascertain final discharge, after recycling, to drain/sewer.

Action taken/ Status after the meeting held on 09.08.2010:

1. Reminder letter seeking application for Consent to Operate under Air and Water Acts issued on 03.09.10.  

2. The unit has applied for consent to operate.

WTP was inspected by team of DPCC officials on 07.01.2011 and observations made are as under:
· Unit has installed the recycling plant of 12 MGD.
· Left out or back wash water from the treatment units is being recycled.   
· 100 percent left out/back wash is being recycled.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011 :

Issue renewal of consent.
Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC decision Consent to operate issued on 09.02.2011 valid upto 30.09.2013

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011 :

No action.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Chandrawal  Water Treatment Plant-I

(35 MGD)

Consent status:

· Consent to Establish issued on 08.02.10 valid upto 07.02.2011.
· Consent to operate issued on 01.09.10 valid upto 27.06.2013.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue CTO.

Action taken/ Status after the meeting held on 20.04.2010:

1. Consent to Operate under Air and Water Acts issued on 01.09.10.  

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

No action. Ask the unit to recycle the backwash water in the plant.

Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC(MSW) decision a letter to recycle the backwash water has been issued. No action taken report received as yet.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011 :

Call a meeting of DJB officers before MS to discuss treatment system and recycling of filter backwash water.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

                         Chandrawal  Water Treatment Plant-II

(55 MGD)
Consent status:

· Consent to Establish issued on 08.02.10 valid upto 07.02.2011.
· Consent to Operate issued on 01.09.2010 valid upto 27.06.2013.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue CTO.

Action taken/ Status after the meeting held on 09.08.2010:

1. Consent to Operate under Air and Water Acts issued on 01.09.2010.  
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011 :

No action.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011 :

Call a meeting of DJB officers before MS to discuss treatment system and recycling of filter backwash water.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Bhagirathi Water Treatment Plant

Consent status:

· Consent to Establish issued  on 08.02.10 valid upto 07.02.2011.
· Not applied for consent to operate.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue reminder seeking application for consent to operate.

Action taken/ Status after the meeting held on 09.08.2010:

1. Reminder letter seeking application for Consent to Operate under Air and Water Acts issued on 03.09.2010.  

2.  Not applied for consent to operate.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit to submit application for renewal of consent under air and water act.
Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC decision a letter seeking submission of application for renewal of consent under air and water act was issued on 04.02.2011.however DJB has not applied till date.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011 :

Issue reminder seeking application for renewal of consent to operate.

Call a meeting of DJB officers before MS to discuss treatment system and recycling of filter backwash water.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

                                Sonia Vihar Water Treatment Plant
Consent status:

· Consent to operate granted on 13.03.2007 valid upto 08.12.2009.
· Consent to operate granted on 09.02.2011 valid upto 02.12.2013.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue reminder seeking application for consent to operate.

Action taken/ Status after the meeting held on 09.08.2010:

1. Reminder letter seeking application for Consent to Operate under Air and Water Acts issued on 03.09.2010.  

2. Applied for consent to operate (renewal) on 03.12.2010.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Issue renewal of consent and ask the unit to recycle the backwash water in the plant.
Action taken/ Status after the meeting held on 09.08.2010:

1. In compliance of CMC decision Consent to operate issued on 09.02.2011 valid upto 02.12.2013 and a letter for recycling the backwash water in the plant has been issued. No action taken report received as yet.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011 :

Call a meeting of DJB officers before MS to discuss treatment system and recycling of filter backwash water.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Annexure -3
Jhilmil & Friends Colony Indl Area CETP ( 16.8 MLD)

[
Consent status of CETP

· CTR issued on 07.05.10 and valid upto 03.01.2013.
· Renewal of authorization issued on 09.09.2010 valid upto 08.09.2015.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue authorization (Renewal) under HWM Rules.

Action taken/ Status after the meeting held on 09.08.2010:
1. Renewal of authorization under HWM rules issued on 09.09.2010.

2. Besides above in compliance of CMC(MSW) decision a letter regarding Bank Guarantee was issued on 17.09.10

3. In response of our letter dated 17.09.10 a reply was received on 25.09.10. In letter they have mentioned following points:
A. Regarding parameter :

(i) The historical data clearly indicates of the fact that Jhilmil CETP is maintaining pH, TSS and BOD parameters within limits always.

(ii) There have been instances of exceedance of TDS or chlorides sometimes but TDS, Chlorides, Fluorides have already been exempted by CMC (MSW) in its meeting on 19.08.2010.

B. Regarding Bank Guarantee 

(i) CETP Society pointed out functions of Delhi Pollution Control Committee as per the Water, Air, Hazardous Waste and Noise Pollution  Act as specified by Govt. of India and it has mentioned that the demand of Bank Guarantee is nowhere in the mandate of the DPCC. Society also objected that they are maintaining the essential parameters of pH, TSS, and BOD within limits always so there is no requirement of submission of any Bank Guarantee. 

4. A letter was received on 09.09.10 regarding repair of Doppler flow meter from CETP societies. 
CETP was inspected by team of DPCC officials on 13.09.2010 and 08.12.2010 the observations made are as under: 
· Flow meter installed after equalization tank is under maintenance.

· There are two vacuum drum filters out of which one is out of order due to non availability of space parts and another is not functioning properly.

· An arrangement for fitting the V- notch in tube settler is required.

· There are two flash mixers out of which one found out of order.

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	September,2010
	October,2010

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-252

Cr(Total)-4.0
	Meeting Standards except TDS 
	       TSS-256 
	Meeting Standards




             

	November, 2010
	December, 2010

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-272

Cr(Total)-2.44
	Meeting Standards except TDS
	Meeting Standards                
	       TDS-3220

      Fluoride-2.4


    All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:
Inform CMC to take action against individual units as waste water reaching at inlet of CETP is not meeting the standard. Issue reminder seeking bank guarantee and also removal of deficiencies observed during inspection. 

Action taken/ Status after the meeting held on 11.01.2011:

1. In response to CMC (MSW) decision a note issued to CMC to take action against individual units as waste water reaching at inlet of CETP is not meeting the standard on 17.03.2011. No action taken report received. Also a reminder seeking bank guarantee and removal of deficiencies observed issued on 09.02.2011.

2. In response to our letter the Society has submitted a point wise reply wherein it is stating that all the parameters except TDS is being maintained regularly. Regarding discrepancies w.r.t operation of CETP it has reported the plant has been in operation since 2005 and is under aging and the machinery needs overhauling and maintenance regularly, vacuum filter is under replacement for the same society has already initiated action and its replacement shall be in place by June 2011and work of rectification of weir plate shall be in place by June 2011.further regarding submission of bank guarantee it has mentioned that bank guarantee is not applicable as CETP is regularly maintaining the parameters within limit.
CETP was inspected by team of DPCC officials on 14.03.2011 the observations made are as under: 
· Flow meter installed after equalization tank is under repair.

· Out of two vacuum drum filter one is out of order due to non availability of spare parts. A proper alternative arrangement for solidification of sludge is required.

· Sludge transfer pump to drum filters not found at site. At present temporary arrangement of sludge transfer from sludge tender to equalization tank no-2 has been made.                                                                                                                                                                                                                                                                                                                                       

· Out of three agitators in equalization tank no-1, one agitator found not in order.

· There are two flash mixers out of which one found out of order.

· Total intake in Jan -130.272 ML Feb-125.838 ML upto 13th March-49.981 ML Average flow-4.491 MLD, Total Sludge Stored-101.15 MT.
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	January,2011
	February,2011

	Inlet
	Outlet
	Inlet
	Outlet

	Meeting Standards


	 Cl-1100

TDS-3380

Fluoride-2.4

 
	Meeting Standards


	TDS-2200




             

	March, 2011
	April, 2011

	Inlet
	Outlet
	Inlet
	Outlet

	Meeting Standards


	 TDS-3100

Fluoride-2.1


	                    
	TDS-2400

Sulphide-3.0




    All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated  10/06/2011:

Issue reminder for submission of Bank Guarantee.

Ask the CETP Society to rectify the deficiencies.
Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

GTK Road Indl Area CETP ( 6 MLD)

Consent Status of CETP

· CTE issued to DSIIDC on 20.01.04 valid upto 19.01.05. 

· CTO issued to DSIIDC on 15.09.04 valid upto 27.07.07.

· Not applied for renewal of consent to operate.
· Authorization issued on 27.01.2005. Valid upto 26.01.07.

·  Not applied for renewal of authorization.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue D O letter to the Commissioner of Industries requesting him to take appropriate action against the CETP Society with in 15 days under the provisions of CETP Act, failing which action as decided earlier to prosecute the Society will be taken. Also, the list of defaulters provided by Society to be sent to the Appropriate Authority.

Action taken/ Status after the meeting held on 09.08.2010:

1. In compliance of CMC (MSW) decision a DO letter was issued on 24.09.2010 and a list of defaulters is sent to COI for necessary action on 08.09.2010.

2. A reminder D.O letter was again issued to Commissioner of Industries by Chairman DPCC on 08.12.2010. However no response has been received so far

3. Besides above in compliance of CMC (MSW) decision a letter regarding Bank Guarantee was issued on 29.09.2010.

4. In response to our letter dated 29.09.2010 CETP submitted a reply on 07.10.2010 in which it has stated that its performance had always been in line to the requirements of department for parameters of pH, TSS and BOD, and hence has asked the basis of demand for a bank guarantee.

5. A letter was received from CETP Society regarding monthly analysis report of inlet & outlet effluent of CETP Nangloi on 30.12.2010.

6. Not applied for renewal of consent and authorization under HWM Rules.
CETP was inspected by team of DPCC officials on 10.09.2010 and 13.12.2010 the observations made are as under:
· No flow meter at inlet of CETP
· There are four pumps in REPS pumping station out of which one is under maintenance.
· There are two equalization tanks with two aerators in each tank. Out of which one aerator found not in operation in each tank.
· There is no fixed arrangement for discharging the effluent from sludge thickener. At present a temporary arrangement with flexible pipe and pump has been made.
· There are three pumps for discharging treated effluent to clear water holding tank out of which one is under maintenance.
· As reported the vacuum drum filters are not in operation. Also no dry sludge observed near sludge collection site.
· Display boards are not as per HWM Rules.
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	September,2010
	October,2010

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-1600

Cr(Total)-3.94
	Meeting Standards 
	       TSS-428 
	Meeting Standards




             

	November, 2010
	December, 2010

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-468
	Fluoride-2.5
	Meeting Standards

               
	Meeting Standards




    All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Call the Society for personal hearing before Chairman, DPCC.

Issue reminder seeking bank guarantee and also removal of deficiencies observed during inspection.
Action taken/ Status after the meeting held on 11.01.2011

1. In compliance of CMC (MSW) decision a letter was issued on  07.02.2011 but president could not attend the personal hearing  and thereafter a reminder was issued on 07.03.2011 for personal hearing in the Conference room of Chairman, DPCC at 6th Level, C Wing, Delhi Secretariat, New Delhi.
2. In response of our letter dated 7.03.11 a reply was received on 11.03.11. In letter the president is diverting the issue and have requested for date, time and venue of next meeting on any day during 24th– 31st March 2011. However CETP has not applied for consent as well as authorization under HWM Rules till date.
3. As decided a D.O letter was issued to commissioner of industries on 09.05.11.reply is awaited.

4. Additional Commissioner of Industries (CETP) took a meeting with  Shri S.P. Gupta, President, G.T. Karnal Road, CETP Society in the presence of Sh. S.K. Singh, Dy. Commissioner of Industries (CETP) and Sh. Sharat Kumar, Chief Project Manager (CETP DSIIDC) and minutes of the meeting dated 18.05.2011. In regard to renewal of consent to operate by DPCC in favour of G.T. Karnal Road, CETP Society the Appropriate Authority is of the view that matter is between DPCC and CETP society. In case it is mandatory to get renewed the consent to operate for the CETP Plant in that case DPCC being regulatory body should take necessary step in this regard as per provision of relevant Act/Law in the matter. The standard of treatment and discharge also as per law. 
]

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	January,2011
	February,2011

	Inlet
	Outlet
	Inlet
	Outlet

	Meeting Standards
	Meeting Standards 
	Meeting Standards 
	Sulphide-3.2


             

	March, 2011
	April, 2011

	Inlet
	Outlet
	Inlet
	Outlet

	Meeting Standards
	Floride-4.0
	Meeting Standards          
	Meeting Standards


    All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10/06/2011:

Launch prosecution proceedings against all office bearers of the CETP Society for not applying for consent.

Also, ask the CETP Society to submit Bank Guarantee.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

                            Lawrence Road CETP (12 MLD)
Consent status of CETP
· CTR issued on 11.05.2010 and valid upto 13.12.2010. Not applied for renewal.
· Authorization valid upto 26.01.07. Applied for renewal of authorization under HWM Rules on 06.12.07.
·  Not applied for authorization under HWM Rules as per new fee structure.
 Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Ask the unit to submit fresh application for authorization under HWM Rules. Send comments on IIT Delhi report, if required. 

Action taken/ Status after the meeting held on 09.08.2010:

1.  A letter is issued for compliance of decision of  CMC(MSW) meeting on 03.09.2010
2. Besides above in compliance of CMC (MSW) decision a letter regarding Bank Guarantee was issued on 15.10.10.
3. Regarding Bank Guarantee the CETP submitted a reply dated 29.11.2010 in which they have mentioned that generally TSS has been found beyond the permissible limits at the inlet of CETP for which DPCC is empowered to take necessary action.
4.  DSIIDC has not submitted any reply regarding our letter dated 03.09.2010.However has submitted reply regarding Bank Guarantee on 11.12.2010

5. Not applied for renewal of authorization under HWM Rules

6. DSIIDC has submitted a letter dated 21.10.2010 regarding modification of CETP, for which they have engaged IIT Delhi and wants comments of DPCC on the IIT report. 
7. In this regard it is to inform, that there is no need to comment on this issue as IIT-Delhi is an expert in research and academic field if agreed and approved.
CETP was inspected by team of DPCC officials on 10.09.2010 and 09.12.2010 the observations made are as under: 
-    At the time of inspection the CETP was found partially operational.

· Flow meter installed near receiving chamber found not in operation. 

· The grit removal arrangement consisting of three separate sections with chains found not in operations. Therefore the effluent received from REPS is directly received in equalization tank.

· There are two equalization tanks with two agitators in each tank but tank no-I is used as storage tank without having motor in agitators.

· There are two pumps for dosing of alum, polyelectrolyte and bleaching respectively out of which only pumps for dosing of polyelectrolyte are operational and other found non-operational.

· Also there is no fixed arrangement for dosing of Alum, Polyelectrolyte near flash mixer at present open plastic pipes has been provided for the same.

· At present no arrangement has been made for pre-chlorination in PCT.

·  There are three pumps for flash mixer pump house out of which two are under maintenance, thereof no standby arrangement.

· There are three pumps in clear water pump house out of which one is under maintenance.

· At present treated effluent from tube settler is being bypassed from DMF & ACF and directly discharged into drain.

· The sludge generated in tube settler is not being transferred to sludge thickener holding tank and vacuum drum filter it is being discharge directly into drain. 
· Regular cleaning is required in flocculation tank and tube settler for removal of scum.

· As reported no record of sludge is being maintained in CETP Lawrence Road.
· As informed the average flow reaching  CETP is 1.889 MLD due to heavy silt in REPS.
· No display board as per HWM Rules.

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	September,2010
	October,2010

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-280
	BOD-38

TDS-3200

Sulphide-3.5

 
	Meeting Standards 
	BOD-48

Cl-1049

Fluoride-2.08




             

	November, 2010
	December, 2010

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-268
	BOD-50

Cl-1240

TDS-3520

Fluoride-2.2
	Meeting Standards                  
	BOD-48

TDS-3040

Fluoride-2.2




    All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Issue reminder seeking bank guarantee and also issue SCN for removal of deficiencies observed during inspection.
Action taken/ Status after the meeting held on 11.01.2011:   

1. In compliance of CMC(MSW) decision a show cause notice regarding the removal of deficiencies observed during inspection and bank guarantee were issued to DSIIDC on 11.02.2011.

2. In response to our letter DSIIDC has submitted its point wise reply on 8.03.2011 is as follows:-

i) CETP is being operated upto tertiary level.

ii) For the rectification of flow meter, the concerned manufacturer has been asked to inspect the flow meter & to submit the estimate for the same.

iii) As the mechanical system for grit separation has become out of order, the grit is being collected manually as being done in other CETPs.

iv)  Earlier one of the equalization tank was being used as anaerobic tank and not as a storage tank for the treatment of BOD. Now both the equalization tank is being used and the agitator of tank no.1 has been made functional.

v) Non- functional Dosing pumps have been rectified.

vi) Fixed arrangement for dosing of alum, polyelectrolyte is already there. The HDPE Pipe Lines were provided as a temporary measure for dosing of chemicals as the dosing pumps were under maintenance.

vii) New system is being installed for dosing for prechlorination in PCT as the earlier system has been chocked and rectification of the same is not possible.

viii) Standby arrangement has been made for flash mixture pump house.

ix) No Comment.

x) The treated effluent is being discharged into the drain after passing through DMF & ACF.

xi) The Sludge is being dewatered through sludge thickener and vacuum filter & only the rinse water after the cleaning of sludge thickener and sludge holding tank is discharged sometimes into the drain.

xii) Regular cleaning of Flocculation Tank and tube settler is done as and when required.

xiii) Sludge record is being maintained.

xiv)  No comment.

xv) New display boards as per HWM rules have been installed as the earlier display boards were destroyed due to corrosion.

CETP was inspected by team of DPCC officials on 08.03.2011 the observations made are as under: 
· Flow meter installed near receiving chamber found not in operation.
· Cleaning is required in screens chamber.
· The grit removal arrangement found not in operation.
· A proper arrangement for collection of floating materials Scum from screens is required.
· Out of two equalization tanks one found in use and in other tanks cleaning is being done, but removed sludge from this tank has been placed around the equalization tank on ground. 
· The pump for dosing of bleaching are in under maintenance and no arrangement for pre- chlorination in PCT.
· There is not fixed pipe for polyelectrolyte dosing.
· Flow mixer found not in operation. There are three pumps in flash mixer pump house out of which is under maintenance.
· There are three pumps in equalization pump house out of which one is under maintenance.
· There are three pumps in clear water pumping station out of which one is under maintenance.
· Regular cleaning is required in flocculator and tube settler.
· There is a provision pass the effluent from tube settler to clean water tank without passing the effluent through DMF’s  & ACF’s.
· There is no proper are arrangement for solidification of sludge as vaccum durm filter unit is under maintenance.
· As reported there is no record of sludge.
· There are 9 DMF’s and 6ACF’s at present waste water is passing through a pair of 3 DMF’s and 2 ACF’s .  
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	January, 2011
	February, 2011

	Inlet
	Outlet
	Inlet
	Outlet

	Meeting Standards
	TDS-3180 
	Non Functional




          

	March, 2011
	April, 2011

	Inlet
	Outlet
	Inlet
	Outlet

	Meeting Standards
	Meeting Standards
	Meeting Standards
	BOD- 40

Fluroide-3.1


  All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated  10/06/2011:            

Call personal hearing before MS, DPCC.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Badli Industrial Estate CETP ( 12 MLD)

Consent status of CETP
· Renewal of Consent issued on 07.05.2010 and valid upto 29.11.2012 
· Renewal of authorization under HWM Rules issued on 08.10.2010 valid upto 08.10.2015
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue authorization (Renewal) under HWM Rules with the condition to submit fees for the same according to revised fee structure with in 15 days.

Action taken/ Status after the meeting held on 09.08.2010:

1. Renewal of authorization under HWM rules issued on 08.10.2010.

2. A letter issued for compliance of decision of  CMC(MSW) meeting on 06.09.2010
3. Besides above in compliance of CMC (MSW) decision a letter regarding Bank Guarantee was issued on 29.09.2010.
4. No reply received from the Society in response to our letter.
CETP was inspected by team of DPCC officials on 20.09.2010 and  07.12.2010 the observations made are as under:
· Flow meter at inlet found in operation. 

· pH at inlet is – 5.8
·  Significant amount of Sludge is observed in equalization tank, PST, Sludge thickener.

· There are two sludge holding tanks which are almost full with sludge; there is requirement of additional sludge holding tanks.

· As informed and also as per the reading shown by flow meter the average intake flow is 0.5 MLD due to much quantity of grit, silt etc in REPH, which maintained by DSIIDC.

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	September,2010
	October,2010

	Inlet
	Outlet
	Inlet
	Outlet

	pH-3.4

TSS-596

Pb-6.6
	Meeting Standards 
	TSS-2884

Cu-3.2

Cr(Total)-3.1

Oil & Grease-24.0
	Meeting Standards




             

	November, 2010
	December, 2010

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-2772
	Fluoride-3.4
	Meeting Standards
	Fluoride-2.8


All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Issue reminder seeking bank guarantee and also removal of deficiencies observed during inspection.
Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC(MSW) decision a letter regarding the submission of

     Bank guarantee and removal of deficiencies were issued on         09.02.2011.

2. In response to our letter  CETP has submitted a reply on 14th March 2011 alongwith a copy of earlier letter dated 1st June 2010 where in it is stating that  all the quarries raised by you has already been answered, however no comment w.r.t. Bank Guarantee. 

CETP was inspected by team of DPCC officials on 31.03.2011 and following observations made are as under:
· CETP found not in operation due to maintenance work carried out by DSIIDC in REPH. 
· Flow meter at inlet found not in operation. Meter reading: 482695 m3 /hr. 

     -   Significant amount of Sludge is observed in equalization tank, PST,           Sludge thickener therefore removal of sludge is required.

· There are two sludge holding tanks which are almost full with sludge; there is requirement of additional sludge holding tanks.

· Total intake flow in January 2011-15 ML, February 2011- 12 ML, March 2011- NIL, Total sludge stored at site- 358051 kg.

· Average intake flow is 0.5 MLD. As reported the CETP is not operational since 28th February due to maintenance work in REPH.

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	January,2011
	February,2011

	Inlet
	Outlet
	Inlet
	Outlet

	Meeting Standards


	TDS-2130
	Meeting Standards


	Meeting Standards



	February,2011
	                        April,2011

	Inlet
	Outlet
	Inlet
	Outlet

	Non functional
	Cu- 6.42

Cr(Total)- 4.10
	Fluoride- 2.8


All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated  10/06/2011:            

Issue reminder for submission of Bank Guarantee.

Ask the CETP Society to rectify the deficiencies.
Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

MAYAPURI CETP  (12 MLD)

Consent status of CETP
·  Renewal of consent to operate on issued on 10.09.2010 valid upto 05.05.2013.

· Renewal of authorization under HMW Rules on 09.09.2010 valid upto 08.09.2015.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue CTO (R) and renewal of authorization under HWM Rules. 

Action taken/ Status after the meeting held on 09.08.2010:

1. Consent to operate issued on 10.09.2010 valid upto 05.05.2013.
2. Renewal of authorization under HMW Rules on 09.09.2010 valid upto 08.09.2015.
3. Besides above in compliance of CMC (MSW) decision a letter regarding Bank Guarantee was issued on 23.09.2010.
4. A letter was received by CETP Society on 24.12.2010 regarding parameter analysis report for the period of Aug 10 to Dec 10. 
5. No reply received from the Society.
CETP was inspected by team of DPCC officials on 09.09.2010  and 23.12.2010 the  observations made are as under: 
· Flow meter installed after equalization pump house found in operation.

· There are two equalization tanks with three aerators in each tank out of which in one equalization tank one aerator found under maintenance.

· Cleaning is required in receiving chamber. 

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	September,2010
	October,2010

	Inlet
	Outlet
	Inlet
	Outlet

	Meeting Standards
	Meeting Standards (except TDS) 
	 TSS-572
	Meeting Standards




             

	November, 2010
	December, 2010

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-406

Cr(Total)-2.30
	Meeting Standards
	Meeting Standards            
	Sulphide-3.7


    All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Issue reminder seeking bank guarantee and also removal of deficiencies observed during inspection.
Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC (MSW) decision a letter was issued regarding bank guarantee and also removal of deficiencies observed during inspection.

2. In response to our letter CETP has submitted a reply on 08.03.2011.wherein it has reported all the discrepancies have been removed and requested to withdraw the imposed bank guarantee.
CETP was inspected by team of DPCC officials on 15.03.2011 the  observations made are as under: 
· Flow meter installed after equalization pump house found in operation on meter reading-6427254m3.

· There are two equalization tanks out of which in one tank cleaning work was going on.

· There are two vaccum drum filters out of which one drum filters out of which one drum filter cloth has turn of and needs to be change.

· Total intake in Jan-70.48 ML, Feb- 68.96 ML upto 14th March-35.3 ML.

· Average flow-2.75 MLD

· Total Sludge Stored- 175416 Kg. 

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	January,2011

	Inlet
	Inlet

	 Meeting Standards


	 Meeting Standards



	February,2011

	Inlet
	Inlet

	 Meeting Standards


	  Fluoride-2.1




	March, 2011
	April, 2011

	Inlet
	Outlet
	Inlet
	Outlet

	Meeting Standards


	Fluoride-2.1
	Oil &Grease- 22.4
	  Fluoride-2.4




     

        All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated  10/06/2011:           

Issue reminder for submission of Bank Guarantee.

Ask the CETP Society to rectify the deficiencies.
Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

MANGOL PURI CETP (2.4 MLD)

Consent status of CETP

· Consent to operate issued on 01.09.2010 and valid upto 28.06.2013

· Authorization under HMW Rules issued on 27.01.05 valid upto 26.01.07
· Not  applied for Authorization under HMW Rules.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue CTO (R) and put up file with in 30 days regarding applicability of authorization under HWM Rules, as the treatment scheme is biological. 

Action taken/ Status after the meeting held on 09.08.2010:

1. Consent to operate issued on 01.09.2010 and valid upto 28.06.2013.

2. In compliance with the CMC (MSW) meeting decision a letter regarding bank guarantee was issued on 29.09.2010.

3. in compliance with the CMC (MSW) meeting decision a letter was sent to CETP Society, on 26.11.2010 stating that according to HWM Rules, 2008 CETP has been mentioned  to generate hazardous waste irrespective of treatment scheme, so Society is requested to submit sludge analysis report from NABL accredited laboratory within 30 days of issuance of letter.

4. No reply has been received with respect to our letter dated 26.11.2010  

CETP was inspected by team of DPCC officials on 09.09.2010 and 16.12.2010 the observations made are as under: 
· Flow meter installed at Primary Clarifier found in operation.
· There are three pumps in REPS out of which one is found out of order.

· There are two equalization tanks with one floating aerator in each tank out of which in one tank one aerator found not in operation.

·  There are two pumps in equalization feed pump house out of which one pump found out of order

· There are two aeration tanks with two aerators in each tank, all are found in operation.

· No proper arrangement for sludge solidification. At present sludge from sludge thickener is being transferred to sludge storage area.
· There are two pumps in DMF feeding pump house out of which one found under maintenance.

· There are two pumps for clear water pumping out of which one found out of order.

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	September,2010
	October,2010

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-300
	Cl-2900 
	TSS-572
	Cl-3000

Fluoride-2.5




          

	November, 2010
	December,  2010

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-586
	Cl-1520

Fluoride-5.5
	Meeting standards          

	Cl-1680

TDS-8420


    All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Earlier decision ratified. Issue reminder seeking bank guarantee and submission of sludge analysis report from NABL accredited laboratory

and removal of deficiencies observed during inspection. 
Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC (MSW) decision a letter was issued regarding bank guarantee and submission of sludge analysis report from NABL accredited laboratory and also removal of deficiencies observed during inspection dated 09.02.2011.

2. In response to our letter CETP has submitted a reply on 30.03.2011.wherein it has reported all the discrepancies have been removed and now the plant is fully operational.
CETP was inspected by team of DPCC officials on 08.03.2011 the observations made are as under: 
· Flow meter installed at Primary Clarifier found in operation. Meter Reading -435773m3.

· There are three pumps in REPS, out of which two are under maintenance.

· There are two equalization tanks with one floating aerator in each tank out of which in one tank one aerator found under repair.

·  There are three pumps in DMF’S pump house out of which one is under maintenance.

· There are three pumps in ACF’S pumps house out of which one is under maintenance.

· There are three pumps in return sludge house out of which one is under maintenance.

· There is no proper arrangement for solidification of sludge. At present sludge in transfer to sludge storage shed from sludge thickner.

· There are two pumps in clear water pump house. Out of which one found out of order.

· Total intake in Jan-34.81 ML, Feb -34.07 ML and upto 5th March-7.5 ML

· Average flow-0.9 MLD.

· Total sludge stored-92980 Kg.
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-
	January,2011
	February,2011

	Inlet
	Outlet
	Inlet
	Outlet

	Meeting Standards
	Cl-2520

TDS-5290


	Meeting Standards
	Cl-3480

       TDS-8800




	March, 2011
	April, 2011

	Inlet
	Outlet
	Inlet
	Outlet

	Meeting Standards
	Cl-1530

TDS-4400

Fluoride-4.8


	Meeting Standards
	Cl-4060

TDS-7800


All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10/06/2011:              

Issue reminder for submission of Bank Guarantee.

Ask the CETP Society to rectify the deficiencies and submit test report of the sludge generated by the operation of the CETP as sought earlier.
Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Wazirpur Indl Area CETP ( 24 MLD)

Consent status of CETP
· Consent to operate issued on 01.09.2010 and valid upto 11.07.2013. 
· Renewal of authorization under HMW Rules issued on 03.03.11 and valid upto 02.03.16.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue CTO (R) and renewal of authorization under HWM Rules. 

Action taken/ Status after the meeting held  09.08.2010 on :

1. Consent to operate issued on 01.09.2010 valid upto 11.07.2013. Authorization could not be issued as CETP had not applied for authorization as per new fee structure in this regard the file was put up administratively. 
2. Besides above in compliance of CMC (MSW) decision a letter regarding Bank Guarantee was issued on 23.09.2010.

3. No reply received from the Society.

4. A copy of letter was received from Executive Engineer (NW) III, DJB regarding surcharging of sewer on a/c of non operation of sewage pumping station at Wazirpur Industrial Area.

5. A letter was sent to Sh. Sharat Kumar, Chief Project Manager, Wazirpur Industrial Area. Asking for submission of report for the reasons for the non-functioning of pumps and time required with a copy to Executive Engineer (NW) III, DJB on 3.12.2010.

6. In response to our letter Chief Project Manager, Wazirpur Industrial Area submitted that pumps and sluice gate of Raw Effluent Pumping station are getting frequently damaged because of low acidic waste water. They also mentioned that pumps are already repaired and in operation and sluice gate still is under repaired within 15 days.

7. CETP has applied for renewal of authorization with Fees. 

CETP was inspected by team of DPCC officials on 16.09.2010 and 07.12.2010, the observations made are as under: 
· Flow meter installed after REPS is under maintenance.

· Equalization tank was found almost filled with sludge during last inspection, the condition is still same. 

· Cleaning is required in REPS, receiving and grit chambers.

· As informed, the average intake is 0.87 MLD.

· There are two vacuum drum filters out of which one is under maintenance. 
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	September,2010
	October,2010

	Inlet
	Outlet
	Inlet
	Outlet

	pH-3

Ni-6.86

Cu-3.84
	 Cl-2100
	         pH-2.3

       Ni-7.70

Cu-4.22

Zn-22.6

Cr(Total)-82.6
	Meeting standards.




             

	November, 2010
	December, 2010

	Inlet
	Outlet
	Inlet
	Outlet

	pH-1.9

TSS-280

Ni-18.4

Cr(Total)-64.8
	TSS-102

Cr(Total)-3.2

Fluoride-3.2
	Ni-8.4

Cu-5.62

Zn-26.3    

Cr(Total)-71.5          
	TDS-2290


    All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011 : 

 Issue renewal of authorization.

        Issue reminder seeking bank guarantee and removal of    deficiencies              observed during inspection. 
Action taken/ Status after the meeting held  11.01.2011 on :

1. In compliance of CMC decision renewal of authorization under HMW Rules issued on 03.03.11 and valid upto 02.03.16.and a reminder seeking bank guarantee and removal of deficiencies observed was also issued.
2. No reply received from the Society.

CETP was inspected by team of DPCC officials on 07.03.11 the observations made are as under: 
· Flow meter installed after REPS is under repair/ maintenance.

· Equalization tank was found almost filled almost with sludge. 

· Cleaning is required in REPS, receiving and grit chambers.

· As informed, the average intake is 1.2 MLD.

· Out of two drum filters, one is still under maintenance.

· Total Intake flow in Jan-29.60 ML.

· Feb:- 34.95 ML upto 7.03.2011-7.4ML

· Total Sludge Stored at site-4508.09 MT.
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	January,2011
	February, 2011

	Inlet
	Outlet
	Inlet
	Outlet

	Ni-12.4

Cu-6.8

Cr-56.68


	TDS-4940

Cr-3.2
	BOD-90     

 Ni-9.2

Cu-5.8

Zn-24.2

Cr(Total)-68.2            
	TDS-3900

Fluoride-2.2




	March, 2011
	April, 2011

	Inlet
	Outlet
	Inlet
	Outlet

	Ni-8.6

Cu-7.4

Cr(Total)-64.8            
	TDS-3600


	Ni-10.4

Cu-6.8

Cr(Total)-76.2            
	TDS-3900




All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated  10/06/2011:         

Issue reminder for submission of Bank Guarantee.

Ask the CETP Society to rectify the deficiencies observed during two previous inspections.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell


DSIDC Nangloi & Udyog Nagar Indl Area CETP ( 12 MLD)

Consent status of CETP
· Consent to operate was issued on 01.09.2010 and valid upto 07.06.2013 
· Renewal of authorization under HWM Rules issued on 09.09.2010 and valid upto 08.09.2015
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue CTO and renewal of authorization under HWM Rules. 

Action taken/ Status after the meeting held on 09.08.2010:

1. Consent to operate issued on 01.09.2010 valid upto 11.07.2013.
2. Renewal of authorization under HMW Rules issued on 09.09.2010
3. Besides above in compliance of CMC (MSW) decision a letter regarding Bank Guarantee was issued on 23.09.2010.

4. In response to our letter dated 23.09.2010 CETP Society submitted a reply through a letter dated 08.10.2010, that they are not receiving any effluent reports since June, 2010 thus DPCC should not arrive at a conclusion of BG arbitrarily. They asked DPCC to send monthly reports regularly and also to keep the letter at abeyance till they receive effluent analysis reports. 

CETP was inspected by team of DPCC officials on 09.09.2010 and 2.12.2010 the observations made are as under: 
· There are two flow meters one is for Udyog Nagar and second one is for DSIIDC Shed, both are in operation.

· Cleaning is required in pre-chlorination tank.

· Cleaning is also required in final outlet tank.

· Filter cloth of one drum filter has not been replaced so far.

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	September,2010
	October,2010

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-574

Cr(Total)-2.1
	Meeting Standards 
	      TSS-1120
	Cl-2000




             

	November, 2010
	December, 2010

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-1128
	Fluoride-2.2
	Meeting standards
	Cl-1130

TDS-5170


    All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of 

MSW Cell dated 11.01.2011 :

Issue reminder seeking bank guarantee and removal of deficiencies observed during inspection. 
Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC (MSW) decision a letter was issued regarding bank guarantee and also removal of deficiencies observed during inspection dated 09.02.2011.

2. In response to our letter CETP has submitted a reply on 18.02.2011 wherein it is stating that TSS parameters of effluent and the inlet of the CETP plant are beyond our control as inlet of CETP is connected DJB conveyance system and it shall be in better position to explain about TSS beyond the prescribed range and all the deficiencies have been rectified. In regard to bank guarantee he has mentioned that the analysis reports of samples collected by DPCC lab are not being sent since July 2010 onwards in absence of reports, we are not in a position to asses the performance of the plant and thus, your arbitrary decision of submitting a bank guarantee of Rs 1 lakh is baseless.
CETP was inspected by team of DPCC officials on 08.03.2011 the observations made are as under: 
· There are two flow meters one for Udyog Nagar and another for DSIIDC Nagloi shed:

·  Meter Reading of Udyog Nagar- 2172638 m3/day
Meter Reading of DSIIDC- 1031818 m3/day.

· There are three chambers with chain & scraper system for grit removal. Out of which one is under maintenance.

· There are three pumps in flash mixer pump house out of which one is under maintenance.

· Total intake in the month Jan-36.191, Feb-54.364 ML and upto 8.03.2011—14.287ML. 

Average flow -1.94 MLD

Total Sludge-153733 kg
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

        

	January ,2011
	February ,2011

	Inlet
	Outlet
	Inlet
	Outlet

	         Meeting standards.


	Cl-1330

TDS-2460


	         Meeting standards.


	Cl-1780

TDS-4800




	March, 2011
	April, 2011

	Inlet
	Outlet
	Inlet
	Outlet

	     Meeting standards             
	Cl-1330

TDS-2460

Fluoride-3.7

Sulphide-6.8


	Meeting Standards
	Cl-2810

TDS-4300




    All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10/06/2010:

Issue reminder for submission of Bank Guarantee.

Ask the CETP Society to rectify the deficiencies.
Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

SMA Indl Area CETP ( 12 MLD)
Consent status of CETP
· Consent to operate issued on 07.09.2010 and valid upto 01.07.2013.

· Renewal of authorization under HWM Rules issued on 09.09.2010 valid upto 08.09.2015
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated  09.08.2010:

Issue CTO ® and renewal of authorization under HWM Rules , subject to  condition that the BOD level is within limit . 

Action taken/ Status after the meeting held on 09.08.2010:

1. Consent to operate issued on 07.09.2010 and valid upto 01.07.2013.
2. Renewal of authorization under HMW Rules issued on 09.09.2010 and valid upto 08.09.2015
3. Besides above in compliance of CMC (MSW) decision a letter regarding Bank Guarantee was issued on 23.09.2010.
4. No reply received from the Society.
CETP was inspected by team of DPCC officials on 10.09.2010 and 31.12.2010 observations made are as under: 
-     Flow meter installed at REPS. Meter Reading is

· Cleaning is required in screens of grit chambers.

· Significant amount of grit/sludge is observed in equalization tanks.

· Cleaning is required in Tube settler

· There are two vacuum drum filters out of which one is under maintenance. 
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	September,2010
	October,2010

	Inlet
	Outlet
	Inlet
	Outlet

	Cr(Total)-2.4
	Meeting Standards except TDS 
	TSS-1420

Cr(Total)-3.53
	Fluoride-2.8




             

	November, 2010
	December, 2010

	Inlet
	Outlet
	Inlet
	Outlet

	pH-2.7

Ni-6.8

Cu-9.0

Cr(Total)-23.8
	Fluoride-3.7
	Non-functional


    All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Issue reminder seeking bank guarantee and removal of deficiencies observed during inspection. 

Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC(MSW) decision a reminder seeking bank guarantee and removal of deficiencies observed was issued on 09.02.2011.
2. No reply has been received. 

CETP was inspected by team of DPCC officials on 28.02.2011 observations made are as under: 
· Flow meter installed at REPS. Meter Reading is-2538339m3
· Removal of sludge is required in equalization tanks.

· Cleaning is required in final holding tank.

· Total intake in Jan-46.901 ML,Feb- 42.260ML,Average Flow-1.406 ML,Total Sludge Stored -1238.5 MT

· pH at inlet of CETP-4.8. 
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-        

	January ,2011
	February ,2011

	Inlet
	Outlet
	Inlet
	Outlet

	        Ni-8.8

Cu-6.64 

Cr(Total)-26.2


	TDS-2420


	Cr (Total)-4.9


	Cl-1030

TDS-5600

Sulphide-3.0




All Values are in mg/l expect pH
	March, 2011
	April, 2011

	Inlet
	Outlet
	Inlet
	Outlet

	     Ni-10.4

Cu-8.7

Cr. (Total)-32.4

             
	TDS-2700

Fluoride-3.7


	Ni-3.42
	Cl-1130

TDS-3400      




Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10/06/2011:

Issue reminder for submission of Bank Guarantee.

Ask the CETP Society to rectify the deficiencies.
Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

                                         Okhla CETP  (24 MLD)

Consent status of CETP

· Consent to operate issued on 15.09.2004 and valid up 27.07.07. 
· Applied for renewal of consent on 13-02-07.
· Not applied for renewal of consent.
· Not applied for renewal of authorization under HMW Rules. 
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue reminder for renewal of 

consent under Air and Water Acts and Authorization under HWM Rules, within 1 month.

Action taken/ Status after the meeting held on 09.08.2010:

1. Reminder Letter Issued for renewal of Consent to Operate (Renewal) under Air and Water Acts and authorization under HWM Rules, within 1 month on 06.09.2010.

2.  Besides above in compliance of CMC (MSW) decision a letter regarding Bank Guarantee was issued on 29.09.2010.
3. A letter was received by Okhla CETP Society on 29.09.2010 in which they mentioned that they are taking an action to apply for authorization under HWM Rules.
CETP was inspected by team of DPCC officials on 30.09.2010 and 30.12.2010 the observations made are as under:
· No effluent is being received  from Phase-I Okhla, since mid of August 2010, as informed
· There are two flow meters for measuring flow received from REPH-I and REPH-II but without totaliser.

· There are two equalization tanks with two aerators in each tank. However in equalization tank no-I aerators are under maintenance.

· The tube settler consisting of four parts out of which one part is under maintenance. Also fencing is required around the tube settler.

· The treated waste water is being passed through DMFs only.
· There are two flocculators, both are found operational. 
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	September,2010
	October,2010

	Inlet
	Outlet
	Inlet
	Outlet

	Meeting Standards
	BOD-36

Sulphide-3.2 
	TSS-268
	BOD-36

Sulphide-3.2




             

	November, 2010
	December, 2010

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-818
	TSS-166

BOD-37
	Meeting Standards
	BOD-37

Sulphide-3.2




    All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit to submit application under air and water act with requisite consent fee as well as application for authorization under HWM Rules. Issue reminder seeking bank guarantee and removal of deficiencies observed during inspection. 
Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC decision a letter for submission of application under air and water act with requisite consent fee as well as application for authorization under HWM Rules as well as for reminder for seeking bank guarantee and removal of deficiencies observed during inspection were issued on 9.02.2011.

2. No reply has been received till date.

 CETP was inspected by team of DPCC officials on 14.03.2011 and  observations made are as under: 
· No effluent is being received  from Phase-I Okhla, since mid of August 2010, as informed
· There are two flow meters without totaliser. Out of three one for equalization pump house found out of order. 
· The tube settler consisting of four parts out of which one part is out of order Also fencing is required around the tube settler.
· Vaccum drum filter section is almost corroded hence a suitable arrangement for solidification of sludge is required.
· The treated waste water is being passed through DMFs only.
· Total intake in Jan-25 ML,Feb- 33.06ML,upto 14th March-16.06 ML

          Average Flow-1 ML,Total Sludge Stored -30710 MT.

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	January,2011
	February,2011

	Inlet
	Outlet
	Inlet
	Outlet

	Non-Functional 
	Meeting Standards
	         BOD-35

Sulphide-3.5

TDS-2800




             

	March, 2011
	April, 2011

	Inlet
	Outlet
	Inlet
	Outlet

	Meeting Standards
	TSS-3100

BOD-42

Fluoride-3.3

Sulphide-8.8
	Non- Functional


    All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10/06/2011 :

 Call the CETP Society for personal hearing as the Society has failed to apply for CTO( R).

Issue reminder to MoEF, GOI seeking clarification regarding the sludge generated by the CETP.

Call a meeting of officers of DSIIDC to discuss issue of REPS operation and maintenance.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

NARELA CETP (22  MLD)

Consent status of CETP

· Consent to establish granted on 20.01.04 for a period one year. 
· Applied for consent to operate on 03.03.06. 
· Not applied for Renewal of Consent.
· Not applied for authorization under HMW Rules. 
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Issue letter seeking application for renewal of consent under Air and Water Acts and Authorization under HWM Rules, within 1 month to Narela CETP Society .

Action taken/ Status after the meeting held on 09.08.2010 :

1. Reminder Letter Issued to Narela CETP Society for renewal of Consent to Operate (Renewal) under Air and Water Acts and authorization under HWM Rules, within 1 month on 03.09.2010.

2.  Besides above in compliance of CMC (MSW) decision a letter regarding Bank Guarantee was issued on 29.09.2010.

3. No reply received from the Society.

CETP was inspected by team of DPCC officials on 14.09.2010 and 28.12.2010the observations made are as under: 
· Flow meter installed near REPS is found not in operation.

· There are 5 pumps in REPS out of which 4 are in operation.

· A proper arrangement is required for disposal of silt/floating material near screen chamber.

· There is no arrangement for removal oil and grease.

· There are two grit/silt removal tanks with one scraper and silt removal arrangement in each tank but these are not functioning in both tanks.

· The blowers (2 Nos) for aeration tank in equalization tank are not functioning.

· Significant amount of silt/grit observed in equalization tank.

· There are two flash mixer out of which one found in operation

· There are two flocculation tanks with two scrappers/agitators both are not in operation.

· Cleaning is required in tube settler. Also proper arrangement of weir is required.

· Significant amount of sludge is observed in aeration tanks.

· There are 3 pumps in primary clarifier pumping station out of which one found not in operation.

· There is no proper arrangement for sludge removal from tube settler and clarifier.

· The treated waste water is not being passed through DMFs and ACFs at present it is being by passed and directly discharged to post chlorination tank.

· There is no arrangement for post chlorination

· There are 8 tanks in one side and 6 tanks at another side for chemical mixing out of which only 2 tanks for alum mixing and 2 tanks for poly electrolyte are being used.

· All the (16nos) sludge drying beds have fully occupied and open to sky. Hence an alternative arrangement is required.

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	September,2010
	October,2010

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-1160

Cr(Total)-2.7
	TSS-196

BOD-48
	Meeting Standards
	 BOD-38

Cl-1049

Fluoride-2.81


             

	November, 2010
	December, 2010

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-548
	TSS-232

BOD-45

Fluoride-2.1
	Meeting Standards
	BOD-41

Fluoride-2.3


    All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit to submit application under air and water act with requisite consent fee as well as application for authorization under HWM Rules. Issue reminder seeking bank guarantee and removal of deficiencies observed during inspection. 
A reminder seeking bank guarantee and removal of deficiencies observed was issued on 09.02.2011.
Action taken/ Status after the meeting held on 11.01.2011 :

1. In compliance of CMC(MSW) decision a reminder seeking Bank Guarantee and asking the unit to submit application under air and water act with requisite consent fee as well as application for authorization under HWM Rules was issued on 09.02.2011.

2. No reply received from the Society.

CETP was inspected by team of DPCC officials on 07.03.2011 the observations made are as under: 
-Flow meter installed near REPS was not found in operation.

- Out of five pumps in REPS only four are in operation.

-An arrangement for collection/ Storage of silt/ floating material near screen      chamber is required.

-There are two silt/ grit removal tanks with one Scrappers and one silt removal arrangement in each tank, but these systems found not in operation in both tanks.

- Out of two flocculation tanks with two scrappers but both are not in    operation. 

   Out of two blowers for aeration only one was in operation.

-Out of three pumps in primary clarifier pumping station, two are   operational.

- The treated waste water was not being passed through DMF’s amd ACF’s    and also being discharged without post chlorination. 

- There are 8 tanks in Chemical mixing chamber out of which two tanks for    alum mixing and two tanks for poly electrolyte are in use. 

Total water in tank in Jan 294 ML, Feb 290 ML upto 07.03.2011 – 19.5 ML Average-9.5 MLD. Total Sludge -16 X 400m3=6400 m3                                             

- All the (16nos) sludge drying beds have been fully occupied. An alternative arrangement for sludge disposal is required.

-Sludge is observed in equalization, aeration tank therefore cleaning is required.

-Proper weir plate arrangement is required in tube settler.   

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-   

	March, 2011
	April, 2011

	Inlet
	Outlet
	Inlet
	Outlet

	Meeting Standards
	Fluoride-2.9


	Meeting Standards
	BOD- 38      




           
	January ,2011
	February ,2011

	Inlet
	Outlet
	Inlet
	Outlet

	Meeting Standards
	Sulphide-5.9  
	Meeting Standards
	Meeting Standards


All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10/06/2011 :

Issue reminder for submission of Bank Guarantee, application for consent under Water and Air acts and authorization under HWM Rules.

Ask the CETP Society to rectify the deficiencies.
Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Udyog Vihar (Bawana) Industrial Area CETP ( 35 MLD)

Consent status of CETP
· Applied for Consent to Establish on 05.08.02. Consent to Establish was granted on 20.01.2004 for a period of one year.
· DSIIDC has submitted an incomplete application for consent to operate without consent fee by speed post on 04.05.2010. 
· DSIIDC has submitted an application for authorization under HWM Rules without consent fee by speed post on 18.05.2011. 

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Put up issue of revised consent fees, wrt CETPs and STPs, in next DPCC meeting. Issue letter to DSIIDC seeking all the documents missing while submitting earlier application.

Action taken/ Status after the meeting held on 09.08.2010:

1. Letter Issued to DSIIDC seeking all the documents missing while submitting earlier application on 03.09.2010 .

2. Besides above in compliance of CMC (MSW) decision a letter regarding Bank Guarantee was issued on 15.10.2010.

3. A letter regarding incomplete application for consent to operate was issued to Chief Project Manager on 14.09.2010

4. A letter in response to our above mentioned letter was received on 22.12.2010 in which it was submitted that Bawana plant is itself a CETP unit to treat industrial effluent generated from Bawana Industrial Area. Therefore, all capital investment on the plant is towards Pollution Control equipment which is exempted for payment of fee for consent to operate.

5. Issue of fees was discussed in DPCC meeting held on 22.12.2010 and it was decided to seek clarification from WBSPCB.

6. DSIIDC has not submitted any reply regarding submission of Bank Guarantee.

7. A Letter in response to our letter regarding consent to operate under the water Act, 1974 and Air act is received from DSIIDC on 7.4.2011.
CETP was inspected by team of DPCC officials on 13.09.2010 and 28.12.2010 the observations made are as under:
· There are three flow meters at intake out of which two are operational

      but all are not functioning.

· Cleaning is required in stilling chamber, oil & grease chamber, grit chamber. 

· Oil skimmers are not functioning.
· There are two rack classifier attached with grit chamber out of which one is functional.

· There are two aeration tanks with 9 aerators in each tank, out of which 7 aerators are functioning and two are not functioning.

· The centrifugal system for solidification of sludge is under trail.

· The units after secondary settling tank like chemical house, tube settler, gravity sand filter are under trial.

· No dosing of Alum, Poly electrolyte observed.

· As informed at present post chlorination is being done.

· There are four pumps in equalization pumping stations out of which one found not in operation. 

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:
Ask the unit to deposit required consent fee for consent under air and water act as well as application for authorization under HWM Rules and to rectify the deficiencies observed during inspection. Also, Issue reminder seeking bank guarantee.  

Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC (MSW) decision a letter regarding Bank Guarantee and for deposit required consent fee for consent under air and water act was issued on 03.03.2011.

2. In response to our letter DSIIDC has submitted its reply on 08.03.2011 in which it has reported that deficiencies have been rectified and matter regarding payment is being taken up with higher up. Further it has requested to waive off consent fee as CETP is itself a waste water pollution control system and also for bank guarantee as DSIIDC is a government undertaking ​​​​​​​​​​​​​​​​​​.

3. Further DSIIDC has submitted a letter regarding waiving off consent fee as CETP is itself a waste water pollution control system and also for bank guarantee as DSIIDC is a government undertaking ​​​​​​​​​​​​​​​​​​on 07.04.2011.

CETP was inspected by team of DPCC officials on 31.03.2011 :

· There are three flow meters at intake out of which one is found out of order.

· Meter Reading of IInd meter-98603m3. 
· Meter Reading of IIIrd meter-445068m3.
· Oil skimmers are not functioning. 
· There are two rack classifier attached to grit chamber out of which one found non-operational. Also a proper arrangement for silt storage is required.

· There are two equalization tanks with four agitator float mixtures in each tanks, both tanks are being used, but one agitator found non operational. 

· There are four pumps in equalization pump house stations out of which one is found non-operational.

· There is an arrangement of primary dosing with a provision of agitator near primary sediment action tanks, but it is not in use.

· There are two aeration tanks with 9 aerators in each tank, both are in use, but in one tank 5 aerators are not functioning.

· At present treated waste water from secondary sediment in tank is being directive discharged to drain, without adding chemicals and passing through tube settler, saved filter etc.

· There are two thinker, both are in use, but scraper of one thickener is not functioning.

· No record of sludge is available at site.

· There is an arrangement for polyelectrolyte dosing in sludge thickener and   centrifugal inlet, but not in practice at present.    

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-        

All Values are in mg/l expect pH
	April, 2011
	May, 2011

	Inlet
	Outlet
	Inlet
	Outlet

	Cu-3.24


	Cl-1520

TDS-5200
	Result awaited


Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated  10/06/2011:
Call DSIIDC officer(s) for personal hearing before MS, DPCC.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Najafgarh Road Industrial area, CETP ( 9.6 MLD)
Consent status of CETP
· DSIDC has submitted a letter dated 03.08.2007 in respect of DO letter 17.07.2007, that the EPCA has already directed not to go for further construction in view of spare capacity in other functional CETPs. As regards settling the dispute with the contractor, DSIDC looking into it as per the terms of the contract separately.

· DSIDC applied for Consent to Establish on 03-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

Report was examined by Dr. B.K Guha Committee and recommended that this area should have separate CETP, since there is no surplus capacity in the CETP in the nearby vicinity.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
Wait for study report.

Action taken/ Status after the meeting held on 09.08.2010:

No communication has been received so far regarding study report.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011 :

Seek ATR from DSIIDC and COI on the study assigned to Sri Ram Institute of Industrial Research Institute regarding the CETP.

Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC (MSW) meeting a letter for seeking ATR from DSIIDC and COI on the study assigned to Sri Ram Institute of Industrial Research Institute regarding the CETP on 09.02.2011.

2. No reply has been received till date.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10/06/2011:

Call DSIIDC officer(s) for personal hearing before MS, DPCC.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Naraina Industrial Area, CETP ( 21.6 MLD)

Consent status of CETP
· DSIDC applied for Consent to Establish on 02-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

·  EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and it was appraised by the representative of DSIDC that CETP is under installation and it is at final stage of construction and after commissioning of the same may be handed over to CETP Society of the area. 
· CETP has submitted an incomplete application for consent to operate without consent fee by speed post on 04.05.2010. 

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
Put up issue of revised consent fees, wrt CETPs and STPs, in next DPCC meeting. Issue letter to DSIIDC seeking all the documents missing while submitting earlier application. Also, ask DSIIDC for rectification of deficiencies observed during the inspection.

Action taken/ Status after the meeting held on 09.08.2010:

1. Letter Issued to DSIIDC seeking all the documents missing while submitting earlier application on 14.09.2010.

2.  Besides above in compliance of CMC (MSW) decision a letter regarding Bank Guarantee was issued on 15.10.2010.
3. In response to our letter dated 14.09.2010, the Society submitted that all the deficiencies mentioned had already been removed and since Naraina plant is itself a CETP unit, therefore all capital investment on the plant is towards Pollution Control equipment which is exempted for payment of fee for consent to operate.

4. DSIIDC has not submitted any reply regarding submission of Bank Guarantee.
CETP was inspected by team of DPCC officials on 20.09.2010 and 30.12.2010 the observations made are as under:
· Flow meter installed in effluent transfer pump house found in operation. 
· During inspection all the units of CETP found not in operation. Also it appears that it is not being operated since few days.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011 :
Ask the unit to deposit required consent fee for consent under air and water act as well as application for authorization under HWM Rules and issue SCN for non operation of CETP. Issue reminder seeking bank guarantee. 
Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance to CMC decision a letter dated 10.02.2011 asking unit to deposit required consent fee for consent under air and water act as well as application for authorization under HWM Rules and  SCN for non operation of CETP. A reminder seeking bank guarantee is also issued.

2. In response to our letter DSIIDC has submitted its reply on 04.03.2011 in which it has reported that at the time of inspection CETP was not in operation as some of the equipments were under routine maintenance and operating agency have also been directed to ensure the continuous operation of all the units and now CETP is being operated continuously, regarding consent fee the issue is being taken up with higher up. however he has requested to waive off consent fee as CETP is itself a waste water pollution control system and also for bank guarantee as DSIIDC is a government undertaking ​​​​​​​​​​​​​​​​​​.

3. Further DSIIDC has submitted a letter regarding exemption for depositing of consent fee as CETP is itself a waste water pollution control unit and also for exemption for depositing bank guarantee as DSIIDC is a government undertaking ​​​​​​​​​​​​​​​​​​on 07.04.2011.

CETP was inspected by team of DPCC officials on 15.03.2011  the observations made are as under:
· The CETP found not in operation. 

· The condition of equalization tanks, flash, Vaccum drum filter. Clear water holding tank etc shows that plant is not being operating since long.  
· Effluent transfer pump house, but it is not showing any reading. As per record that last reading of 14.03.2011 is -1555140m3 
Average intake- 4.5MLD

Total sludge stored-792271kg

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-        

	April, 2011
	May, 2011

	Inlet
	Outlet
	Inlet
	Outlet

	Cr-2.32


	BOD-38

Sulphide-3.5
	Result awaited


All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated  10/06/2011:
Ask the CETP Society to apply for consent and rectify the deficiencies.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Okhla Industrial Estate CETP ( 1.2 MLD)
Consent status of CETP
· DSIDC applied for Consent to Establish on 06-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

     Report was examined by Dr. B.K Guha Committee and recommended      that an independent CETP may be installed for this industrial area
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

No Action

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:
No action.

 Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated  10/06/2011:
No action.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

Anand Parbat CETP ( 24 MLD)

Consent status of CETP
· DSIDC applied for Consent to Establish on 05.08.02.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP. 

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and recommended that an independent CETP may be installed for this industrial area.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
No Action
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:
No action.

 Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10/06/2011:
No action.

Chairman  M. S.
  Member    Prof. S.K Gupta          AD         SEE      EE    
DPCC      DPCC    Env. Deptt. Member(Acd. Inst)   (MSW)    MSW Cell

                                                   Annexure- 4                                                                                                                                                                                                                                                         
Badarpur Thermal Power Station
Status of Consent: 

Consent issued on 11-05-2010  valid up to 16-02-2013.

Renewal of authorization under HWM Rules issued on 06.09.2010 and valid upto 05.09.2015.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
Issue renewal of authorization under HWM Rules.
Action taken/ Status after the meeting held on 09.08.2010:
1. Renewal of authorization under HWM Rules is issued on 06.09.2010 and valid upto 05.09.2015.

2. DPCC  Monitoring results for the months of September, October, November and December 2010 are as under:
	S.No.


	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter*
	Sulphur Dioxide
	NOx**

	
	
	Sep. 10
	Oct.10
	Sep. 10
	Oct. 10
	Sep.  10
	Oct.

10

	1.
	Duct of unit no. 1A
	58
	#
	383
	#
	158
	#

	2.
	Duct of unit no. 1B
	62
	61
	373
	328
	158
	112

	3.
	Duct of unit no. 2A
	135
	59
	362
	416
	239
	104

	4.
	Duct of unit no. 2B
	128
	58
	394
	384
	239
	104

	5.
	Duct of unit no. 3A
	81
	60
	309
	288
	230
	153

	6.
	Duct of unit no. 3B
	192
	63
	346
	280
	230
	153

	7.
	Duct of unit no. 4A
	93
	#
	453
	#
	109
	#

	8.
	Duct of unit no. 4B
	71
	#
	479
	#
	109
	#

	9.
	Duct of unit no. 5A
	#
	69
	#
	380
	#
	194

	10.
	Duct of unit no. 5B
	#
	59
	#
	392
	#
	194


# Shut Down/ Under Maintenance

* Normalized at 12% CO2

** Normalized at 6% O2

	S.No.


	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter*
	Sulphur Dioxide
	NOx**

	
	
	Nov. 10
	Dec. 10
	Nov 10
	Dec. 10
	Nov. 10
	Dec. 10

	1.
	Duct of unit no. 1A
	#
	108
	#
	304
	#
	128

	2.
	Duct of unit no. 1B
	#
	85
	#
	280
	#
	128

	3.
	Duct of unit no. 2A
	#
	75
	#
	320
	#
	149

	4.
	Duct of unit no. 2B
	#
	86
	#
	328
	#
	149

	5.
	Duct of unit no. 3A
	104
	78
	312
	312
	160
	146

	6.
	Duct of unit no. 3B
	98
	80
	304
	324
	160
	146

	7.
	Duct of unit no. 4A
	104
	117
	400
	400
	186
	94

	8.
	Duct of unit no. 4B
	91
	99
	380
	432
	186
	94

	9.
	Duct of unit no. 5A
	68
	101
	328
	448
	138
	123

	10.
	Duct of unit no. 5B
	55
	85
	336
	480
	138
	126


3. DPCC Monitoring reports for waste water quality from Ash Pond for the month of September, October and November  2010 is as under:

                                                  September 2010

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	STP
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature 
	0.50
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	07.09.2010
	7.8
	14
	0.4
	7.1
	9.5
	Nil 
	7.5
	16
	1.6
	10
	32
	--


                                                  October 2010

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	STP
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature 
	0.50
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	21.10.2010
	7.9
	20
	0.4
	7.7
	8.5
	Nil 
	   7.9
	24
	1.2
	10
	50
	--


                                                  November 2010

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	STP
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature 
	0.50
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	24.11.2010
	8.2
	18
	<1.0
	7.6
	8.8
	Nil 
	   7.9
	26
	1.2
	18
	72
	--


4. Monthly monitoring reports of NTPC limited of August, September, October 2010 was received on and, 22.09.2010, 18.10.2010, 20.11.2020 respectively.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit to submit the status report for achieving the SPM level of 50 mg/Nm3 on the basis of action plan submitted by the unit.
Action taken/ Status after the meeting held on 11.01.2011:
1. In compliance of CMC decision a letter was issued on 28.01.2011.

2. Reply received on 04.03.2011 with following information:

a. To achieve the target of SPM as <50 mg/Nm3, retrofitting of additional     fields will be done under R &M scheme with an estimated cost of Rs. 57     Crores. This work is in the process of award.

b. Regarding Stage-I units, DTL & CERC have directed for a minimum     expenditure on these units as these units will be phased out after installation     & commissioning of Badarpur CCPP, Stage-III, phase- I ( 1050 MW) gas-     based plant.

   To keep these ESPs of Stage-I (3X95 MW) units in healthy condition    and        to meet the statutory limit of SPM on sustainable basis, the old ESP       controllers of these units will be replaced by latest microprocessor based    Controllers. The Contract for work awarded on 26.02.2011.
3. DPCC Monitoring results for the months of January, February, March & April           2011 are as under:
	S.No.


	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter*
	Sulphur Dioxide
	NOx**

	
	
	Jan. 11
	Feb. 11
	Jan. 11
	Feb. 11
	Jan. 11
	Feb. 11

	1.
	Duct of unit no. 1A
	73
	69
	288
	280
	138
	128

	2.
	Duct of unit no. 1B
	107
	51
	280
	260
	138
	128

	3.
	Duct of unit no. 2A
	81
	102
	320
	320
	130
	98

	4.
	Duct of unit no. 2B
	87
	106
	332
	288
	130
	98

	5.
	Duct of unit no. 3A
	103
	101
	336
	360
	150
	148

	6.
	Duct of unit no. 3B
	81
	164
	344
	288
	150
	148

	7.
	Duct of unit no. 4A
	63
	69
	360
	312
	169
	191

	8.
	Duct of unit no. 4B
	72
	73
	380
	320
	169
	191

	9.
	Duct of unit no. 5A
	82
	48
	368
	328
	158
	219

	10.
	Duct of unit no. 5B
	79
	73
	400
	340
	158
	219


Standard of particulate matter- 150 mg/Nm3 
# Shut Down/ Under Maintenance

* Normalized at 12% CO2

** Normalized at 6% O2

	S.No.


	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter*
	Sulphur Dioxide
	NOx**

	
	
	Mar. 11
	Apr.11
	Mar. 11
	Apr.11
	Mar. 11
	Apr.11

	1.
	Duct of unit no. 1A
	79
	84
	348
	328
	187
	152

	2.
	Duct of unit no. 1B
	62
	77
	320
	352
	187
	152

	3.
	Duct of unit no. 2A
	52
	73
	371
	460
	188
	151

	4.
	Duct of unit no. 2B
	60
	98
	384
	448
	188
	151

	5.
	Duct of unit no. 3A
	88
	105
	360
	328
	182
	160

	6.
	Duct of unit no. 3B
	87
	71
	340
	368
	182
	160

	7.
	Duct of unit no. 4A
	100
	97
	292
	392
	211
	168

	8.
	Duct of unit no. 4B
	104
	111
	324
	404
	211
	168

	9.
	Duct of unit no. 5A
	78
	95
	360
	412
	164
	162

	10.
	Duct of unit no. 5B
	110
	82
	348
	420
	164
	162


2. DPCC Monitoring reports for waste water quality from Ash Pond for the month of December2010, January, February, March, April and May 2011 is as under:

                                                  December 2010

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	STP
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature 
	0.50
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	24.12.2010
	7.7
	-
	1.2
	7.4
	9.5
	Nil 
	7.9
	-
	1.2
	20
	64
	--

	28.01.2011
	8.0
	-
	1.2
	7.4
	9.2
	Nil 
	8.0
	-
	1.6
	23
	96
	--

	18.02.2011
	7.4
	-
	1.2
	7.7
	10.0
	Nil 
	   7.2
	-
	1.6
	22
	72
	--

	29.03.2011
	7.5
	14
	ND
	7.8
	9.5
	Nil 
	   7.4
	 32
	1.2
	17
	72
	--

	27.04.2011
	7.2
	--
	1.6
	7.0
	9.0
	Nil 
	   7.6
	 --
	1.2
	19
	92
	--

	27.05.2011
	8.1
	14
	1.2
	7.7
	9.2
	Nil 
	   7.6
	 18
	1.6
	18
	80
	--


3. Monthly monitoring reports of NTPC limited of November, December 2010, & January February and April 2011 was received on and, 11-12-2010, 21.01.2011, 18.02.2011& 28.02.2011, 14.03.2011 & 23.05.2011 respectively.
4. PM emission levels in one of the ducts exceeds the limit of 150 mg/Nm3.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:
 Issue letter seeking progress report on PM emission control below 50 mg/Nm3 
Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell
Rajghat Power Station

Status of Consent: Renewal of Consent to Operate issued on 08.02.2010 valid upto 16.04.2012.  
Applied for authorization under HWM Rules on 19.10.2010
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Seek present status regarding progress in action taken to comply with the norm of 50mg/Nm3 w.r.t Particulate Matter. Also ask a revised application under HWM Rules 1989, amended to date.
Action taken/ Status after the meeting held on 09.08.2010:
1. In compliance to CMC decision a letter has been issue by DPCC on 
        06-09-2010. 
2.   The Unit has not submitted any present status to comply with DPCC norms 
3.   Annual Environment Statement for the year 2009-2010 received on        18.08.2010 in respect of Rajghat Power House.
4. Environmental status/ Pollution measures report for the month of August, September, October and November 2010 in regard to RPH received on 22.09.2010, 21.10.2010, 23.11.2010 and 22.12.2010.
5. Show Cause Notice for closure u/s 31 (A) of the Air (Prevention & Control of Pollution) Act, 1981 as amended to date was issued on 12.10.2010.
6. A letter was received on 27.10.2010 from M/s Rajghat Thermal Power Plant in reply of show cause notice regarding reduction of stack emission to meet DPCC norms.
7. A letter was received on 24.11.2010 from M/s Rajghat Thermal Power Plant regarding performance of ESPs at Rajghat Power House wherein it has been mentioned about the early retirement of Rajghat Power House.
8. A letter has been issued on 04.01.2011 to provide the specific time frame for the same.
9. DPCC Monitoring results for the months of August, September, October  2010 are as under:
	
S.No.


	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	
	
	Sep 10
	Oct10
	Sep 10
	Oct 10
	Sep 10
	Oct 10

	1.
	Duct of unit no. IA
	      #
	198
	      #
	336
	      #
	141

	2.
	Duct of unit no. IB
	#
	185
	#
	320
	#
	141

	3.
	Duct of unit no.IIA
	198
	134
	330
	300
	153
	116

	4.
	Duct of unit no. IIB
	183
	129
	341
	280
	153
	116


	
S.

No.


	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	
	
	Nov 10
	Dec 10
	Nov 10
	Dec 10
	Nov 10
	Dec 10

	1.
	Duct of unit no. IA
	#
	184
	#
	408
	#
	102

	2.
	Duct of unit no. IB
	#
	205
	#
	384
	#
	102

	3.
	Duct of unit no.IIA
	111
	111
	297
	360
	136
	130

	4.
	Duct of unit no. IIB
	87
	128
	274
	392
	136
	130


9.  DPCC Monitoring reports for waste water quality from Ash Pond for the month of September, October, November 2010 is as under: 

September 2010

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	STP
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature 
	0.50
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	30.08.2010
	7.6
	34
	1.6
	--
	--
	--
	--
	--
	--
	--
	--
	


October 2010

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	STP
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature 
	0.50
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	27.10.2010
	7.5
	24
	0.4
	--
	         --
	--
	--
	--
	--
	--
	--
	--


                                                  November 2010

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	STP
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature 
	0.50
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	19.11.2010
	7.5
	16
	1.2
	-
	-
	-
	-
	-
	-
	-
	-
	--


Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:
Ask the unit to submit the action plan for closing the plant.

Action taken/ Status after the meeting held on 11.01.2011

1. In compliance to CMC decision, letter was issued on 28-01-2011 seeking action plan for closure of the plant. 
2. The Unit has not submitted any action plan for closing the plant.

3. DPCC Monitoring results for the months of January, February and March & April 2011are as under:
	
S.No.


	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	
	
	Jan. 11
	Feb. 11
	Jan. 11
	Feb. 11
	Jan. 11
	Feb. 11

	1.
	Duct of unit no. IA
	176
	193
	304
	208
	116
	83

	2.
	Duct of unit no. IB
	192
	177
	280
	240
	116
	83

	3.
	Duct of unit no.IIA
	137
	120
	312
	260
	92
	107

	4.
	Duct of unit no. IIB
	131
	138
	292
	272
	92
	107


\

	
S.

No.


	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	
	
	Mar. 11
	Apr.11
	Mar. 11
	Apr.11
	Mar. 11
	Apr.11

	1.
	Duct of unit no. IA
	234
	132
	280
	320
	219
	213

	2.
	Duct of unit no. IB
	190
	127
	288
	340
	227
	256

	3.
	Duct of unit no.IIA
	117
	198
	320
	360
	94
	190

	4.
	Duct of unit no. IIB
	158
	173
	322
	300
	126
	186


9.  DPCC Monitoring reports for waste water quality from Ash Pond for the month of December 2010, January and February March, April & May 2011 is as under:  

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	STP
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature 
	0.50
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	20.12.2010
	7.8
	-
	1.6
	--
	--
	--
	--
	--
	--
	--
	--
	

	24.01.2011
	7.4
	-
	1.6
	--
	         --
	--
	--
	--
	--
	--
	--
	--

	14.02.2011
	7.6
	-
	1.6
	-
	-
	-
	-
	-
	-
	-
	-
	--

	23.03.2011
	7.5
	  18
	1.6
	-
	-
	-
	-
	-
	-
	-
	-
	--

	19.04.2011
	7.4
	  --
	3.6
	-
	-
	-
	-
	-
	-
	-
	-
	--

	12.05.2011
	7.5
	 20
	1.2
	-
	-
	-
	-
	-
	-
	-
	-
	--


Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:
Issue reminder asking the unit to submit the action plan for closing the plant.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

Pragati Power Station, ITO

Status of Consent:  Renewal of Consent to Operate issued on 18.01.2011 valid upto 07.12.2013

Applied for renewal of authorization under HWM rules on 12.10.2010
Authorization under HWM Rules was issued on 31.01.2011 for a valid period of five years.
1.  DPCC Monitoring reports for waste water from Ash Pond for the month of May, June, 2010 are as under:

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	CMB
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature
	0.50
	6.5-9.0
	50
	10
	30
	250
	STP

Standards 

	05.05.10
	--
	--
	--
	--
	--
	--
	7.4
	28
	1.2
	18
	96
	--

	04.06.10
	--
	--
	--
	--
	--
	--
	7.9
	32
	1.0
	25
	90
	- 


Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Ask for revised application under HWM Rules, 1989, amended.

Action taken/ Status after the meeting held on 09.08.2010:

1. Letter was sent on 03.09.2010 asking for revised application under HWM Rules, 1989, amended.

2. Letters regarding Pollution measures report for the months of August, September, October and November received on 20.09.2010, 19.10.2010, 19.11.2010 and 16.12.2010 respectively.

3. Applied for renewal of Consent to Operate Air & Water for the period of three years on 08.12.2010 along with requisite documents.

4. Annual Environmental Statement of 2009-2010 in respect of Pragati        Power Station (PPS) of Pragati Power Corporation Limited was received on 10.08.2010.

5. DPCC Monitoring results for the months of  August, September, October and November and December 2010 are as under:
	S.No.


	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	
	
	Aug

10
	Sept10
	Oct

10
	Aug

10
	Sept10
	Oct

10
	Aug

10
	Sept

10
	Oct

10

	1.
	Duct of unit no. I
	--
	--
	--
	--
	--
	--
	10
	10
	10

	2.
	Duct of unit no. II
	--
	--
	--
	--
	--
	--
	ND
	10
	10


	S.No.


	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	
	
	Oct

10
	Nov10
	Dec

10
	Oct

10
	Nov10
	Dec

10
	Oct

10
	Nov

10
	Dec

10

	1.
	Duct of unit no. I
	--
	--
	--
	--
	--
	--
	10
	10
	10

	2.
	Duct of unit no. II
	--
	--
	--
	--
	--
	--
	10
	10
	15


7.    DPCC Monitoring reports for waste water from Ash Pond for the month of     August and September 2010 are as under:

August 2010

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	CMB
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature
	0.50
	6.5-9.0
	50
	10
	30
	250
	STP

Standards 

	06.08.10
	--
	--
	--
	--
	--
	--
	7.2
	28
	1.2
	14
	64
	--


October 2010

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	CMB
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature
	0.50
	6.5-9.0
	50
	10
	30
	250
	STP

Standards 

	19.10.2010
	--
	--
	--
	--
	--
	--
	7.6
	44
	1.2
	10
	56
	--


November 2010

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	CMB
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature 
	0.50
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	22.11.2010
	-
	-
	-
	-
	-
	Nil 
	   8.3
	20
	<1.0
	20
	60
	--


Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:
Consent under Air & Water Act is granted and authorization under HWM Rules also granted.

Action taken/ Status after the meeting held on 11.01.2011:
1. Consent to Operate (Renewal) Air & Water was issued on 18.01.2011.

2. Authorization under HWM Rules was issued on 31.01.2011.

3. Annual environmental Statement for the year 2010-2011 was received on 26.05.2011.

4. DPCC Monitoring results for the months of January, February, March & April  2011 are as under:
	

S.No


	Sampling Location


	Concentration in ppm

	
	
	Nox

	
	
	Jan,11
	Feb, 11
	Mar,11
	April, 11


	1.
	Duct of unit no. I
	10
	ND
	#
	#


	2.
	Duct of unit no. II
	10
	10
	#
	#



5. DPCC Monitoring reports for waste water from Ash Pond for the month of December 2010, January, February,  March,  April & May 2011 are as under:

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	CMB
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature
	0.50
	6.5-9.0
	50
	10
	30
	250
	STP

Standards 

	24.12.2010
	--
	--
	--
	--
	--
	--
	--
	--
	--
	--
	--
	No discharge

	25.01.2011
	--
	--
	--
	--
	--
	--
	--
	--
	--
	--
	--
	No discharge

	28.02.2011
	-
	-
	-
	-
	-
	Nil 
	 7.5
	-
	1.6
	22
	72
	--

	25.03.2011
	--
	--
	--
	--
	      --
	--
	--
	--
	--
	--
	--
	--

	11.04.2011
	--
	--
	--
	--
	      --
	--
	--
	--
	--
	--
	--
	--

	10.05.2011
	--
	--
	--
	--
	      --
	--
	--
	--
	--
	--
	--
	--


Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:
No action.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

I.P. Gas Turbine Power Station
 Status of Consent: 
Consent to Operate valid up to 04.01.2011.Applied for renewal.

Applied for renewal of authorization under HWM rules on 1.11.2010
Status of Authorization: Authorization issued to the unit on 31.01.2011 for a valid period of five years.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Ask for revised application under HWM Rules, 1989, amended to date.

Action taken/ Status after the meeting held on 09.08.2010:

1. A letter was sent on 03.09.2010 asking for Consent under Air/Water Act & Authorization for under HWM Rules, 1989, amended to date.

2. Applied for renewal of authorization under HWM Rules on 1.11.2010 

3. DPCC Monitoring results for the months of August, September 2010 are as under:

	

S.No.


	Sampling Location


	Concentration in ppm

	
	
	Nox

	
	
	Aug,10
	Sept, 10
	Oct,10

	1.
	Duct of unit no. I
	#
	51
	51

	2.
	Duct of unit no. II
	#
	46
	51

	3.
	Duct of unit no. III
	61
	61
	#

	4.
	Duct of unit no. IV
	          61
	61
	56

	5.
	Duct of unit no. V
	#
	#
	61

	6.
	Duct of unit no. VI
	#
	#
	61


# - Shut Down/ Under maintenance, 

	

S.No.


	Sampling Location


	Concentration in ppm

	
	
	Nox

	
	
	Nov,10
	Dec, 10

	1.
	Duct of unit no. I
	#
	41

	2.
	Duct of unit no. II
	#
	41

	3.
	Duct of unit no. III
	#
	46

	4.
	Duct of unit no. IV
	           #
	46

	5.
	Duct of unit no. V
	#
	51

	6.
	Duct of unit no. VI
	51
	51


4. DPCC Monitoring reports for waste water from Ash Pond for the month of August, September, October 2010 are as under:
	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	ETP
	Remarks 

	
	pH
	TSS
	Oil & Grease
	Ph
	Temperature Difference 
	Free available Chlorine
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature 
	0.50
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	06.08.2010
	--
	--
	--
	--
	--
	--
	7.6
	44
	1.2
	13
	64
	--

	31.08.2010
	--
	--
	--
	--
	--
	--
	7.6
	12
	1.6
	12
	52
	--

	19.10.2010
	--
	--
	--
	--
	--
	--
	7.6
	50
	2.4
	16
	68
	--


Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:
Authorization granted and ask the unit to submit an application for seeking the consent under Air & Water Act.

Action taken/ Status after the meeting held on 11.01.2011:

1. In compliance of CMC decision Authorization has been issued on 31.01.201.

2. An application for Renewal of Consent to Operate received.
3. DPCC Monitoring results for the months of January, February, March & April 2011 are as under:

	

S. No


	Sampling Location


	Concentration in ppm

	
	
	Nox

	
	
	Jan,11
	Feb, 11
	Mar,11
	April, 11

	1.
	Duct of unit no. I
	#
	#
	#
	#

	2.
	Duct of unit no. II
	#
	#
	#
	#

	3.
	Duct of unit no. III
	56
	46
	#
	#

	4.
	Duct of unit no. IV
	56
	46
	#
	#

	5.
	Duct of unit no. V
	51
	51
	#
	#

	6.
	Duct of unit no. VI
	51
	51
	#
	#


# - Shut Down/ Under maintenance,
4. DPCC Monitoring reports for waste water from Ash Pond for the month of November, December 2010 & January, February, March, April & May 2011 are as under:
	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	ETP
	Remarks 

	
	pH
	TSS
	Oil & Grease
	Ph
	Temperature Difference 
	Free available Chlorine
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature 
	0.50
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	22.11.2010
	--
	--
	--
	--
	--
	--
	6.8
	32
	1.2
	22
	64
	--

	28.12.2010
	--
	--
	--
	--
	--
	--
	7.6
	--
	1.6
	22
	72
	--

	25.01.2011
	--
	--
	--
	--
	--
	--
	7.5
	--
	2.4
	24
	108
	--

	28.02.2011
	--
	--
	--
	--
	--
	--
	6.7
	--
	4.0
	19
	144
	--

	23.03.2011
	--
	--
	--
	--
	--
	--
	--
	--
	--
	--
	--
	--

	11.04.2011
	--
	--
	--
	--
	--
	--
	--
	--
	--
	--
	--
	--

	10.05.2011
	--
	--
	--
	--
	--
	--
	--
	--
	--
	--
	--
	--


Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:
Grant renewal of consent to operate.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

Pragati Power Station , Bawana

Status of Consent: 
Consent to establish issued for one year for 1600 MW on 27/7/2007.

Not applied for consent to operate.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Ask the unit to submit progress report on construction and commissioning of the plant and apply for CTO before operation of the project.
Action taken/ Status after the meeting held on 19.01.2010:

1. Letter w.r.t. Compliance of Committee (MSW) meeting held on 19.01.2010 issued on 12.02.2010.

2. Reply Awaited.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
Issue D.O. letter from MS, DPCC to Secretary (Power), GNCTD seeking progress report on construction and commissioning of the plant and urge them to apply for CTO before commissioning of the project.

Action taken/ Status after the meeting held on 20.04.2010:

1. D.O letter from MS, DPCC to Secretary (Power), GNCTD seeking progress report on construction and commissioning of the plant and urge them to apply for CTO before commissioning of the project was issued on 02.06.2010.

2. Reply awaited.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010

Issue reminder asking the unit to apply for CTO.

Action taken/ Status after the meeting held on 09.08.2010:

1. A letter has been issued on 03.09.2010 requesting to submit an application for Consent to Operate.
2. Not applied for CTO.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011: 
No action

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011: 
Inspection be carried out to know the operational status.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

Combined Cycle Power Plant at Sector-11, Rohini, Delhi BY NDPL

Status of Consent: Applied for Consent to establish for 108 MW on 10.07.08.
Consent to operate issued on 24.01.2011 and valid upto 01.12.2013.

Details of the Project:

Proposed capacity of the plant is 108 MW (Natural Gas based Combined Cycle Power Plant). 

Plot Area     :- 



24281 sq. m 

No. of workers 
:-


60

Proposed date of commissioning: -
May, 2009 (Open Cycle) and August, 2009 





(Closed Cycle).

Total Capital Investment: -

Rs. 256.48 Crores

Water consumption: -


8640 KLD (Treated Effluent from Rithala 





STP).


ETP proposed for treatment of 4320 KLD and after treatment effluent will be utilized for floor washing, dust suppression and greenbelt while the remaining will be discharged to nallah near the project site.  

Domestic effluent:-
108 KLD to be disposed of Sewer of Drain. 

No D.G. Set proposed. 


Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
No action.

Action taken/ Status after the meeting held on 09.08.2010:

1. The unit has applied for CTO on 02.12.2010 along with provisional technical        adequacy report of the pollution control systems on 20.12.2010.
· Submitted adequacy report is examined and found the design parameter of neutralization tank and guard tank is adequate as well as efficient to neutralize the waste water coming from different sources/sections of the unit. 
2. The unit had paid the consent fee for period of three years towards the operational     period and Consent Fee for period of 1 year towards CTE from the date of Expiry     of CTE.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:
Consent to Operate is granted.

Action taken/ Status after the meeting held on 11.01.2011:

1. Consent to Operate has been issued on 24.01.2011. 
2. Unit submitted a letter to seek NOC regarding storage of chlorine etc.

3. It was communicated consent has been granted by DPCC.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:
Issue authorization under HWM Rules.

Also, inspect the plant to know the pollution control status.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell
Pragati Power Corporation Ltd., Bamnauli

Name of the agency: M/s Pragati Power Corporation Ltd., IP Estate, Ring Road, New Delhi.
Particulars of the project: Generating Electricity 
Status of Consent: Applied for consent to establish on 18.09.09.
Details of the project: 

a. Proposed activities are for generating electricity of 750 MW (Nominal)/8010 MW (max). 

b. Proposed Investment on the project is Rs.3022.17 crores.

c. Total Plot Area is 2,00,000 sq m

d. Built up area- 1,00,000 sq m.

e. Proposed to be commissioned from 2011-12.

f. No of workers & other staff- 480 persons

g. Water consumption:

Domestic – NIL, 

Industrial cooling – 38,400 KLD, 

Processing – 2,400 KLD,
Other (Gardening) – 2,400 KLD

h. Quantity of domestic waste generated is 10 KLD and Industrial is 19920 KLD.

i. DG Sets proposed to be installed – 2 X 1500 KVA with acoustic enclosure.

j. Perpetual lease by DDA for this land is enclosed.  

Environmental Clearance Status:

Telephonically discussed with the authorities and it is revealed that formal Environmental Clearance is awaited. However, presentation has been made before the committee on 07.12.2010 in MoEF.

Remarks:

1. Unit applied for CTE along with EIA report with a request to conduct public hearing.

2. No request/direction from MoEF, GOI received for conducting public hearing, before issuance of EC. 

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:
SEE to check with the department of Power, GNCTD, Dy. Commissioner and MoEF and put the file on the issue of conducting public hearing without waiting for minutes. 
Action taken/ Status after the meeting held on 19.01.2010:

1. Public Notice for public hearing published on 12.03.2010.

2. Public Hearing conducted in the office of Deputy Commissioner (South- West) on 16.04.2010, Minutes/ Findings/ Outcomes of the hearing are under preparation.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
Await for Environmental Clearance (EC).

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

No action
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

No action

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:
Ask the unit to submit a copy of  Environmental Clearance.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

Fly ash generation and its utilization by Thermal Power Plants

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
Ask the units to submit complete report on generation and utilization of fly ash including cumulative quantity (enclosing Performa) till date.

Action taken/ Status after the meeting held on 20.04.2010:

1. A letter was issued asking units to submit complete report on generation and utilization of fly ash including cumulative quantity (enclosing Performa) till date on 20.05.2010.

2. A copy of letter was received by GM, IPGCL-PPCL regarding submission of Annual compliance on Fly Ash generation & utilization for the year 2009-10 on 15.06.2010 in response to our earlier letter dated 20.05.2010 

3. Monthly report on Ash generation and utilization for the months of March, April, May, June 2010 dated 15.06.2010 and 16.07.2010 received from Rajghat power house.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
Issue reminder seeking the details of fly ash utilization with cumulative generation since inception.
Action taken/ Status after the meeting held on 09.08.2010:

1. Reminder letters were issued seeking the details of fly ash utilization with cumulative generation since inception to Badarpur Thermal Power Station and Rajghat Power House Complex on date 03.09.2010.
2. No reply has been received till date.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

A meeting of the Senior Officer may be called at the level of Member Secretary.

Action taken/ Status after the meeting held on 11.01.2011:

1. A meeting held on 17.02.2011in response to the meeting. Report filed by Badarpur Thermal Power Station. But report is not received from Rajghat Power House. 
2. Monitoring committee has been constituted by State Government on 29.04.2011, for the implementation of provisions of Notification dated 03.11.2009. Composition of the committee is as under:-
· Secretary (Environment) - Chairman

· Representative form Power Department- Member

· Representatives from NDMC, MCD, PWD, CPWD, DCB, DSIIDC, I&FC NHAI- Members

· Member secretary, Delhi Pollution Control Committee- Member
The Committee will meet once in three months to review the progress regarding implementation of the Notification
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Issue reminder to Rajghat Power Plant to submit details of fly ash utilization including cumulative generation and its utilization.

Also, ask IP Power plant to submit the details as fly ash.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

Annexure - 5
Modern Poultry & Egg market at Ghazipur, New Delhi.

Name of the agency: M/s Delhi Agriculture Marketing Board, 9, Institutional Area, Pankha Road, Janakpuri, New Delhi-110058.
Particulars of the project: Modern Poultry & Egg market at Ghazipur, New Delhi.
Status of Consent: 

Consent to Establish issued on 09.02.2010, valid up to 07.02.2011.

Details of the project: 

a. Product is dressing of Poultry birds- 48 lakhs birds/ month. 

b. Raw material is Poultry birds- 576 lakhs/ annum. 

c. Proposed Investment on the project is Rs.133.5 crores.

d. Quantity of waste to be disposed per day is 30 TPD.

e. Total Plot Area is 60200 sq m and Built up area- 48160 sq m

f. Sanctioned Power Load /power required– 2925 KW

g. Proposed to be commissioned from March, 2010.

h. No of workers: 

a) During construction phase – 100 b) During operational phase-   25

i. Water consumption:

Domestic - 91000 LPD, 
Industrial cooling/ boiler feeds - 92000 LPD       processing   - 1120000 LPD,
Other (Gardening) – 108000 LPD

j. Quantity of domestic waste generated is 80000 LPD and Industrial is 1100000 LPD

k. Proposed Effluent Treatment Plant of 1200 KLD with tertiary treatment & UV Irradiation and reuse in flushing, HVAC, DG, Horticulture (C/52 of the file). A STP of 200KLD is also proposed (C/58 of the file). 

l. DG Sets proposed to be installed – 2 X 1000 KVA + 2 X 625 KVA.

m. Land allotted by DDA for this purpose (allotment letter at C/4-6)  

Remarks:

As per the provisions of EIA notification dated 14.09.06 the following construction projects are to be required Environmental Clearance from MoEF:

Building and Construction Projects having built up area ≥ 20000 sqm and < 150000 sqm of built up area. 

Townships and Area Development Projects having covering an area ≥ 50 ha and or built up area ≥ 150000 sqm.   

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
MS, DPCC to take a meeting with Director, DAMB.

Action taken/ Status after the meeting held on 20.4.2010:

A meeting of MS, DPCC with Director, DAMB was held on 02.06.2010 to discuss the issues related to installation of ETP and rectification of the deficiencies observed during the inspection. DAMB was advised to get the consultancy from empanelled consultants of DPCC.

A letter was received from DAMB on 16.06.2010 informing that offer has been invited from the consultants empanelled with DPCC and will be received by 23.06.2010.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
Issue letter to seeking present status regarding installation of ETP and ask the unit to install ETP in 3 months.

Action taken/ Status after the meeting held on 09.08.2010:

1. A letter has been issued on 06.09.2010 to seek compliance affidavit on conditions laid down in Environmental Clearance.

2.  In response to our letter DAMB has submitted a reply on 1.10.2010 that Jamila Milia Islamia has been appointed as a consultant for installation of ETP and the time bound programme of installation of ETP will be submitted to DPCC.
3.   No time bound programme submitted by the unit.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

A meeting may be called at the level of Chairman DPCC
Action taken/ Status after the meeting held on 11.01.2011:

1. A meeting held on 03.02.2011 in the office of Chairman, DPCC.

2. Show Cause Notice of directions u/s 33(A) issued on 09.03.2011 for removal of deficiencies and to install ETP with in three months.
3. Reply received with following information:
i) Operation / Working condition: The slaughtering is presently done under sheds. The proposal to make a slaughtering under enclosed shed/ premises is being worked out and would be soon implemented.

ii) Installation of ETP: It is to inform that consultant has been engaged to design the ETP.
    4. Inspection carried out on 01.06.2011 and no progress made towards any improvement on site, and latest inspection findings are:-
a) Chicken Dressing plant not made.

b) Installation of ETP has been initiated by inviting quotation as updated.

c) Open slaughtering being made.

d) Waste water containing the blood is flowing openly on land.

e) Birds menace is there because of open slaughtering and littering of birds’ slaughtered parts.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Issue directions u/s 33(A) of Water Act 1974 to install ETP by 30.9.2011 failing which the unit will be closed down and water/ power supplies will be disconnected.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell


                  Delhi Food Processing Complex (Meat) at Ghazipur, Delhi

Name & Address: Municipal Corporation of Delhi, Delhi Food Processing Complex (Meat) at Ghazipur, Delhi 

Correspondence Address: MCD Department of Veterinary Services, Room No. 56, Town Hall, Delhi-06
Status of Consent: 

Consent to Establish valid upto 13.09.09. 
Consent to Operate valid upto 18.10.2012.
Activity: Slaughter House 

Status: 

Applied for consent to establish under Air & Water Act on 02-06-05 EIA report not submitted alongwith the application.  The case was earlier dealt by EIA Cell and matter was sent to Ministry of Environment & Forest, since issues related to EIA notification and Hon’ble Supreme Court Orders are also involved in this case, letter was also issued on 30-08-07 by EIA Cell regarding seeking information about the Environment clearance by MOEF however reply to the said letter has not been received so far. As directed inspection was conducted by a team comprising of DPCC officials and Dr. T.K. Joshi, Head, CEOH on 24-08-07(Copy enclosed).  During the inspection the civil construction work as well as fixation and erection of machineries was going on.  The work of construction of ETP was also going on. In the vicinity the rendering plant is also coming up and an ETP was also seen.  The inspection of the facility could not be done since no responsible person at the site.  Details of the ETP submitted with the project report mentions about Physico Chemical Treatment.  Since waste water generated from both the section (i) Slaughter House (ii) Rendering Plant has mainly organic waste which is biodegradable, therefore Physico Chemical Treatment should be avoided since as per HW Rules it will be generating Hazardous Waste.  Besides above unit should also go for better sludge handling mechanism Letter was issued followed by the reminder letter as decided by the BMW Committee & Reply along with Report on ETP/ Rapid EIA Report received. MOEF Clearance yet to be received.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
Obtain the compliance affidavit from the unit.

Action taken/ Status after the meeting held on 20.4.2010:

A letter was issued to the unit on 10.05.2010 regarding the submission of compliance affidavit w.r.t the conditions laid down by MoEF, GOI while issuing environmental clearance.

· No response is received from the unit as well as MCD.

· Consent to operate and establish were given with conditions and compliance is not received so far. 

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
Issue letter seeking compliance affidavit of EC conditions and also to submit effluent and emission reports as stipulated in the CTO issued earlier.
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Action taken/ Status after the meeting held on 09.08.2010:

1. A letter was issued to the unit on 06.09.2010 regarding the submission of compliance affidavit w.r.t the conditions laid down by MoEF, GOI while issuing environmental clearance.

2. Compliance affidavit not submitted.
3. Unit had submitted its Analysis reports on 15.11.2010 in respect of DG Sets, Boiler and Effluent treatment plant. 
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:
To inspect and monitor the rendering plant.  Also call a meeting of MCD officers at the level of Chairman, DPCC regarding not filing the compliance affidavit against the conditions stipulated in the Environmental  Clearance issued by MoEF. 

Action taken/ Status after the meeting held on 11.01.2011:
1. Subsequent to the CMC decision dated 11.01.011, inspection was carried out and meeting was called before chairman, DPCC on 03.02.2011. This meeting was attended by the officials of MCD & Frigorifico Allana Limited (Operator of Slaughter House), during Meeting MCD was asked to complied the following:
i) The consentee shall make possible efforts to reuse the entire treated effluent generated after the treatment of industrial waste water from both ETP.

ii) The industrial waste water from both the ETPs, after treatment shall be discharged into a closed conduit at one point only through a terminal outlet with arrangement for flow measurement.

iii) The solid waste generated should be properly collected and segregated. Wet garbage should be composted and dry/inert solid waste should be disposed off to the approved sites for land filling after recovering recyclable material.

iv) The consentee shall install Air Diffusers to control odour problems.

v) The consentee shall install Rain Water Harvesting System so that the Rain Water shall be used for plant. Rain water harvesting for roof run-off and surface run-off, as plan submitted should be implemented. Before recharging the surface run off, pre-treatment must be done to remove suspended matter, oil and grease. The bore well for rainwater recharging should be kept at least 5 mts. above the highest ground water table.

vi) The ground water level and its quality should be monitored regularly in consultation with Central Ground Water Authority.

vii) Provision of a green belt shall be made to segregate slaughter house from sanitary land fill site.

viii) The consentee shall install a separate system for collection of blood for converting it into value added product.
2. Show Cause notice U/s 33(A) of Water Act, 1974 issued on 17.02.2011.

3. Reply received promising to rectify the deficiencies & submit compliance affidavit on the condition of Consent & Environmental Clearance. No time bound action plan submitted.

4. Latest inspection was conducted on 01.06.2011 and its findings are:-

i) Unit is found in operation. 

ii) Two establishment Rendering plant & and Slaughter house are in operation stage.

iii) ETP of both establishments are operating.

iv) Aeration system in the ETP of Rendering plant no found adequate since blowers are not working at full.

v) Flow meter not installed at rendering plant.

vi) Treated water of Slaughter house is not being circulated or reused at full.

vii) Compliance report against the conditions of Consent+ EC not provided.

viii) Treated water is only being drained; hence purpose of treatment is no use.

ix) Rain water harvesting facility not installed.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:
Issue reminder to remove the deficiencies and to submit compliance affidavit on the EC & consent conditions.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell


 Municipal Waste Complex at Gazipur Bio-gas Plant Site

Name of the agency: M/s East Delhi Waste Processing Company Ltd. (EDWPCL)
Particulars of the project: 

     Setting up of integrated Municipal Waste Complex at Ghazipur Bio-gas Plant Site, Ghazipur. 

     The capacity of the project would be 1200TPD. The treatment/ processing of the MSW would be based on DST-TIFAC technology of mixed municipal waste to RDF Fluff preparation and bio-gas generation from the organic waste. The power generation would be 10-12 MW.

Status of Consent: 

Applied for consent to establish under Air & Water Acts on 22-06-07 & Consent to establish has been issued on 03.07.07 which was valid upto 21.06.08 (C/306) and expired on 22.06.08.

Status of authorization under MSW Rules: 

Applied for authorization under MSW Rules on 30.03.07 and Authorization under MSW Rules was also issued on 03.07.07 for the period of two years (C/303).

Action regarding clearance from other departments: 

Letter issued on 10.05.07 to the operator of the facility to submit:

Detailed project report.

Site clearance certificate from the land owning agency.

EIA clearance from Ministry of Environment & Forests, Government of India.

View of Air Force Base Station, Town and Country Planning, Department of UD, Govt. of India etc.

Status:
· Detailed project report is not received.

· Site clearance certificate from the land owning agency is not received.

· EIA clearance from Ministry of Environment & Forests, Government of India is not received.

· View of Air Force Base Station, Town and Country Planning, Department of UD, Govt. of India etc are not received.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

No Action.

Action taken/ Status after the meeting held on 19.01.2010:

1. Representation from the unit was received on 17.02.2010 and 16.04.2010 regarding extension of validity of Authorization under MSW Rules 2000, for next two years i.e. 2nd July 2011.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
Inform the unit that an extension of authorization under MSW Rules, 2000 is not required till the facility starts operating.

Action taken/ Status after the meeting held on 20.04.2010:

A letter was issued by DPCC on 26.07.2010 to M/s East Delhi Waste Processing Co. Pvt. Ltd (EDWPCL) stating that an extension of authorization under MSW Rules, 2000 is not required till the facility starts operating.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
No action

Municipal Waste Complex at Gazipur Bio-gas Plant Site

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

No Action

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Issue letter to the project proponent to submit progress report on the project.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

Development of Engineered Landfill site at Jaitpur/Tajpur

Name of the agency: Municipal Corporation of Delhi.
Particulars of the project: 

Development of Engineered Landfill site at Jaitpur/ Tajpur

Agency applied by MCD is Birla Technical Services.

The capacity of waste to be disposed off 1000-1500 TPD.  

Construction, operation and maintenance of this ESL are to be carried out in 32.464 acre of abandoned stone quarry.  

The present status of the site is as under as per brief note received from Sh. Arun Kumar (Spl. Proj.), MCD:- 

Survey of the quarry carried out.

All Geotechnical investigation including monitoring wells testing of rock/water sample completed.

Preliminary final designed checked and approved through IIT Delhi.

Final designed under submission by BTS.

De-watering completed in major portion/in progress in remaining isolated small pits.

Sumps/Pump houses established for stoppage of incoming water to the quarry.

Part fencing works completed.

Ramp under construction.

Sludge removed from dewatered area.

Site grading works in progress.

Status of authorization under MSW Rules: 

Applied for authorization under MSW Rules on 07.01.04 and Authorization under MSW Rules was also issued on 23.06.04 and valid till construction & operation of the project.

Status:
The site was inspected by DPPC official on 27.06.08 along with official from MCD and Birla Technical Services and it was observed that progress with regard to development of landfill site is very slow.  As per brief note received from MCD some public hindrance also was encountered in the month of April, 2008.  However, it is expected that by the end of this financial year, operation in one cell will be started in parallel to remaining construction activity.    

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
MS, DPCC to take a meeting with DEMS, MCD.

Action taken/ Status after the meeting held on 20.4.2010:

· MS, DPCC took a meeting on 04.06.2010 as decided by CMC.

· Mr. J.P Bansal EE, attended the meeting from MCD and informed that work has been stopped w.e.f September, 2008. Case is under consideration with arbitration. 

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
No action at present.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated:
Ask the unit to submit status report regarding the consideration of plant with arbitration and what is the further programme regarding this site.

Action taken/ Status after the meeting held on11.01.2011:
1. In compliance of CMC decision a letter issued on 28.01.2011. 
          The unit has submitted its reply with the information Since, M/s BTS to whom           the work was awarded has virtually abandoned the project unilaterally. The           next course of action with regard to execution of the project is to be decided. 

M/s BTS moved to Ho’ble High court of Delhi for appointment of arbitrator and Sh. O.P. Goel, Ex. Director, General, CPWD has been appointed as sole arbitrator. Arbitration proceedings are going on.

 Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:
Ask the unit to submit present status on the arbitration process.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

Timarpur Okhla Waste Management Company Limited
Name of the agency: New Delhi Municipal Council. (M/s Timarpur-Okhla Waste Management Company Private Ltd).  
CTO issued on 20.01.2010, valid up to 20.01.2012.

NOC of AAI received from the unit on 22.01.2010.

Authorization under MSW Rules issued on 04.02.2010, valid up to 03.02.2012.
Particulars of the project: 

Setting up of integrated municipal waste complex at NDMC Plant Site.  Sukhdev Vihar, Okhla.  The capacity of the project would be 950 TPD beside 150 TPD green garbage.  The treatment / processing of the MSW would be based on DST-TIFAC technology of mixed MW to RDF/ Fluff preparation and bio gas generation from the organic waste.  The power generation would be 10MW. Cost of project is Rs. 1742.62 million.  

Status of Consent: 

· Consent to establish under Air and Water Act has been issued on 03.07.07 and valid upto 09.05.08.

· Requested for extension of consent to establish for two year along with consent fee of Rs. 5200/- vide letter dated 01.07.08 after expiry of the consent.  No formal application submitted for extension of consent to establish under Air and Water Act.  

· The unit has submitted another letter on 17.07.08 with a request that the application was submitted earlier for extension of the consent to establish after the lapse of due date (i.e. expiry of consent to establish on 09.05.08), it is understood that a fine of Rs.2600/- is payable.  They have requested that this additional amount may be adjusted from DD No. 357265 dated 30.06.08 for Rs.5200/- for Timarpur project vide letter dated 01.07.08 wherein only Rs.2600/- is payable to DPCC.
· Copy of Share Transfer Agreement between IL&FS Infrastructure Development Corporation Limited, Jindal Urban Infrastructure Ltd & Timarpur Okhla Waste Management Company Pvt. Ltd.  is also enclosed with letter dated 17.07.08.
Status of authorization under MSW Rules: 

Authorization under MSW Rules was issued on 09.03.07 and valid upto 08.03.09.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
· No Action.

· Case related to Municipal Solid Waste Complex of Timarpur also has been clubbed by CMC in its meeting held on 20.04.2010

· This project of Okhla Timarpur waste facility has been inaugurated by Hon’ble CM on 28.06.2010.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
No action

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:
No action

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:
No action.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

IL&FS Compost Plant at Okhla

Name of the agency: Municipal Corporation of Delhi and IL & FS Waste      Management and Urban Services Ltd. 
Particulars of the project: 

Revival of the Compost Plant of Municipal Corporation of Delhi at Okhla, Delhi (The compost plant at Okhla is existing plant of MCD which stopped operation in 1994 and MCD now has handed over this plant to IL & FS for revival of up gradation).   

Status of Consent: 

Consent to establish has been issued on 29.01.08.

The unit has applied for consent to operate on 21.01.09, CTO issued on 20.01.2010, valid up to 20.01.2012. 

Status of authorization under MSW Rules: 

Applied for authorization for setting up and operation of waste processing facility on 20/11/07 (C/1 to 67), Authorization under MSW Rules issued on 04.02.2010, valid up to 03.02.2012.

Details of the project: 

Processing technology is composting through open
air aerobic window composting method.

Quantity of waste to be processed is 200 TPD.

Investment on the project is Rs.6.2 crores.

Quantity of waste to be disposed per day is 40 TPD.

 Plot Area is 29000 sq m and Built up area- 4000 sq m 

 Sanctioned Power Load – 280 KW

  Revival period the compost plant will be start on 1 March, 2008.

  Water consumption for domestic is 2000LPD & for processing is 20,000 LPD

  Quantity of domestic waste generated is 1500 LPD and leach ate to be recycled in       composition process

   100 KVA DG Set proposed to be installed.

   Concession Agreement between MCD and IL & FS is placed at (C/71 to 103).

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue CTO and issue letter to AAI seeking their views giving final 15 days without waiting for minutes. Even if the reply/views are not received within 15 days, put up the file administratively for decision.

Action taken/ Status after the meeting held on 19.01.2010:

CTO issued on 20.01.2010, valid up to 20.01.2012.

NOC of AAI received from the unit on 22.01.2010.

Authorization under MSW Rules issued on 04.02.2010, valid up to 03.02.2012.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
No Action.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
No action
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:
No action

Action taken/ Status after the meeting held on 11.01.2011:

1. An inspection was approved on file, accordingly was carried out on 18.05.2011, findings are following:

i)   Garbage provided by Delhi waste management Co. from the MCD area and by RAMKAY ENVIRO from NDMC area.

ii) Total Garbage Received on an average 150 MT/ Day.

iii) Production output of organic manure is 25-30 MT/day & having an arrangement with NFL & Coremondal International ltd. & Kribhco for manure supply.

iv) Reject waste around 60-65 MT/ day is being sent to Okhla Landfill site.

v) A.R.C.C tank is constructed for collecting the leachate and it is recycled over garbage for maintaining the moisture content.

vi) It is reported that ENRACULAM (Effective manures + Mollasis with water) is being sprayed to control smell, larva and for fast decomposition.

vii) Leachate treatment provision not given.

viii) Odour control measures are not taken.

ix) Separate storm drain provision is not adequate. 

2. An application was received on 24.05.2011 for expanding the capacity of Okhla Compost Plant with an additional activity of RDF production to minimize the quantum of rejects going to landfill as inert. 
3. Show cause notice of directions u/s 5 of the Environment (Protection) Act, 1986 as amended to date, read along with Municipal Solid Wastes (Management and Handling) Rules, 2000 as amended to date has been  issued on 03.06.2011.
4. Reply against the show cause notice awaited.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Decision, to issue SCN of directions u/s 5 of Environment (Protection) Act, 1986, taken on file ratified.

Put up administratively after the receipt of the reply.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

Compost Plant at Tikri Khurd/ Khampur

Name of the agency: M/s Spiral Services, New Sabzi Mandi, Azad Pur, Delhi
Particulars of the project: 

A.P.M.C. Compost Plant at Tikri Khurd/ Khampur, G.T. Karnal Road, Delhi-40 
Status of Consent: 

· Consent to Operate issued on 20.01.2010, valid up to 03.03.2011. Applied for renewal on 01.03.2011.

Status of authorization under MSW Rules: 

Authorization under MSW Rules 2000 issued on 25.01.2010, valid up to 24.01.2012.

Details of the project: 

Processing technology is composting through open air aerobic window composting method.

Quantity of waste to be processed is 200 TPD.

Investment on the project is Rs.1.6 crores.

Quantity of waste to be disposed per day is 30 TPD.

Plot Area is 24000 sq m.

Built up area- 1000 sq m

Sanctioned Power Load – 5 KV

Proposed to be commissioned from March, 2008 (earlier unit exist since 17.01.02).

Water consumption for domestic is 1440 LPD &  for processing  is  5000 LPD

Quantity of domestic waste generated is 1000 LPD & having 2 septic tanks and leach ate to be recycled in composition process.

No DG Set proposed to be installed.

Agreement between APMC and Spiral Services is placed at (C-/3 to 11).

Status:

· Applied for consent to operate under Orange category on 04.03.08. 

· Views/ Comments/ NOC were received only from Town and Country Planning Organization, Ministry of U.D. (C/44- 45) asked before issued of authorization under MSW, Rules. Views/ Comments/ NOC are still awaited from Air Force, DDA and Central Ground Water Board.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:

Inspect and report.

Action taken/ Status after the meeting held on 09.08.2010:

Compost plant was inspected by team of DPCC officials on 14.12.2010 and the following observations are made:

a. Compost plant complying with the conditions mentioned in Annexure I

b. Proper lining of RCC is provided to prevent percolation of leachate.

c. Waste was properly tagged/ labeled and managed.

d. DG Set of 25 KVA found.

e. Rejects from the waste are not being sent to landfill.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit to file an application for consent prior to its expiry of the granted consent and also ask to furnish the report why the reject material of composting is not being sent to sanitary land fill site (SLF).

Action taken/ Status after the meeting held on 11.01.2011:
A letter has been issued on 21.04.2011.
No reply received till date.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Issue reminder for removal of deficiencies as communicated earlier.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

Compost Plant of Municipal Corporation of Delhi at By Pass, Bhalswa, Delhi
Name of the agency: Nature Waste Management India Pvt. Ltd. MCD Compost Plant, G. T. Karnal Road, By Pass, Bhalswa, Delhi -110042

Status of Consent: 

CTO issued on 20.01.2010, valid up to 26.10.2012.

Status of authorization under MSW Rules: 

Authorization issued on 21.01.2010, valid up to 20.01.2012.
Particulars of the project: 

Compost Plant of Municipal Corporation of Delhi at G. T. Karnal Road, By Pass, Bhalswa, Delhi-110042

Details of the project: 

a. Processing technology is composting through open air aerobic by Excel Technology.

b. Quantity of waste to be processed is 600 TPD.

c. Investment on the project is Rs.10 Crores.

d. Plot Area is 48552 sq m and Built up area- 16000 sq m 

e. Sanctioned Power Load – 125 KVA (K.No. 451099026136)

f. Water consumption for domestic is 500 LPD & for processing is 1,000 LPD (In summer months 3,000 LPD).

g. Quantity of domestic waste generated is Nil.

h. No trade effluent generated.  Only effluent from the rain water-re circulated to the waste heap.  

i. 82.5 KVA DG Set installed which is without acoustic enclosure and proper stack height. 

j. Agreement for sub-contractor is placed at (C/1-25).

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
Expedite Inspect and report.

Action taken/ Status after the meeting held on 09.08.2010:

Compost plant was inspected by the team of DPCC officials on 14.12.2010 and the following observations were made:

1. During inspection unit was found operational.

2. Unit doesn’t have any measures to control pollution caused by conversion of garbage into manure.

3. Protective measures in respect of ground water contamination are not taken.

4. Leachate observed and was flowing openly on land.

5. Stray animals and bird menace also observed and no safeguards are taken.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:
Ask the unit to control the water pollution caused by leachate and also give the direction to take the measure for controlling the birds menace.

Action taken/ Status after the meeting held on 11.01.2011:

1. A letter issued on 07.03.2011.

2. No reply received so far.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:
Issue reminder for removal of deficiencies as communicated earlier.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

Wholesale Flower market at IFC, Ghazipur, NH-24, New Delhi
Name of the agency: M/s Delhi Agriculture Marketing Board, 9, Institutional Area, Pankha Road, Janakpuri, New Delhi-110058.
Particulars of the project: Setting up Wholesale Flower market at IFC, Ghazipur, NH24, New Delhi.

Status of Consent: 

Applied for consent to establish under Air & Water Acts vided ID. No. 27420 dt. 19.09.08, Consent to Establish issued on 09.02.2010, valid up to 07.02.2011.

Details of the project: 
a. Proposed activities are setting up wholesale flower market and multilevel parking. 

b. Proposed Investment on the project is Rs.116.89 crores.

c. Total Plot Area is 150866.22 sq m

d. Built up area- 103049.84 sq m.

e. Sanctioned Power Load /power required– 4000 KW.

f. Proposed to be commissioned from December, 2008.

g. No of workers: 

a) During construction phase – 100 b) During operational phase-   25

h. Water consumption:

Domestic – 154.5 KLD, 
Industrial cooling - 52 KLD, 

Processing   - 50 KLD,
Other (Gardening) – 108 KLD

i. Quantity of domestic waste generated is 136 KLD and Industrial is Nil.

j. Proposed Sewage Treatment Plant of 150 KLD with primary and secondary treatment and treated domestic effluent will be partly utilized for green belt, DG. Set and AC Cooling and rest will be discharge into sewerage system.

k. Sludge Generating from STP will be used as manure for gardening purpose/ Sold as per standard practices.

l. DG Sets proposed to be installed – 3 X 1250 KVA + 1 X 1650 KVA with acoustic enclosure.

m. Perpetual lease by DDA for this land is enclosed.  

n. As per application unit will be taken authorization under Hazardous Waste Rules for storage of hazardous waste (used oil from DG Set) during operational phase. 

Remarks:

As per the provisions of EIA notification dated 14.09.06 the following construction projects are to be required Environmental Clearance from MoEF:

Building and Construction Projects having built up area ≥ 20000 sqm and < 150000 sqm of built up area. 

Townships and Area Development Projects having covering an area ≥ 50 ha and or built up area ≥150000 sqm.   

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
Seek compliance affidavit on the conditions laid down in EC.

Action taken/ Status after the meeting held on 09.08.2010:
1. A letter has been issued on 03.09.2010 to seek compliance affidavit on the conditions laid down in EC. No response is received.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit to submit a compliance affidavit against the conditions stipulated in the Environment Clearance issued by MoEF and also ask to submit the present status of unit.

Action taken/ Status after the meeting held on 11.01.2011:
A letter issued on 07.02.2011 to ask the unit to submit a compliance affidavit against the conditions stipulated in the Environment Clearance issued by MoEF and also ask to submit the present status of unit.

No response received so far.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Issue reminder for submission of an affidavit on compliance of the conditions laid down vide Environmental Clearance.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell


Bio-Tag, #281, MIG, Pocket- B, Sector-14, Dwarka, New Delhi-110078

Name of the agency: Bio-Tag, #281, MIG, Pocket- B, Sector-14, Dwarka, New Delhi- 110078

Particulars of the project: Composting.

Status of authorization: Applied for Authorization for- A) Setting up & operation of waste processing and disposal facility and B) Setting up & operation of disposal facility, on 08.03.2010.

Details of the Project:- 

Processing of Waste 

i.  Location of site 




Kakrola, New Delhi.

ii.  Name of waste processing technology  
Composting

iii.  Details of processing technology 

Submitted 

iv. Quantity of waste to be processed 

per day 





20 TPD

v.  Site clearance (from local authority)
N.A. 

vi.  Details of agreement between municipal 

      authority and operating agency 

N.A. 

vii.  Utilization programme for waste 

       processed (Product utilization)
the Compost generated will be at the plant sold at the market.

viii.  Methodology for disposal of waste 

       processing rejects (quantity & quality) Sent to Bhalsawa SLF.

ix.  Measures to be taken for prevention and 

      control of environment pollution 
The equipments as per CPCB, DPCC and MSW Rules will be installed as per requirement.

x.  Investment on Project and expected 

     returns 





2-3 lakhs

xi.  Measures to be taken for safety of 

     workers working in the plant 
Gloves, masks, safety shoes, helmets, safety against fire Hazards, electrical safety equipment.

Disposal of Waste

i.
Number of sites identified


Bhalsawa SLF

ii.
Layout maps of site 



Nil

iii.
Quantity of waste to be disposed per day
15-20 TPD 

iv.
Nature and composition of waste 
  
All inert materials

v.
Details of methodology or criteria 

followed for site selection 


N.A. 

vi.
Details of existing site under operation 
N.A.

vii.
Methodology and operation details of 

landfilling





N.A. 

viii.
Measures taken to check environmental

pollution 





N.A.  


Remarks:

Detailed project report is submitted by the applicant.

Action taken/ Status after the meeting held on 20.04.2010:

1. Application for Consent to Establish (CTE) under Water (prevention and control of pollution) Act, 1947 and under Air (Prevention and Control of Pollution) Act, 1981 was received on 03.05.2010 from BIO-TAG.

2. Application was found deficient in details of waste collection, transportation and disposal site.

Bio-Tag, #281, MIG, Pocket- B, Sector-14, Dwarka, New Delhi-110078

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
Issue letter asking the applicant to provide missing details and submit the copies of agreements with MCD/DEMS for collection and disposal of MSW.

Action taken/ Status after the meeting held on 09.08.2010:

A letter has been issued on 03.09.2010 to provide missing details and submit the copies of agreements with MCD/DEMS for collection and disposal of MSW

No response has been received so far. 

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:
Call a personal hearing at the level of Member Secretary DPCC.
Action taken/ Status after the meeting held on 11.01.2011:

1. A meeting has been held on 27.04.2011 at the level of Member Secretary DPCC.
2. Unit has not attended the said meeting.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:
Issue SCN for refusal of CTE under Air and Water Acts and authorization under MSW Rules, 2000.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

Sanitary Landfill Site (Municipal Corporation of Delhi), Bhalaswa, New Delhi

Name of the agency: CSE Department, Municipal Corporation of Delhi.

Particulars of the project: Sanitary Landfill Site.

Status of authorization: Applied for Authorization for operation of disposal facility.

Details of the Project:-    Processing of Waste 





Remarks:   Detailed project report is submitted by the applicant.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
· Put up administratively.

· Case was put up administratively and subsequently decided to place the case in CMC.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
Put up administratively.
Action taken/ Status after the meeting held on 09.08.2010
1. In compliance of CMC decision file was put up administratively wherein it was decided to place it before the committee.

Note: Application filed by the agency i.e. local body is very old approx 7 years) hence unit may be asked to file new application with latest details.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit to apply for Authorization under MSW Rules.

Action taken/ Status after the meeting held on11.01.2011:
A letter was issued on 28.01.2011, to DEMS, seeking application for authorization under MSW Rules, 2000.

Not applied for authorization as yet. 

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Issue reminder seeking application for authorization under MSW Rules, 2000.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell


Sanitary Landfill Site (Municipal Corporation of Delhi), Ghazipur, New Delhi

Name of the agency: CSE Department, Municipal Corporation of Delhi.

Particulars of the project: Sanitary Landfill Site.

Status of authorization: Applied for Authorization for operation of disposal facility.

Details of the Project:-  Processing of Waste 





Remarks:   Detailed project report is submitted by the applicant.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
· Put up administratively.

· Case was put up administratively and subsequently decided to place the case in CMC.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
Put up administratively.
Action taken/ Status after the meeting held on 09.08.2010
1. In compliance of CMC decision file was put up administratively wherein it was decided to place it before the committee.

Note: Application filed by the agency i.e. local body is very old approx 7 years) hence unit may be asked to file new application with latest details.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Ask the unit to apply for Authorization under MSW Rules.

Action taken/ Status after the meeting held on 11.01.2011:
A letter was issued on 28.01.2011, to DEMS, seeking application for authorization under MSW Rules, 2000.

Not applied for authorization as yet. 

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:
Issue reminder seeking application for authorization under MSW Rules, 2000.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell


Sanitary Landfill Site (Municipal Corporation of Delhi), Okhla, Phase-I, New Delhi

Name of the agency: CSE Department, Municipal Corporation of Delhi.

Particulars of the project: Sanitary Landfill Site.

Status of authorization: Applied for Authorization for operation of disposal facility.

Details of the Project: - Processing of Waste 





Remarks:   Detailed project report is submitted by the applicant.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
· Put up administratively.

· Case was put up administratively and subsequently decided to place the case in CMC.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
Put up administratively.
Action taken/ Status after the meeting held on 09.08.2010
1. In compliance of CMC decision file was put up administratively wherein it was decided to place it before the committee.

Note: Application filed by the agency i.e. local body is very old approx 7 years) hence unit may be asked to file new application with latest details.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:
Ask the unit to apply for Authorization under MSW Rules.

Action taken/ Status after the meeting held on 11.01.2011:

A letter was issued on 28.01.2011, to DEMS, seeking application for authorization under MSW Rules, 2000.

Not applied for authorization as yet. 

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:
Issue reminder seeking application for authorization under MSW Rules, 2000.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

Integrated Municipal Solid Waste Management Facility at Bawana- Narela

Name of the agency: Delhi MSW Solutions Ltd. (a Ramky Group Venture) 

Particulars of the project: Integrated MSW management facility.
EC is granted to the unit on 25.10.2010.

The processing of disposal facility is planned for 4000 TPD (I phase 1500 TPD, II phase 2500 TPD). 

Involved activities are segregation, composting, RDF and SLF with leachate collection and treatment of waste.

MSW coming to the facility will go through material recovery facility and will be diversed into three streams of compost, RDF & recyclables.

Trade effluent is 145 KLD and activated sludge ETP is proposed which is a two stage biological treatment.

Waste water will be generated from the landfill and compost leachate in addition to domestic waste water from drinking and cooking etc.
Status of Consent: Consent to Establish issued on 18.01.2011 and valid upto 17.01.2011.
Status of authorization: Applied for Authorization under MSW Rules, on 10.01.2011

Status of Consent: Applied for Consent to Operate on 21.04.2011

Status of Environmental Clearance: EC granted by MoEF, GOI on 25.10.2010.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
No Action.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 09.08.2010:
Seek application for CTE.

Action taken/ Status after the meeting held on 09.08.2010

A letter has been issued on 03.09.2010 seeking application for Consent to Establish and the unit has submitted application for CTE

 Applied for Authorization under MSW Rules, on 10.01.2011
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 11.01.2011:

Consent to Establish is granted. Application for Authorization under MSW Rules will be considered at the time of operation of the unit.

Action taken/ Status after the meeting held on 11.01.2011:

1. Consent to Establish was issued on 18.01.2011.

2. Applied for Consent to Operate on 21.04.2011

3. Consent to Operate has been issued on 02.06.2011for a period of 2 months as per the decision on file on submission administratively.

4. Authorization under MSW (Management & Handling) Rules, 2000 has been issued 03.06.2011for a period of 2 months as decided by the authority on file.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 10.06.2011:

Decision, taken on file, to issue CTO under Water and Air Acts and authorization under MSW Rules, 2000 for two months ratified.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

Annexure-6

LAEC agenda Part -1
Installation of CETP at Patparganj Indl Area:

Decision taken in CMC (MSW) meeting held on 28.02.08:
As reported by DSIDC officials, untreated effluent of Patparganj Industrial Area is being treated by PWD. An inspection is to be done of Patparganj Industrial Area to check whether PWD is treating domestic waste, by SEE (MSWM). A letter may be sent to PWD in this regard, and inspection report submitted in file in 15 days.
Action by: MSWM Cell

Action Taken Report:
Letter has been issued to SE (PWD) on 25.03.05 (C/174).

The area has been inspected by SEE (MSW) along with officials from DSIIDC and Industry Department on 11.04.08. The inspection report has been forwarded and Chairman, DPCC desired that this may be discussed in CMC (MSW). A list of Industries who has applied for the consent under orange category in DPCC from Patparganj Indl. Area (PIA) was also sent to DSIIDC on 10.04.08. Sewerage plan of Patparganj Industrial Area has been received from PWD. Officials from concerned departments have been called in the meeting.
Decision taken in CMC (MSW) meeting held on 20.04.2010

Issue reminder D.O. letter from MS, DPCC to COI, seeking clarification regarding installation of CETP at Patparganj.

Action Taken Report:
A  reminder D.O. letter from MS, DPCC to COI, seeking clarification regarding installation of CETP at Patparganj was issued on 02.06.2010 
Decision taken in CMC(MSW) meeting held on 09.08.2010

Issue D.O letter from Chairman, DPCC to COI, seeking clarification regarding installation of CETP at Patparganj

Action Taken Report:
A reminder D.O. letter from MS, DPCC to COI, seeking clarification regarding installation of CETP at Patparganj was issued on 24.09.2010 

Decision taken in CMC(MSW) meeting held on 11.01.2011

Call a meeting of DSIDC and COI officials at the level of Chairman, DPCC

Action Taken Report:
Meeting has been scheduled on 24.03.2011, minutes of the meeting has been circulated.

Installation of CETP at Patparganj Industrial Area: The officers present from the office of Commissioner Industries & Delhi State Industrial & Infrastructure Development Corporation (DSIIDC) presented the facts that industries in Patparganj Industrial Area are using the Ground Water as a source of water and according to the study conducted by IIT, the area generates only 1.0 to 1.5 MLD of waste water. Nature of the waste is mainly domestic in nature as there are very less effluent discharging industrial units. However, heavy metal in small quantity may be there & treatment of heavy metals will be well taken by individual ETPs. After reviewing the facts Chairman, DPCC was felt that CETP will be required separately for treating the effluent and it was suggested that, an option may be explored to have a modern low cost small CETP for adequate treatment for the effluent generated by the industries located in Patparganj Industrial Area.   
Decision taken in CMC(MSW) meeting held on 10.6.2011:
Seek progress report on the decisions taken in the meeting dated 24.3.2011 taken by Chairman, DPCC.

Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell

LAEC agenda Part -2
Removal of encroachments on the roads of WIA:

Decision taken in CMC (MSW) meeting held on 28.02.08:
A letter will be sent to Sh. Naresh Kumar, Additional Commissioner, MCD, regarding removal of Encroachment on the roads of DSIDC sheds, so that work of conveyance system may be completed by DJB within two months. The copy of this letter will be sent to Managing Director, DSIDC by MS, immediately.

Action Taken Report:

Letter has been issued to Sh. Naresh Kumar, Additional Commissioner, MCD on 25.03.08 with a copy to MD, DSIIDC (C/177). Reply is awaited. Representative from MCD & DSIIDC called for the meeting.

Decision taken in CMC(MSW) meeting held on 20.04.2010:
Issue reminder D.O. letter from MS, DPCC to Commissioner, MCD with a copy to Pr. Secretary (UD) enclosing copies of previous letters.

Action Taken Report:

 D.O. letter was issued on 02.06.2010. Reply awaited

Decision taken in CMC(MSW) meeting held on 09.08.2010:
Issue reminder D.O. letter from MS, DPCC to Commissioner, MCD with a copy to Pr. Secretary (UD) enclosing copies of previous letters.

Action Taken Report:

D.O. letter issued on 27.09.2010 with a copy to Principal Secretary (UD).

Reply awaited.

Decision taken in CMC(MSW) meeting held on 11.01.2011:
Call a meeting of Zonal Chief Engineer and Superintendent Engineer of MCD at the level of Member Secretary 

Action Taken Report:
Meeting held on 17.02.2011.Officials attended briefed the issue. It was assured that the encroachment will be removed and report in this regard will be filed to DPCC. Report not received so far
Decision taken in CMC(MSW) meeting held on 10.6.2011:
Inspection be carryout to check the present status.

Also, call a meeting of the concerned officers before Chief Secretary, GNCTD.
Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
SEE  EE 

DPCC   DPCC    Env. Deptt.    Member (Acd. Inst)   (MSW) MSWM Cell

LAEC agenda Part -3
Removal of encroachment by DDA in WIA:

Decision taken in CMC (MSW) meeting held on 28.02.08

A letter will be issued to the new Vice Chairman, DDA by Chairman, DPCC, enclosing a copy of the previous letter. File to be submitted immediately. 

Action by: MSWM Cell
Action Taken Report:
Letter has been issued to VC, DDA on 21.04.08 (C/217). Reply is awaited. Representative from DDA called for the meeting.
Decision taken in CMC(MSW) meeting held on 19.01.2010:
Issue D.O. letter to VC, DDA from Chairman, DPCC with copy to Secretary to LG, GNCTD and CS, GNCTD giving reference and enclosing copy of previous reference to take measures to prevent dumping of waste water and MSW. 

Action Taken Report:
D.O. letter to VC, DDA from Chairman, DPCC with copy to Secretary to LG, GNCTD and CS, GNCTD, issued on 23.03.2010. Reply awaited.

Decision taken in CMC(MSW) meeting held on 20.04.2010:
Issue reminder D.O. letter from MS, DPCC to VC, DDA with copy to Secretary to LG, GNCTD and CS, GNCTD giving reference and enclosing copy of previous reference to take measures to prevent dumping of waste water and MSW. 

Action Taken Report:
D.O. letter to VC, DDA from Chairman, DPCC with copy to P. Secretary to LG, GNCTD and CS, GNCTD, issued on 02.06.2010. Reply awaited

Decision taken in CMC(MSW) meeting held on 09.08.2010:

Issue reminder D.O. letter from MS, DPCC to VC, DDA. 
Action Taken Report:

D.O. letter to VC, DDA from Chairman, DPCC with copy to P. Secretary to LG, GNCTD and CS, GNCTD, issued on 27.09.2010.

Reply awaited

Decision taken in CMC(MSW) meeting held on 11.01.2011:
Call a meeting of concerned officers in the office of Chief Secretary, Govt. of NCT of Delhi.
Action Taken Report:
File submitted to the Office of chief Secretary seeking suitable date for meeting. File yet to be received.

Decision taken in CMC(MSW) meeting held on 10.6.2011:
Expedite the meeting of the concerned officers before Chief Secretary, GNCTD.
Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell
LAEC agenda Part -4
Construction of roads in WIA:

Decision taken in CMC (MSW) meeting held on 28.02.08:
MCD informed that all the work w.r.t. main circular roads & A Block in Wazirpur Industrial Area will be completed within the scheduled time of 6 months i.e. May, 2008. SEE may submit a monthly progress report on this in each CMC (MSW).

Action by: MSWM Cell

Action Taken Report:

Letter has been issued to DC (Rohini Zone), MCD on 25.03.08 (C/175). Reply is awaited. Representative from MCD called for the meeting.

Decision taken in CMC(MSW) meeting held on 20.04.2010:
Issue a letter to Commissioner, MCD for completion of roads in WIA.

Action Taken Report:

D.O. letter from Chairman, DPCC to Commissioner, MCD with a copy to Pr. Secretary (UD), GNCTD issued on 02.06.2010. Letter from Commissioner, MCD was received on 21.06.2010 stating that MCD has prepared a comprehensive action plan to cover all roads of WIA and its funding position

Decision taken in CMC(MSW) meeting held on 09.08.2010:
Issue a letter from Chairman, DPCC to Commissioner, MCD seeking status and time frame for completion of roads in WIA.

Action Taken Report:

A letter was issued on 7.10.2010 for seeking status and time frame for completion of roads in WIA. 

Reply awaited.

Decision taken in CMC(MSW) meeting held on 11.01.2011:
Call a meeting of DSIDC and COI officials at the level of Chairman, DPCC

Action Taken Report:

Meeting held on 24.03.2011 and minutes circulated.
Construction of roads in WIA: During discussion, MCD officials raised the problem of budget and also told that Central Road Fund (CRF) scheme has been disbanded, Chairman, DPCC asked to bring this matter to notice of Commissioner, MCD. Chairman emphasized on construction of roads and suggested to start this work on priority. It was also suggested that DSIDC and MCD should discuss the matter together and sort out if there are any problems in this regard.

No progress/action taken report received yet.
Decision taken in CMC(MSW) meeting held on 10.6.2011:
Seek progress report on the decisions taken in the meeting dated 24.3.2011 taken by Chairman, DPCC.
Chairman
M. S.
      Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC
DPCC    Env. Deptt.    Member (Acd. Inst)   
(MSW) MSWM Cell
Annexure – 7

Construction and Demolition waste facility:


The file was transferred by the BMW Cell to MSW Cell only on 09.6.2011 and so the issue was taken up as Table Agenda – 1. Application for consent to operate received on 19.01.2011. IL & FS, has not applied for authorization under MSW Rules, 2000.

Decision on 10.06.2011:

Ask the unit to apply for the authorization under MSW Rules, 2000. Also, an inspection be carried out to check the status of pollution control systems.

Chairman
M. S.
      Member     Prof. S.K Gupta     A.D      SEE
 EE 

DPCC      DPCC    Env. Deptt.    Member (Acd. Inst)  (MSW) MSWM Cell

Sanjay Motor Lorry, Seelampur:


As the applicant is collecting paper/card board waste from shopping malls and big commercial establishments and is reselling after segregation of the same. After detailed discussion, it was felt that the provisions of MSW Rules, 2000 are not applicable to the present activity.

Decision 10.06.2011:

Delete the item from the agenda for future meetings and make the application for authorization infructuous.

Chairman
M. S.
  Member        Prof. S.K Gupta
A.D
     SEE
 EE 

DPCC      DPCC    Env. Deptt.    Member (Acd. Inst)   (MSW)     MSWM Cell

