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1. Sh. J. K. Dadoo, Chairman, DPCC



- Chairman

2. Prof. S.K. Gupta , IIT, Delhi




- Member

3. Sh. K. Mahesh, Member Secretary, DPCC

- Member

4. Sh. B. Kumar, SEE, DPCC




- Member

5. Dr. Chetna Harjai, Scientist, Deptt. of Env., GNCTD
- Member 

6. E.E & AEEs of MSWM Cell



- Member

7. Sh. R C  Tewari, Dy. CE (E), DSIIDC Ltd. 
- Special Invitee

8. Sh. Sharat Kumar, EE (E&M), DSIIDC Ltd. 
- Special Invitee

9. Sh. A. K. Shrivastava




- Special Invitee

10. Sh. S.K. Dahiya, EE, DJB



- Special Invitee
11. Sh. V K Pahuja, ZE (NW) IV, DJB


- Special Invitee

12. Sh. S. K. Jain, AE/ LM/NZ, DDA


- Special Invitee
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Minutes of the 9th meeting of CMC (MSW) held on 12.05.2008 in the conference room of Chairman, DPCC

The list of participants attended the meeting including special invitees is enclosed.

The 9th meeting of CMC (MSW) held on 12.09.08 in the conference room of Chairman, DPCC and following decisions w.r.t. follow up action on the pending issues of the Local Area Environment Committee, were taken in the meeting:

Agenda- 1
	S. No.
	Decision taken in CMC (MSW) held on 28.02.08
	Action taken
	Decision taken in CMC (MSW) on 12.05.08

	A
	As reported by DSIDC officials, untreated effluent of Patparganj Industrial Area is being treated by PWD. An inspection is to be done of Patparganj Industrial Area to check whether PWD is treating domestic waste, by SEE (MSWM). A letter may be sent to PWD in this regard, and inspection report submitted in file in 15 days.
Action by: MSWM Cell
	Letter has been issued to SE (PWD) on 25.03.05 (C/174).

The area has been inspected by SEE (MSW) along with officials from DSIIDC and Industry Department on 11.04.08. The inspection report has been forwarded and Chairman, DPCC desired that this may be discussed in CMC (MSW). A list of Industries who has applied for the consent under orange category in DPCC from Patparganj Indl. Area (PIA) was also sent to DSIIDC on 10.04.08. Sewerage plan of Patparganj Industrial Area has been received from PWD. Officials from concerned departments have been called in the meeting.
	DSIDC has confirmed that they will get the feasibility study done following due procedures and submit the report to CMC (MSW), DPCC within 03 months including the quantum of total water generated in PIA. The  feasibility report shall also have the recommendation for transportation of waste water generated to Jhilmil CETP or construction of seperate CETP at PIA. 

	B
	1. DJB shall send the list of 30 units which have not paid the requisite fee for permission from DJB, for connection into conveyance system to DPCC with a copy to CETP Society, Wazirpur. In case industrial units do not pay the requisite fee, DPCC will pay the fee to DJB and recover from the units later as the urgency of connecting individual lines to the conveyance system is more important in pubic interest than the amount of Rs, 500/- charged to each unit by DJB. However, DJB will sanction the permission to industrial units immediately.

2. A letter will be sent to Sh. Naresh Kumar, Additional Commissioner, MCD, regarding removal of Encroachment on the roads of DSIDC sheds, so that work of conveyance system may be completed by DJB within two months. The copy of this letter will be sent to Managing Director, DSIDC by MS, immediately.

3. DSIDC has informed that the pump will be repaired within 15 days time. This may be confirmed in file.

Action by: MSWM Cell
	1. Letter has been issued to DJB on 01.04.08 (C/181). Reply is awaited. Further as per approval notices u/s 33(A) of water Act have been issued to 30 units on 04.04.08 & the list of 30 units were received from DJB. The status of notice issued and their replies is enclosed. Accordingly, 17 units have connected their sewer line to conveyance system, 5 units have taken necessary approval from DJB, 4 unit did not submitted their reply and notices received back undelivered from 2 units. No proper reply from 1 unit.
2. Letter has been issued to Sh. Naresh Kumar, Additional Commissioner, MCD on 25.03.08 with a copy to MD, DSIIDC (C/177). Reply is awaited. Representative from MCD & DSIIDC called for the meeting.
3. Letter issued to CE, DSIIDC on 25.03.08 (C/176). Reply received vide letter dated 31.03.08 (C/218) informing that three pumps are functioning at present but with the continuous low pH it can not be ensure how long pumps can sustain. Representative from DSIIDC & CETP society called for the meeting.
	Out of 30 units which have not responded so far are given one month final times after which necessary penal action under the Water Act will be taken. 
The concerned MCD officials Sh. Anil Mittal has confirmed that he will take a copy of the letter written to Addl. Commissioner, MCD and get the encroachment removed within 15 days.

CETP Society must confirm in writing why CETP was not functional on 04.04.2008 when DPCC laboratory inspected for waste water monitoring.  

	C
	A letter will be issued to the new Vice Chairman, DDA by Chairman, DPCC, enclosing a copy of the previous letter. File to be submitted immediately. 

Action by: MSWM Cell
	Letter has been issued to VC, DDA on 21.04.08 (C/217). Reply is awaited. Representative from DDA called for the meeting.
	The DDA official present is shifting the responsibility to the Engineering Wing, DDA. He is directed to ensure reply within 01 week. 

	D
	Construction of roads in WIA:

MCD informed that all the work w.r.t. main circular roads & A Block in Wazirpur Industrial Area, will be completed within the scheduled time of 6 months i.e. May, 2008. SEE may submit a monthly progress report on this in each CMC (MSW).

Action by: MSWM Cell
	Letter has been issued to DC (Rohini Zone), MCD on 25.03.08 (C/175). Reply is awaited. Representative from MCD called for the meeting.


	The MCD official present has confirmed that 3.5 Km road completed and remaining 6.5 Km will be completed by October, 2008.

	E
	Matter regarding illegal hazardous waste dumping sites: 
Reminder letters will be sent to the concerned officials.

Action by: MSWM Cell
	Reminder letter have been sent on 25.03.08. No reply received so far. Officials of the concerned departments have been called for the meeting.
	EE (MSWM) will visit all the 23 dump sites identified by M/s Ramky consultant and submit the factual report by next month for appropriate action under the HWM Rules. 


Action by: MSWM Cell

	
	Public notice has been issued on 08.03.08 for obtaining applications for the award. Three applications were received so far. A meeting of the committee for this purpose was also held on 23.04.08. Letter issued to special inspection team for inspection of above said 3 units.
	Call on next meeting of CMC (MSWM). 
	

	G
	Identification of industrial unit for developing as a model unit in the field of Hazardous Waste management :

One more public notice will be published in a Hindi Newspaper.

Action by: MSWM Cell
	One more public notice has been issued on 27.03.08. No response received so far again from the industry. Hence, Chairman (DPCC) has approved to drop this issue. 
	No action.

	H
	Matter regarding TSDF site, at Gumenhera:
1. Deputy Commissioner (South West) will hold a meeting on 03-03-2008 regarding TSDF site at Ghumanhera.

2. Shifting of Hazardous waste stored in Delhi to Kanpur or Udaipur has to be explored by MS continuously and reported to Chairman.

3. Draft Expression of Interest (EOI) for Hazardous Waste Site is to be prepared and put upon file.                                                                                             
Action by: MS / CMC-III


	As informed by Sh. Md. Arif, EE, CMC-III, there is no progress in the matter.
	MS to pursue with DSIIDC for Kanjawala land being acquired by DSIIDC for which Chief Secretary already given order in writing. 

	I
	Matter regarding gas supplies to WIA:
Matter to be followed up with reminders to the gas supplying company by MS.

Action by: MS / CMC-II
	A letter dated 19.04.08 received from IGL, wherein they requested for the list of industrial buyers in WIA for requirement of natural gas.
	The CETP Society confirmed that within 01 month that they will provide the list required by IGL for industrial buyers of natural gas. 

	J
	Matter regarding inspection of the units in WIA:
A meeting of NDPL officials may be called this month regarding the issue of disconnection of supply of electricity of water polluting units during night hours. Chairman has agreed for 18th March at 3:00 pm and accordingly it may be fixed.
Action by: MS / CMC-II
	Meeting with NDPL officials taken place. NDPL submitted its reply and the matter was discussed in CMC (Orange) meeting on 24.4.08 and it was decided that MS will speak to the officials of NDPL
	Meeting to be held in Chairman office with the two representatives of NDPL. 

	K
	Matter regarding electronic waste:
Sh. A.N. Singh, Scientist, Department of Environment along with the DPCC officials will prepare Expression of Interest (EOI) for electronic waste for five processes i.e. Collection & transportation, dismantling, extracting the valuable metal, recycling the valuable metal and disposal of the non recyclable metal and submit the file within 30 days.
Action by: Plg. Cell
	File of e-waste is under submission. Sh. A.N. Singh, Scientist, Department of Environment is preparing EOI with the help of consultant.
One EOI for study already prepared by Planning Cell & A.N. Singh, Scientist jointly 
  
	Transaction Adviser to finalized EOI. MS to pursue. 

	L
	Matter regarding use of jute bags in place of plastic bags:

Member Secretary to follow up this issue and official from Planning Cell will go to Kolkata to expedite this matter. 

Action by: Plg. Cell
	Sh. S. K. Goyal visiting Kolkata. The file is under process for visiting Kolkata from 13-15 May, 2008.
	No action. 


Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
Compost Plant of Municipal Corporation of Delhi at Okhla
Name of the agency: Municipal Corporation of Delhi, O/o the Engineer in Chief, Town Hall, Delhi-6

Particulars of the project: 

Revival of the Compost Plant of Municipal Corporation of Delhi at Okhla, Delhi (The compost plant at Okhla is existing plant of MCD which stopped operation in 1994 and MCD now has handed over this plant to IL & FS for revival of up gradation).   

Status of Consent: 

Consent to establish has been issued on 29.01.08. 

Status of authorization under MSW Rules: 

Applied for authorization for setting up and operation of waste processing facility on 20/11/07 (C/1 to 67).

Details of the project: 

· Processing technology is composting through open
air aerobic window composting method.

· Quantity of waste to be processed is 200 TPD.

· Investment on the project is Rs.6.2 crores.

· Quantity of waste to be disposed per day is 40 TPD.

· Plot Area is 29000 sq m and Built up area- 4000 sq m 

· Sanctioned Power Load – 280 KW

· Revival period the compost plant will be start on 1 March, 2008.

· Water consumption for domestic is 2000LPD &  for processing  is  20,000 LPD

· Quantity of domestic waste generated is 1500 LPD and leach ate to be recycled in composition process

· 100 KVA DG Set proposed to be installed.

· Concession Agreement between MCD and IL & FS is placed at (C/71 to 103).

Decision taken in meeting held on 09.01.08:

· Consent to Establish granted.

· As regard the authorization under MSW Rules, the letter will be sent to the other bodies as mentioned in MSW Rules for their views/NOC and for site clearance to the concerned land owning agency and the copy of these letters will be sent to the project proponent also.
Action taken/ Status after the meeting held on 09.01.08:

· Consent to establish has been issued on 29.01.08. 

· As decided letter was also issued on 29.01.08.  
· Decision taken in meeting held on 28.02.2008:

No action at present.

Status:
Comments have been received from Town & Country planning Organisation, UD, Govt. of India. They suggested 7 modifications in the project (C/126).

Decision of Consent Management Committee in its meeting dated 12.05.2008:
Comment received from Town & Country Planning Organization, UD, Govt of India be forwarded to IL&FS and a reminder should go to others. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM
Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
Compost Plant at Tikri Khurd/ Khampur 
Name of the agency: M/s Spiral Services, New Sabzi Mandi, Azad Pur, Delhi
Particulars of the project: 

Up-gradation of the A.P.M.C. Compost Plant at Tikri Khurd/ Khampur, G.T. Karnal Road, Delhi-40 (Existing plant inaugurated by Delhi C.M. on 17.01.02)
Status of Consent: 

· Consent to establish has been issued on 29.01.08. 

· Applied for consent to operate on 04.03.08.

Status of authorization under MSW Rules: 

Applied for authorization for setting up and operation of waste processing facility on 20/11/07 (C/1-27 and C/30-34).

Details of the project: 

· Processing technology is composting through open air aerobic window composting method.

· Quantity of waste to be processed is 200 TPD.

· Investment on the project is Rs.1.6 crores.

· Quantity of waste to be disposed per day is 30 TPD.

· Plot Area is 24000 sq m.

· Built up area- 1000 sq m

· Sanctioned Power Load – 5 KV

· Proposed to be commissioned from March, 2008 (earlier unit exist since 17.01.02).
· Water consumption for domestic is 1440 LPD &  for processing  is  5000 LPD

· Quantity of domestic waste generated is 1000 LPD & having 2 septic tanks and leach ate to be recycled in composition process.
· No DG Set proposed to be installed.

· Agreement between APMC and Spiral Services is placed at (C-/3 to 11).

Decision taken in meeting held on 09.01.08:

· IL&FS has sent the letter by Fax wherein it is mentioned that IL&FS is working with M/s. Spiral Services in managing the compost facility at Tikkri. In the same letter they have also mentioned that they would provide the following to the existing compost plant i.e. facilitate expansion of plant, purchase and supply of equipment, finance and facilitate accrual of CDM benefit, provide technical assistance in operation of plant and off take composite produced in the plant. In view of this, consent to Establish granted.

· As regard the authorization under MSW Rules, the letter will be sent to the other bodies as mentioned in MSW Rules for their views/NOC and for site clearance to the concerned land owning agency and the copy of these letters will be sent to the project proponent also.
Action taken/ Status after the meeting held on 09.01.08:

· Consent to establish has been issued on 29.01.08. 

· As decided letter was also issued on 29.01.08.  
· Decision taken in meeting held on 28.02.08:
No action at present.

Status:
· Applied for consent to operate under Orange category on 04.03.08. 
· Views/ Comments/ NOC were received only from Town and Country Planning Organization, Ministry of U.D. (C/44- 45) asked before issued of authorization under MSW, Rules. Views/ Comments/ NOC are still awaited from Air Force, DDA and Central Ground Water Board.
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Decision of Consent Management Committee in its meeting dated 12.05.2008:
Comment received from Town & Country Planning Organization, UD, Govt of India be forwarded to M/s Spiral Services / IL&FS and a reminder should go to other. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM
Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
Modern Poultry & Egg market at Ghazipur, New Delhi.

Name of the agency: M/s Delhi Agriculture Marketing Board, 9, Institutional Area, Pankha Road, Janakpuri, New Delhi-110058.
Particulars of the project: Modern Poultry & Egg market at Ghazipur, New Delhi.
Status of Consent: 

Applied for consent to establish under Air & Water Acts vided ID. No. 24811 dt. 24.01.08 (C/1-98)

Details of the project: 

· Product is dressing of Poultry birds- 48 lakhs birds/ month. 

· Raw material is Poultry birds- 576 lakhs/ annum. 

· Proposed Investment on the project is Rs.133.5 crores.

· Quantity of waste to be disposed per day is 30 TPD.

· Total Plot Area is 60200 sq m and Built up area- 48160 sq m

· Sanctioned Power Load /power required– 2925 KW
· Proposed to be commissioned from March, 2010.
· No of workers: 

a) During construction phase – 100 b) During operational phase-   25

· Water consumption:

Domestic - 91000 LPD, 
Industrial cooling/ boiler feeds - 92000 LPD processing   - 1120000 LPD,
Other (Gardening) – 108000 LPD
· Quantity of domestic waste generated is 80000 LPD and Industrial is 1100000 LPD

· Proposed Effluent Treatment Plant of 1200 KLD with tertiary treatment & UV Irradiation and reuse in flushing, HVAC, DG, Horticulture (C/52 of the file). A STP of 200KLD is also proposed (C/58 of the file). 
· DG Sets proposed to be installed – 2 X 1000 KVA + 2 X 625 KVA.
· Land allotted by DDA for this purpose (allotment letter at C/4-6)  
Remarks:

As per the provisions of EIA notification dated 14.09.06 the following construction projects are to be required Environmental Clearance from MoEF:

a) Building and Construction Projects having built up area ≥ 20000 sqm and < 150000 sqm of built up area. 

b) Townships and Area Development Projects having covering an area ≥ 50 ha and or built up area ≥150000 sqm.   
· Decision taken in meeting held on 28.02.08:
Letter to be sent for EIA clearance indicating that if they have any doubt they may contact the EIA cell of MOEF and the copy of this letter will be sent to EIA Cell of MOE&F.

Action taken/ Status after the meeting held on 28.02.08:

Letter issued for Environmental Clearance on 24.03.07. Environmental clearance/ reply are still awaited from the unit or MOEF.

Decision of Consent Management Committee in its meeting dated 12.05.2008:
Issue reminder letter for Environmental Clearance. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM
Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008
Municipal Waste Complex at Gazipur Bio-gas Plant Site

Name of the agency: M/s New Delhi Waste Processing Company Ltd.
Particulars of the project: 

· Setting up of integrated Municipal Waste Complex at Gazipur Bio-gas Plant Site, Gazipur. 

· The capacity of the project would be 1200TPD. The treatment/ processing of the MSW would be based on DST-TIFAC technology of mixed municipal waste to RDF Fluff preparation and bio-gas generation from the organic waste. The power generation would be 10-12 MW.

 Status of Consent: 

Applied for consent to establish under Air & Water Acts on 22-06-07 & Consent to establish has been issued on 03.07.07.
Status of authorization under MSW Rules: 

Applied for authorization under MSW Rules on 30.03.07 and Authorization under MSW Rules was also issued on 03.07.07.
Action regarding clearance from other departments: 

Letter issued on 10.05.07 to the operator of the facility to submit:

· Detailed project report.

· Site clearance certificate from the land owning agency.

· EIA clearance from Ministry of Environment & Forests, Government of India.

· View of Air Force Base Station, Town and Country Planning, Department of UD, Govt. of India etc.

Status:
· Detailed project report is not received.

· Site clearance certificate from the land owning agency is not received.

· EIA clearance from Ministry of Environment & Forests, Government of India is not received.

· View of Air Force Base Station, Town and Country Planning, Department of UD, Govt. of India etc are not received.
· Decision taken in meeting held on 26.06.07:

During the meeting it is decided that conditional Consent to Establish under Air and Water be issued as done in case of Timarpur Incineration Plant site and similarly conditional Authorization under MSW Rules be also issued. 

Action taken/ Status after the meeting held on 26.06.07:

· Consent to establish has been issued on 03.07.07. 

· As decided Authorization under MSW Rules was also issued on 03.07.07.  

Other remarks:

· Reminder letter has been issued on 25.02.08 to the operator for desired information.

· Reminder letter has also been issued on 25.02.08 to Hindon Air Force Station Base, Palam Air Force Station Base, Department of Town and Country Planning, Central Ground Water Board and Deputy Commissioner (East) for obtaining views/ comments /NOC regarding the project. 
· The comments has been received from Department of Town and Country Planning, UD vide letter dated 19.02.08 (C/337).

· Air Headquarter has issued NOC vide letter dated 26.07.07 (C/431).

· As per letter dated 24.04.08 of Deputy Director (LL), DDA addressed to General Manager, Delhi Power Company Ltd., The matter has been examined it is informed that as per MPD-2021, utility is permitted in all land use zones as intimated by Planning Department of DDA (C/436).

Contd..2/-
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· Public hearing for Environmental Clearance has been conducted on 04.03.08 & proceeding is placed at (C/429). A copy of the proceeding has been forwarded to MOEF on 10.03.08 by EIA Cell.  
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Comment received from Town & Country Planning Organization, UD, Govt of India be forwarded to IL&FS and a reminder should go to others. 
Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM
Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
Delhi Food Processing Complex (Meat) at Ghazipur, Delhi

Name & Address: Municipal Corporation of Delhi, Delhi Food Processing Complex (Meat) at Ghazipur, Delhi 

Correspondence Address: MCD Department of Veterinary Services, Room No. 56, Town Hall, Delhi-06
Status of Consent: 
Applied for consent to establish under Air & Water Acts on 02-06-2005

Activity: Slaughter House (1.75 MLD)

Status: 

Applied for consent to establish under Air & Water Act on 02-06-05 EIA report not submitted alongwith the application.  The case was earlier dealt by EIA Cell and matter was sent to Ministry of Environment & Forest, since issues related to EIA notification and Hon’ble Supreme Court Orders are also involved in this case, letter was also issued on 30-08-07 by EIA Cell regarding seeking information about the Environment clearance by MOEF however reply to the said letter has not been received so far. As directed inspection was conducted by a team comprising of DPCC officials and Dr. T.K.Joshi, Head, CEOH on 24-08-07(Copy enclosed).  During the inspection the civil construction work as well as fixation and erection of machineries was going on.  The work of construction of ETP was also going on. In the vicinity the rendering plant is also coming up and an ETP was also seen.  The inspection of the facility could not be done since no responsible person at the site.  Details of the ETP submitted with the project report mentions about Physico Chemical Treatment.  Since waste water generated from both the section (i) Slaughter House (ii) Rendering Plant has mainly organic waste which is biodegradable, therefore Physico Chemical Treatment should be avoided since as per HW Rules it will be generating Hazardous Waste.  Besides above unit should also go for better sludge handling mechanism Letter was issued followed by the reminder letter as decided by the BMW Committee & Reply along with Report on ETP/ Rapid EIA Report received. MOEF Clearance yet to be received.

Decision Taken by the Committee on 04.10.07: 

Report of the inspection team was perused by the Committee. A letter may be issued to concerned officer in M.C.D. for furnishing detailed information on the construction of E.T.P. and its likely completion date and copy of letter to be sent to Sh. Ravi Das Engineer-in-Chief in M.C.D. 

Action Taken Report
w.r.t. meeting on 04.10.07:

Letter issued. Reply not received.

Decision Taken by the Committee on  15.11.07: 

Reminder Letter to be issued.

Action Taken Report w.r.t. meeting on 15.11.07:


Reminder letter issued, Reply along with Report on ETP/ Rapid EIA Report received. MOEF Clearance yet to be received.

Decision Taken by the Committee on 15.01.08: 

MS to Speak to MOEF & Expedite EIA clearance. To be taken up in the next meeting.
· Decision taken in meeting held on 28.02.2008:

Fresh inspection is to be conducted. 
Action taken/ Status after the meeting held on 28.02.08:

Proposed Slaughter House has been inspected on 26.03.08. During the visit Dr. Om Prakash (Manager) and Sh. Alok Tiwari (AE) were also present from Municipal Corporation of Delhi. The following are the observations:

1. The erection and installation of plant & machinery was in progress. As informed that the work of the Slaughter House will be completed & handed over to MCD by 20.05.08, as assured by the contractor in the court.  
Contd…2
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2. Work of installation of ETP for the Slaughter House was under progress and civil & mechanical work is almost completed.  

3. The effluent treatment plant consisting of Physico-chemical, Anaerobic followed by Aerobic processes. 

4. Alum, Poly-Electrolyte, NaOH, HCl, & Sodium Hypo-Chloride will be used in treatment process and dosing tanks have been provided near the reaction tanks. Hence, the sludge generated from the ETP will be in hazardous nature in view of the inspection team. 

5. In the project report, the unit has mentioned that the dewatered sludge will be collected in tractors & disposed off suitably. During inspection it was found that the unit has not taken any steps for compliance of HWM Rules.

6. A sump is constructed in the Slaughter House premises, to collect the effluent and same will be pumped through pipe lines to the ETP, located about 300m away from the Slaughter House. 

7. As informed that the treated effluent will be discharged into the open drain leading to Hindon drain, however, in the later stage it is also proposed to use the treated effluent for gardening and other greening purpose, after closing of adjacent Gazipur Municipal Solid Waste Disposal site. 

8. A rendering plant is also installed near the Slaughter House for processing of dead animal to prepare fish food etc. The rendering plant was found non operational condition; however, as informed that this rendering plant was earlier operated for around 15 days for trial run. 

9. A separate ETP is installed for this rendering plant and found filled with waste water in septic condition. ETP was not in operation. 

10.  Bio gas will be generated from the anaerobic process of ETP and same will be burned in the complex. There is no provision for utilization of biogas.  

11.  As also informed that the application for Environmental Clearance for this Slaughter House & rendering plant is under consideration by Ministry of Environment & Forest. Environmental Clearance will be submitted to DPCC after obtaining it.  
Decision of Consent Management Committee in its meeting dated 12.05.2008:
(i) Inform the unit about point no. 5. The ETP will be based on physiochemical process therefore there will be generation of hazardous waste. Unit may be asked to apply for authorization under HWM Rules. (ii) Unit to submit Environmental Clearance as soon as they obtained. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM

Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
Badarpur Thermal Power Station
Status of Consent: Consent issued on 27.07.2007 and valid up to 21.03.2010.

Action Taken:

This power station was also inspected by Zonal office Lucknow of CPCB on 23.08.07 & observed that particulate matter emission from unit II & V was within the limit. They recommended:

· BTPS should install ash pond effluent recirculation system.

· BTPS should install dedicated fly ash collection system.

· Ash dyke should be designed to withstand the hydraulic load of ash while raising its height, since area downstream of ash pond is densely populated.

- CPCB has desired that BTPS takes majors to implement the above recommendations within a time frame agreed mutually and asked to submit time targeted Action Plan & ATR.
Decision taken in meeting held on 19.10.07:

A letter may be issued to General Manager to comply with CPCB directions given during inspection by CPCB on 23.8.07. This compliance must be done by 31.12.07. 

Action taken/ Status w.r.t. the meeting held on 19.10.07:

· Letter issued on 5.11.07 communicating above decision. 

· No reply received so far.

Decision taken in meeting held on 09.01.08:

MS to speak to the concerned General Manager. The deficiencies noted by the inspection team of CPCB have not been corrected and not replied to. Letter be issued with the last opportunity giving to the unit to comply with the CPCB directions during inspection and complied with it fully.

Action taken/ Status w.r.t. the meeting held on 09.01.08:

A last opportunity letter issued on 31.01.08. A reply dated 28.01.08 was received from the power plant (C/327-328 of the file). Power Plant submitted that:

1. Regarding ash pond overflow recycling:

Corporate Engg., NTPC has been conducted for exploring and conducting a techno-economic feasibility study regarding the installation of this system.

2. Installation of dry ash collection system at plant:
The Dry Ash Extraction and Transportation System (DAETS) for 2X 210 MW of BTPS has already been awarded and is in execution stage. For 3X 95 MW units also there is a proposal of DAETS and for that the talks are going on with NTPC Vidyut Vyapar Nigam (NVVN) Ltd.

3.  Regarding ash dyke design aspect to withstand the hydraulic load while raising its height:
All the necessary precautions have already been taken by Corporate Engg., NTPC in the design aspect of ash dyke raising.

The above said reply has been forwarded to CPCB vide letter dated 11.02.08 after necessary approval on file. 
· Decision taken in meeting held on 28.02.2008:

Letter to be issued bearing the directions for meeting the standard of Particulate Matter of 50 mg/Nm3 along with the copy of the minutes wherein it was decided that the standard for Particulate Matter has been made stringent of 50 mg/Nm3. In case high emission is caused due to high ash content in coal, the ash content may be reduced in the fuel (coal).
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Action taken/ Status w.r.t. the meeting held on 28.02.2008:

· Letter issued to BTPS on 24.03.08 to meet the standard of 50 mg/Nm3 for Particulate Matter. 

· They informed that-  “Comprehensive renovation and modernization package specification for improvement in ESP efficiency to achieve emission <50 mg/Nm3 in 2X210 MW units has been finalized at an estimated cost of Rs 40 crores and expected date of NIT for this package is by the end of June, 2008. Further to meet the MOEF guidelines to use coal having ash less than 34% on annualized average basis, the following action have been taken:-

Use of imported coal having very ash ~8% started at BTPS since Jan. 2008. This low ash imported coal is being blended with high ash coal of BCCL/ CCL. The quantity of low ash coal has been imported till date is around 1.00,000 MT”.

· BTPS has not submitted any Comprehensive renovation and modernization package specification for improvement in ESP efficiency to achieve emission <50 mg/Nm3 in 3X95 MW units.

· BTPS has also not submitted any time bounded programme to achieve emission <50 mg/Nm3.

Decision of Consent Management Committee in its meeting dated 12.05.2008:
In case of two units considered for upgradation, let them confirm the status in next CMC. As regard three remaining units, issue reminder for their response. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM
 Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
I.P. Thermal Power Station

Status of Consent: 
· Consent issued on 19.03.07 and valid up to 27.04.08.

· Applied for Renewal of consent on 17.04.08
Action Taken:

This power station was also inspected by Zonal office Lucknow of CPCB on 20.08.07 & observed that particulate matter emission from unit 3 & 5 was exceeding the limit. They recommended:

· IPTPS should adopt better ESP maintenance practices and ash evacuation system for controlling the emission of particulate matter.

· IPTPS should also take necessary action for better ash pond management to maintain the concentration of suspended solids within the prescribed limit.

· IPTPS should improve over all housekeeping immediately.

· CPCB has desired that IPTPS takes majors to implement the above recommendations within a time frame agreed mutually and asked to submit time targeted Action Plan & ATR.

Decision taken in meeting held on 19.10.07:

A letter may be issued to General Manager to comply with CPCB directions given during inspection by CPCB on 20.8.07.This compliance must be done by 31.12.07. 

Action taken/ Status w.r.t. the meeting held on 19.10.07:

· Letter issued on 5.11.07 communicating above decision. 

· No reply received so far.

Decision taken in meeting held on 09.01.08:
MS to speak to the concerned General Manager. The deficiencies noted by the inspection team of CPCB have not been corrected and not replied to. Letter be issued with the last opportunity giving to the unit to comply with the CPCB directions during inspection and complied with it fully.
Action taken/ Status w.r.t. the meeting held on 09.01.08:

Replies dated 07.01.08 was received from the power plant (C/243-252 of the file). Power plant submitted that:

1. Thermal Power Station should adopt better ESP maintenance practices and Ash evacuation system for controlling the emission of particulate matter:-



DGM (Opr.) IPS stated that the test results of online monitoring/stack (ESP results) unit wise as furnished by Mgr (ESP) are well within the prescribed limit of 50 mg/Nm3. The test results unit-wise are attached as Annexure-I at C/247-249. On examination of these results the stack emission for unit no. 3 was not meeting the prescribed limit of 50 mg/Nm3. In the results sheet it is mentioned that only old ESP was an operation and new ESP installed accidentally failed down and under reconstruction yet. The methods/Practices adopted for ESP maintenance, submitted by the power plant may be seen at Annexure-II(C/246). He has also submitted that Segregating valves are installed on ESP Hoppers of Unit No. 5 and will be installed gradually on other units. MoU with Cement manufacturers were signed for dry ash collection directly from ESP Hoppers.

2. Thermal Power Station should also take necessary actions for better ash pond management to maintain the concentration of suspended solids within the prescribed limit:-


DGM (Opr.) IPS stated that the test results in respect of TSS of the effluent of Ash Pond as furnished by Mgr (Civil) are well with in the prescribed limits. The ATR enclosed as Annexure-III(C/245). He has also stated that in view of closing of I.P. Station by the year 2010, the action for zero discharge at Ash pond has been dropped being costly affair.
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3. Thermal Power Station should improve overall housekeeping:-

The Power Plant submitted that:
a. The area wise house-keeping in respect of water channel/Drain cleaning of B-Channel for maintaining proper flow of sludge / Ash slurry up to DW water tank, cooling water channel, coal mill channel, Ash slurry channel are being regularly maintained through Annual Maintenance Contract for reusing the decanted water for ash transportation.

b. The housekeeping for cleaning of operation floor area at ash pond, Boiler furnace bottom, coal mill reject is also being carried out through separate Annual maintenance contract for suppression of the fugitive dust.

c. Besides above, the activities for disposal of old scrap / waste material from the I.P. site are also being perused with D&R Department and the disposal of old/scrapped cooling towers Units No. 1 are already in hand to keep up the good housekeeping at the plant.
The above said reply has been forwarded to CPCB vide letter dated 11.02.08 after necessary approval on file.

· Decision taken in meeting held on 28.02.2008:

Letter to be issued bearing the directions for meeting the standard of Particulate Matter of 50 mg/Nm3 along with the copy of the minutes wherein it was decided that the standard for Particulate Matter has been made stringent of 50 mg/Nm3. In case high emission is caused due to high ash content in coal, the ash content may be reduced in the fuel (coal).

Action taken/ Status w.r.t. the meeting held on 28.02.2008:

· Letter issued to IPTPS on 24.03.08 to meet the standard of 50 mg/Nm3 for Particulate Matter. 
· A reply dated 01.05.08 received from IPTPS along with data of online monitoring w.e.f. 15.02.08 to 16.03.08. This data is not for all the days between this period and meeting the prescribed limit of 50 mg/Nm3 except a result of unit for on 14.03.08, which is 57 mg/Nm3. The power plant also informed that “in case of new ESP of Unit# 3 which fell accidentally is still under re-erection, ash evacuation system of new ESPs are also under final commissioning stage to get  improved results, stack emission with 50 mg/Nm3 in all Units”. 
· Noise monitoring report for DG set is not meeting the prescribed standards.
· DPCC monitoring reports show that all the operational ducts of this power station are not meeting the standard of 50mg/Nm3 for particulate matter except in duct of unit no. IV on 12.12.07. The Particulate matter in the stacks as per last six DPCC monitoring report are as under:
	S. No.
	Date of monitoring
	Particulate matter in duct of (in mg/Nm3  )

	
	
	Unit No.- II
	Unit No.-III
	Unit No.-IV
	Unit No.-V

	1
	03.10.07
	#
	#
	86
	#

	2
	16.11.07
	96
	89
	51
	#

	3
	12.12.07
	82
	69
	45
	#

	4
	28.01.08
	#
	103
	78
	#

	5
	26.02.08
	80
	101
	124
	#

	6
	19.03.08
	142
	76
	82
	#


# Shut down/ under maintenance.
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Decision of Consent Management Committee in its meeting dated 12.05.2008:

Due to installation of new ESP with unit no. 3, after commissioning the result will improve for unit no. 3 only. There is no proposal to improve efficiencies of other three remaining units. Reminder should be issued. Noise monitoring of D.G. Set is also not meeting the prescribed limit. Therefore, they may be asked to take adequate measures to have noise emissions within the limit. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM
Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
Rajghat Power Station

Status of Consent: Applied for “Consent to Operate” on 30.06.2004.

Action Taken:

· Letter issued to Pr. Secretary (Power) on 17.07.2007.

· The unit has replied that Ministry of Power, GNCTD has taken a decision for closing the coal based power plants in near future. A request has been made that as huge funds are required for installation of ETP, permission may be given that water is used for transporting fly ash to ash ponds. 

· This power station was also inspected by Zonal office Lucknow of CPCB on 21.08.07 & observed that untreated effluent (TSS- 198 mg/l) is being discharge into to river. They recommended:

· Adequate waste water treatment plant should be provided.

· An interrupted access to ash pond area should be provided.

· CPCB has desired that RTPS take measures to implement the above recommendations within a time frame agreed mutually and be asked to submit time targeted Action Plan & ATR.

Decision taken in meeting held on 19.10.07:

A letter may be issued to General Manager to comply with CPCB directions given during inspection by CPCB on 21.8.07. This compliance must be done by 31.12.07. 

Action taken/ Status w.r.t. the meeting held on 19.10.07:

· Letter issued on 5.11.07 communicating above decision (C/353). 

· Though reply is awaited, a letter dated 29.12.07 (C/355) received indicating that revised proposal for installation of low cost water treatment plant to utilize waste water in ash handling plant is under consideration. RPH has also initiated the following works : 

· Cleaning of existing station drain pit about 6m diameter and 6m deep which was already available for treating the station drain water for decantation and action have been initiated for new pipes to connect and pumping the decanted water to ash pump water tank to reuse for transporting ash slurry to ash pond meeting the proposal of DPCC in the letter of the year 2004. 

· Submersible pump installed to reuse backwash water of the filters at WTP and going to drain also reduced.

· Piping connection is almost in final stage for sending the sludge slurry water from WTP (neutralization pit) to ash pond. Thus the discharge at station drain will be further reduced substantially.

· RPH has not submitted their compliance report in respect to the letter dated-5.11.07.  However requested for issuing consent to operate.

Decision taken in meeting held on 09.01.08:

MS to speak to the concerned General Manager. The deficiencies noted by the inspection team of CPCB have not been corrected and not replied to. Letter be issued with the last opportunity giving to the unit to comply with the CPCB directions during inspection and complied with it fully.
Action taken/ Status w.r.t. the meeting held on 09.01.08:

Replies dated 07.01.08 and 08.01.08 were received from the power plant (C/365-367 of the file). Power plant submitted that:

1. Regarding adequate treatment  to the effluent through station drain into the river, the action taken are;

a. One pump alongwith its discharge line are laid and already started reusing back wash water of he gravity filters as inlet to the Aerator (Clarifier) and thus reduced consumption of water and consequently effluent quantity in station drain. Procurement action for one additional pump is also in process to have permanent arrangement.
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b. Needful discharge line piping has been laid from sludge slurry water pumps (clarifier) and connected to the Ash Surry Line and sludge being discharged to the Ash pond thus reducing also the effluent quantity to the station drain.

c. The installation of pumps and lying of discharge pipelines up to the ash pump water tank will be completed by the end of March, 2008. The decanted water of the station drain pit will be utilized for transportation of fly ash in slurry form to the ash pond as per advice of DPCC.


In the meantime time, the above said station drain pit having diameter of 6 meter and depth of 6 meter meant for decantation have been cleaned after removing sludge deposited.


The effluent from various plants including balance effluent from WTP (Neutralization Pit) will be collected in this cleaned station drain pit from where the decanted water be reused for transportation of ash slurry to the ash pond and thus virtually there will be no effluent discharge to river through station drain.

2. Un- interrupted access to ash pond-area – Reg.

The grass/ wild bushes grown in the area during monsoon has been cut and the needful repair of the roads has been done to remove the interruption.
Recommendation of CPCB for dry ash collection –Reg.

Ash Silo Systems have been revived and dry fly ash collection is being done by the cement manufacturer (about 1000 MT/month).

3. Regarding bringing down the particulate matter emission;

Regulation of Bapcon Control System and Auto Rapping System is being done regularly for better operation of ESP fields; attending nozzles of hydro vector and leakages etc. in the ash evacuation system; scheduling have been planned to wash/ clean the ESP insides; straightening/ adjustment of gaps between emitting electrodes and collecting plates as per the recommendation of OEM; replacement of segregating valves & solenoids are being done during shut down to get the maximum efficiency of the combustion of fuel also regulated and use of furnace oil is being minimized to bring down the particulate matter emission through stack well within the permitted limit.

4. Regarding Zero discharge by reusing ash pond overflow water:
The scheme for reusing decanted water from ash pond overflow was initiated but kept in abeyance for some period with the instructions received from Ministry of Power, GNCTD to avoid excess O&M expenditure for the coal based power station like RPH and IPStn. Which are to close by 2010 of so in due course.

However, with the expected running of RPH beyond 2010, this case has been taken up again on the basis of CPCB’s / DPCC’s recommendation for recirculation of ash pond water for making ash slurry to conserve water. This work is expected to be completed by the end of the year 2008.

The above said replies have been forwarded to CPCB vide letter dated 11.02.08 after necessary approval on file.

· Decision taken in meeting held on 28.02.2008:

Letter to be issued bearing the directions for meeting the standard of Particulate Matter of 50 mg/Nm3 along with the copy of the minutes wherein it was decided that the standard for Particulate Matter has been made stringent of 50 mg/Nm3. In case high emission is caused due to high ash content in coal, the ash content may be reduced in the fuel (coal).
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Action taken/ Status w.r.t. the meeting held on 28.02.2008:

· Letter issued to RTH on 24.03.08 to meet the standard of 50 mg/Nm3 for Particulate Matter. 

· A reply dated 02.05.08 received from RPH. They submitted that “in order to achieve the SPM level of 50mg/Nm3, they have taken up the matter with M/s. Bharat Heavy Electrical Limited, the OEM, M/s. Alstom Projects India Limited along with other concerned agencies. All these agencies have opined that the SPM level cannot be reduced directly to 50mg/Nm3 from 150mg/Nm3. The desired level can be achieved in phases. In the first phase the same will be reduced to 80mg/Nm3 by upgradation of the existing controllers of ESPs and in second phase either by increasing the volume of the collecting area of the ESP hoppers or by flue gas conditioning”.

· RTPS has also not submitted any time bounded programme to achieve emission <50 mg/Nm3.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

The unit should reduce the emissions in a phase wise manner as submitted by them. In the first phase they must reduce to 80 mg/Nm3 by upgradation of the existing ESPs. A time bound programme may be submitted to achieve the emissions up to 80 mg/Nm3.
Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM
Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
Pragati Power Station, ITO
Status of Consent: Applied for renewal of the Consent vide ID. No. 24530 dated 18.12.07 (Earlier Consent to operate issued on 21.12.05 and valid up to 12.01.08).

Action Taken:

· Letter issued on 20/8/2007. No reply received so far.

· A letter dt 27.08.07 received from Manager (T) Environment, IPGCL-PPCL, informing that-

- MCD is not allowing to dump the Water Treatment Plant (WTP) sludge at Compost Plant /SLF site of MCD.

- The sludge is being dumped at the side of RTPS ash pond to be used by fly ash manufacturer because it contains more than 50% CaO and it is non hazardous.

- Part of this sludge gets mixed with wet ash in the ash pond as the less quantity required for bricks manufacturing.

- Requested to instruct MCD to accept the sludge.

- If it is not materialized, the disposal in ash pond / fly ash brick manufacturer stockyard will be continued and requested to moderate suitably the Terms & Conditions of the consent issued. 

Decision taken in meeting held on 19.10.07:

In response to letter received from Manager (T) Environment, IPGCL-PPCL be informed that the sludge may be used for brick manufacturing by using available technology and with the help of NGOs like Development Alternative. 

Action taken/ Status w.r.t. the meeting held on 19.10.07:

· Letter issued on 5.11.07 communicating above decision. 

· No reply received so far.

Decision taken in meeting held on 09.01.08:
MS to speak to the concerned General Manager and reminder letter to be issued. 

Action taken/ Status w.r.t. the meeting held on 09.01.08:

A reply was received from the power plant (C/339-351). The reply was not with concrete step taken for utilization of sludge. Reminder letter has been issued on 15.02.08.

· Decision taken in meeting held on 28.02.2008:

To be put up in next CMC (MSW) Meeting.

Status of monthly monitoring conducted by DPCC laboratory:
· Noise monitoring report for DG set is not meeting the prescribed standards. Stack monitoring report is also not submitted as having DG set of 1250 KW.
· Monitoring reports for the month of January and Feb. 2008 were meeting the prescribed standards. However, monitoring could not be conducted in March, 2008 as the plant was found under maintenance/ shutdown on 19.03.08.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

Deficiencies may be informed to the unit, for expeditious action for their rectification. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM
Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
I.P. Gas Turbine Power Station

 Status of Consent: Applied for renewal of the Consent vide ID. No. 24589 dated 27.12.07 (Earlier Consent to operate issued on 23.03.07 and valid up to 04.01.08).

Action Taken: A letter dt 27.08.07 received from Manager (T) Environment, IPGCL-PPCL, informing that-

- MCD is not allowing to dump the Water Treatment Plant (WTP) sludge at Compost Plant /SLF site of MCD.

- The sludge is being dumped at the side of RTPS ash pond to be used by fly ash manufacturer because it contains more than 50% CaO and it is non hazardous.

- Part of this sludge, get mixed with wet ash in the ash pond as the less quantity required for bricks manufacturing.

- Requested to instruct MCD to accept the sludge.

- If it is not materialized, the disposal in ash pond / fly ash brick manufacturer stockyard will be continued and requested to moderate suitably the Terms & Conditions of the consent issued. 

Decision taken in meeting held on 19.10.07:

In response to letter received from Manager (T) Environment, IPGCL-PPCL be informed that the sludge may be used for brick manufacturing by using available technology and with the help of NGOs like Development Alternative. 

Action taken/ Status w.r.t. the meeting held on 19.10.07:

· Letter issued on 5.11.07 communicating above decision. 

· No reply received so far.

Decision taken in meeting held on 09.01.08:
MS to speak to the concerned General Manager and reminder letter to be issued. 

Action taken/ Status w.r.t. the meeting held on 09.01.08:

A reply was received from the power plant (C/440-452). The reply was not with concrete step taken for utilization of sludge. Reminder letter has been issued on 15.02.08.

· Decision taken in meeting held on 28.02.2008:

To be put up in next CMC (MSW) Meeting.

Status of monthly monitoring conducted by DPCC laboratory:
· Noise monitoring report for DG set is not meeting the prescribed standards.
· Last three months monitoring reports for the months of January to March, 2008 were meeting the prescribed standards. However concentration of NOx was found beyond the prescribed limit of 75ppm in GT1, GT5 and GT6 which were 90ppm, 90ppm and 80ppm during monitoring on 17.12.07.
Decision of Consent Management Committee in its meeting dated 28.02.2008 :

Deficiencies may be informed to the unit, for expeditious action for their rectification. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM
Decision of Committee (MSWM) taken in its meeting dated 12.05.2008
MAYAPURI CETP  (12 MLD)

Consent status of CETP

· Consent application for consent to operate was submitted by the CETP Society on 07.05.07
Decision of Committee taken on 19.10.2007

The case of Mayapuri CETP was examined by the Committee and it was found that TSS (at inlet), BOD & TDS (at outlet) are well above the norms. 

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 4.2 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The CETP society will submit a Bank Guarantee of Rs. 5 lakh (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.

Deficiencies mentioned in SCN issued & brief of its reply by CETP Society :

Flow at the inlet observed is very low (in the range of 4-5 MLD) against the installed capacity of 12 MLD.

· Average effluent being received at CETP is 4 to 5 MLD from the date of its operation by DSIDC in year 2002.

· Pressure gauges were non-operational from the time of taking over of CETP from DSIDC, now we have calibrated and all are in functional 

No flow meter installed at outlet of CETP. 

· There is no such provision has been given at outlet for installation of flow meter by DSIDC. 

As per DPCC analysis report dated 09-04-2007 BOD (43) Cl (1030) are not as per the norms.

· Submitted copies of daily analysis reports conducted at plant laboratory wef July to Oct 07.  

Significant quantity of silt/sludge found in equalization tanks & pre chlorination tanks. However, one equalization tank was found without effluent/dry for desilting of silt/sludge. 
· There is no mechanism system were provided by constructing agencies for removal of sludge. However, one equalization tank totally desilted w.e.f. 22.07.07 to 07.08.07.

Pressure gauges attached to DMFs & ACFs found in non operational condition.
· The same were mentioned in the deficiencies to DSIIDC at the time of taking over of CETP from DSIDC. Now we have calibrated the pressure gauges and all are in functional.
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As reported, CETP not being received effluent from REPS- II due to blockage/blocking in pipe line/rising main for one month.
· DSIIDC has carried out work of maintenance of RESP-II in Oct 07 and now effluent is being again received from RESP-II w.e.f. 22.10.07.

Individual connection with conveyance system

· Details of individual connections should be obtained from DJB authorities as they are maintaining the whole conveyance system of the industrial area. There is no such separate conveyance system provided for trade effluent.

Bank Guarantee

· As regard submission of Bank Guarantee of Rs. 5 Lacs, the matter will submitted in the next meting of AGM of CETP Society and confederation of CETPs Societies Delhi for suitable decision.

At present there is no such deficiency at plant and plant is being maintained & operated by the CETP Society efficiently.

Inspection status:

Observation during inspection of CETP on 26.11.07 is as follows:

· Equalization  tank No 1 found empty and cleaned (except sump portion) As reported cleaning/ de silting work completed on 7th Aug 07, approx 25 MT sludge was removed & stored in shed.

· Grit Chamber & Screens are not having proper cleaning mechanism and  clean manually. Removal from screen & grit chamber found lying on katcha floors near it. After drying it will transfer in shed.

· Flocks removed manually from the portion of tank between tube settler & flash mixer & found lying on Katcha floor near the flash mixer & after dying transfer it in shed. 

· Pressure gauges attached to DMFs (12 nos) & ACFs (8 nos) found in non operational condition.
· Flow meter not installed at outlet of CETP. 

· Level meters of equalization tank & final treated tank found in non operational condition.

· Average intake effluent in Oct. 07 was 2.54 MLD.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Member Secretary, DPCC to check whether the then Chairman, DPCC has confirmed the installation of flow meter at outlet of CETP in EPCA meeting through its minutes. 

Since the unit appears to have corrected some of the deficiencies, a fresh inspection may be done and report be submitted in next CMC (MSW) meeting. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 
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Action Taken Report
Letter issued on 28.01.08. CETP society has submitted letter on 13.02.08 informing that the deficiencies pointed out has been corrected and requested for issue of consent.
Inspection status:

Observation during inspection of CETP on 18.01.2008 is as follows:

· One equalization tank (from which silt removed earlier) found in use.

· Another equalization tank found empty & silt removed,found stored in shed. 

· Pressured gauges attached to DMFs& ACFsfound in non operational condition.

· During inspection 6 DMF found operational. As reported they operate DMF on rotation basis.

· Level meter of equalization tank & final treated tank found functional.

· As reports work of flooring near grit chamber & flesh mixer is going to start with in 15 days.    

DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	TSS-296
	_
	TSS-332
	BOD-38          TDS-2200
	TSS-336
	BOD-40
	Non operational
	Non operational


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

To be put up in next CMC (MSW) Meeting.
Action Taken Report
 In response to our letter dated 10.03.08 society has submitted that they have not obtained any analysis report from DPCC for the month of Dec. 07 so far and as per analysis report of Jan. 08, received from DPCC final outlet quality is well within the prescribed norms and requested to issue necessary consent.

A copy of letter dated 04.04.08 addressed to DSIIDC received from CETP society mentioning that the peripheral Sewer/ Rain Water Piper lines laid by DSIIDC are not properly inter- connected  and now CETP society has completed this work. Society has requested to make necessary recovery from the then constructing contractor and amount incurred shall be paid to CETP society.

Vide letter dated 24.04.08 CETP society has submitted point wise counter reply of the affidavit filed by Commissioner of Industries in the Hon’ble Supreme Court mentioning as under:  

1. CETP society have already provided list of the members to the appropriate authority on 24.09.07 

2. The defaulter lists provided to the appropriate authority on 03.03.08, 12.02.08, 02.04.07, 31.11.04 & 26.02.04.

3. Mayapuri CETP society already contributed 50% apportionment cost amounting to Rs. 21809000/- to DSIIDC in time. 

4. Managing Committee of Mayapuri CETP society comprising of elected members of four major Indl. Welfare Association of the area and unanimously re-elected again in its adjourned general body meeting held on 26.04.05 and resolved to work continuously till next AGM. Next meeting of AGM will be scheduled in the month of June 2008.

5. The general body on 26.04.05 resolved that M/s Manmohan & Associated will continuously work as C. A. for society. 
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6. CETP society has already appointed qualified technical staff at CETP as per criteria given by appropriate authority and necessary list have already been sent to Appropriate Authority & Member Secretary, DPCC vide our letter dated 02.01.08 & 15.03.08. 

7. The Bank Account of society are maintained only in 2 nos. banks i.e. HDFC Bank and Canara Bank in Mayapuri Indl. Area and informed to Appropriate Authority in the quarterly returns duly filled up proformas of all information required by the appropriate authority time to time.

8. Apart form this CETP society have sent no. of additional document/ information to the appropriate authority.

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-440
	BOD- 36          TDS-2200
	TSS-368
	BOD-37


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
In view of the parameters BOD & TDS are not meeting the prescribed standard at the outlet of CETP, as per monitoring conducted by DPCC laboratory in month of March, 2008, Bank Guarantee of Rs 5 lakh is confirmed and CETP Society shall submit the Bank Guarantee by 30.06.2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

MANGOL PURI CETP (2.4 MLD)

Consent status of CETP

Consent to operate issued with conditions on 27.07.2007.

Decision of Committee taken on 19.10.2007

A letter issued to CETP society to correct the deficiencies noted during the inspection on 18.07.07and to comply with the earlier conditions which were imposed when the consent to operate was granted. 

It was also found that against the installed capacity of 2.4 MLD, the CETP Society is operating it at only 1.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

 The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The society will submit a Bank Guarantee of Rs. Fifty Thousands (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.

Deficiencies mentioned in SCN issued & brief of its reply by CETP Society:

Pressure gauges attached to DMF & ACF found not in operational condition.

· New pressure gauges have been installed.

No flow meter installed at outlet of CETP.

· There was no flow meter installed at the outlet ever since the plant was constructed and accordingly we have informed the DSIDC. There is no such provision provided by the DSIDC in this matter.

Bank Guarantee

· The matter has been discussed at the confederation level and we shall act in accordance with the other CETP Societies as when it is decided. 

Consent to Operate to was granted on 27.07.2007 with the following conditions: 

1. To increase the effluent quantity.

We ca not import extra effluent from outside the industrial area. Each and every unit is connected to DJB common sewer line with the CETP inflow pipe.

2. To install mechanical dewatering system.

We have already arranged for the submersible pump and this has been installed already in plant.

3. To modify the acoustic enclosure with DG set to achieve the insertion loss.

Our acoustic enclosure with DG et is in sound position ever since it was installed and there is no scope of any further improvement.
Inspection status:

Observation during inspection of CETP on 05.12.07 along with CPCB during training program is as follows:

No flow meter installed at outlet of CETP.

DG Set with acoustic enclosure installed.

CETP Society has shown new pressure gauges during inspection & as reported same shall be installed within 2-3 days.

Average intake effluent during the month of Nov. 07 -  MLD

Flow meter at inlet found operational.
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Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Since the unit appears to have corrected some of the deficiencies, a fresh inspection may be done and report be submitted in next CMC (MSW) meeting. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 

Action Taken Report
Letter issued on 25.01.08.
Inspection status:

Observation during inspection of CETP on 21.01.2008 is as follows:

· Acoustic enclosure installed with DG Set.
· New pressure gauges installed with ACFs & DMFs.

· Flow meter at inlet found operational.
· Total intake during Dec 07 was 34.11 MLD (Average-1.1MLD).

· One aerator (out of four) of aeration tank found under maintenance. 

DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	TSS-268
	Cl-1080      TDS-3900
	TSS - 268
	Cl-1830   TDS-5070
	TSS - 980
	Cl-1040   TDS-3946
	TSS-366
	Cl-1800   TDS-6954


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Letter to be issued to CETP to submit an affidavit as to why there is  fluctuation in the parameters of water analysis report compared to the standards. 

Action Taken Report
Letter issued on 19.03.2008. 

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-480
	Cl-2080      TDS-6700
	TSS-380
	Cl-2153      TDS-5020


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
In view of the parameters Cl & TDS are not meeting the prescribed standard at the outlet of CETP, as per monitoring conducted by DPCC laboratory in month of March and April, 2008, Bank Guarantee of Rs 50,000 is confirmed and CETP Society shall submit the Bank Guarantee by 30.06.2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008
Badli Industrial Estate CETP ( 12 MLD)

Consent status of CETP

Consent to operate issued on 28.02.07 to CETP society for period of three years and valid up 28.12.09.

Decision of Committee taken on 19.10.2007

This CETP was inspected on 17.4.07 and again on 11.7.07 the following deficiencies were noted in first time and the second time as under: -

The CETP society has neither corrected the deficiencies nor sent the reply. In view of the above, issue SCN for revoking of consent u/s 27 of the Water Act.  

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 1.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

 The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The Society will submit a Bank Guarantee of Rs. Five Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.  
Deficiencies mentioned in SCN issued & brief of its reply by CETP Society:

Flow meter sent to repair 

· repaired flow meter again found faulty & now order for new flow meter has been placed & same will is likely to be operational well before 31.12.2007.

No flow meter installed at outlet of CETP.  

· Flow Meter at the outlet was not installed in the plant by DSIIDC. It was agreed by DPCC that the flow meter at the outlet of CETP shall be installed by them only.

Grit chamber, Equalization tank work field with significant quantity of silt/sludge.

· Slit / sludge is accumulated in these tanks inspite of regular cleaning due to presence of solid waste / dust /building material malba in the domestic sewage / storm water carrying road washings/ kacha muddy drain carrying mud into the effluent going into the CETP.

· No arrangement has been provided in the plant to ensure proper cleaning of the tanks. We have already started the process of cleaning of various tanks in the plant by using a borrowed sludge pump.

· No arrangements have been provided by the authorities so far the disposal of the sludge generated in the plant. The tank cleaning activity, therefore, is getting affected due to this problem.

· We are fully committed to follow every rule in letter and sprit and have never allowed any slit / sludge to be kept outside the plant premises.

Pre chlorination as well as post chlorination were non-operational.

· Pre and post chlorination is being done in the plant as per requirements the effluent under treatment.
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Dosing of Alum and Bleaching not being carried out due to defective pipe line.

· Dosing of Alum and bleaching powder too is being as per requirements of the effluent under treatment. In a plant such as ours, it is quite natural to encounter defects due to normal wear and tear and corrosion.

Two number of pressure gauges ( out of 8 ) attached to ACF and 2 gauges (out of 12) of DMFs work found non-operational. 

· All such defects are routinely addressed and taken care of by our team running the plant. 

Two aeration (out of 3) found out of order.

· These were under routine maintenance and were duly made fully operational subsequently.

One vacuum filter found out of order and other also partially operational due to non-operational of vacuum pump.

· Reported out-of-order Vacuum Filter is under break down maintenance requiring major repairs. Effective steps are beings undertaken at our end to make this Filter operational in the shortest possible time. Moreover, the partially operational Vacuum Filter has been made fully operational. As such there is no hitch in the smooth operation of the plant.

TDS

· Neither NEERI has recommended nor DSIIDC has provided any technology / hardware (such as RO, DM plant or evaporation) for reduction of TDS at any stage of operation. CPCB and EPCA have also agreed to keep  the fixing of standard of TDS at abeyance or to raise the standard an achievable value.

· We feel that holding  CETP Society responsible for any lapses talking place outside the plant is neither correct nor justifiable.

· Occurrence of defects in any equipment in a plant like ours is a natural phenomenon which takes place during the course of its normal running. The so-called deficiencies are, therefore, not really deficiencies but issues that may occur during operation of any plant of similar nature. What is important is the fact that appropriate and timely actions have been taken and being taken to ensure proper running of he plant.

Flow intake range - 0.78 to 1.56 MLD.

· This is the responsibility of DJB in terms the Agreement for maintenance and Operation of CETP. However, the management of the Society is taking all measures under its control to ensure compliance of these directions.

· The sewer lines on Badli are badly chocked and require extensive desilting and cleaning. As a result of chocking of the conveyance system, its capacity to carry effluent to the plant is getting severely limited and this also results in its overflowing at several locations in the estate and the effluent gets entry into the open drains of the area.

Bank Guarantee of Rs. Five Lakhs 

· There have been no willful wrong doing / default on our part, there is no justification whatsoever in asking us to submit a bank guarantee. It is therefore, prayed tat this direction may please be withdrawn.

· There is no justification in asking for any affidavit from us on the matter.

· Our request for withdrawing the harsh penalty of imposing a bank guarantee and filing of affidavit shall merit your favorable consideration. 

Inspection status:

Observation during inspection of CETP on 27.11.07 is as follows:

Flow meter at inlet not in operational condition. 

Flow meter at outlet of CETP not installed.

Grit chamber, equalization tank & pre chlorination tanks are fillede with silt/ sludge.

Pre chlorination & post chlorination not done.

Dosing of Alum & bleaching  not carried out since long, pipe lines of dosing defective. 

Pressure gauges of DMF & ACF (4nos) are not functioning.

One vaccume filter is non operational condition.
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Average intake in month of Oct 07 - 0.70 MLD

A shed provided for storage of Hazardous Waste.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Since the unit appears to have corrected some of the deficiencies, a fresh inspection may be done and report be submitted in next CMC (MSW) meeting. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 

Action Taken Report
Letter issued on 25.01.08. 

Inspection status:

Observation during inspection of CETP on 21.01.2008 is as follows:

· Flow meter at inlet found operational. 

· Grit chamber found cleaned. CETP society has installed a sludge pump for removal  of sludge from equalization tank.
· One pre chlorination tank cleaning activity going on during inspection.
· Pre chlorination & post chlorination dosing found functioned.
· Pressure gauges of ACF & DMF found replaced. During inspection 4 ACF & DMF found operational. As reported, ACF & DMF are operated on rotational basis being low intake effluent.
· One vacuum filter found out of order & other found operational.
· Total intake during Dec 07-19.42 ML
DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	TSS- 520                          Cr-2.92
	_
	Non operational
	Non operational
	Cr- 3.6
	_
	Cr-2.41
	_


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

No action. 

Action Taken Report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-480
	_
	Cr- 4.21
	_


Decision of Consent Management Committee in its meeting dated 12.05.2008:

In view of the parameter BOD is not meeting the prescribed standard at the outlet of CETP, as per monitoring conducted by DPCC laboratory in month of April, 2008, Bank Guarantee is reduced from Rs. 5 Lakh to Rs. One Lakh and confirmed to be submitted by 30.06.2008 by CETP Society.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008
Wazirpur Indl Area CETP ( 24 MLD)
Consent status of CETP

Consent to operate issued on 23.02.07 to CETP society for period of three years and valid up 27.12.09.

Decision of Committee taken on 19.10.2007

The unit has not complied with the directions given after inspection on 13.4.07. A SCN notice for closure / revocation of consent be issued.

The unit has further not bothered to correct deficiencies found during the inspection on 19.7.07. It was also found that against the installed capacity of 24 MLD, the CETP Society is operating it at only 3.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

 The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The society will submit a Bank Guarantee of Rs. Ten Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections not done by 31.12.07. The unit is given a last chance to correct its deficiencies by 31.12.07 failing which the consent will be revoked and heavy penalty will be imposed on CETP society. CETP society must operate the CETP plant professionally, efficiently, effectively. Copy should be sent to MD (DSIDC) and Comm. of Industries.
Deficiencies mentioned in SCN issued & brief of its reply by CETP Society :

Flow meter installed at inlet was still out of order. The same has gone to the manufacturer for repair.

· We are taking up the matter with DSIDC who has selected this Hardware for change over to physical/mechanical weir, so that there are no break downs.

No flow meter installed at outlet of CETP.

· In the EPCA meeting (Aug. 2005), the Chairperson, DPCC had promised to provide outlet flow meter, if this is done we shall e grateful.

Flow observed to be in range of 3-4 MLD against instak\lled capacity of 24 MLD.

· All the Small and tiny units operating in the area generated only 3.4 MLD (Trade & Domestic) effluent as per average water consumption calculations. However, effluent what so ever is coming to CETP is being taken care of.

· Matter regarding creation of abnormally higher capacity is subjudice as the industries has been the big losers by way of enhance capital cost as well as recurring operation & maintenance cost.

Receiving chamber & grit chamber filled with silt/ sludge.

· In spite of regular cleaning receiving chamber / grit chamber gets filled with slit due to heavy surge of solid waste due to demolitions by MCD / DDA, and storm water / kacha muddy drain (carrying mud) into the effluent coming to CETP.
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· There is no provision for mechanical cleaning. You are requested to kindly guide / advise us to further streamline the system.

Conveyance system was yet to be commissioned.
· Conveyance system has already been commissioned by any specific short fall may reported to DJB through DSIDC for a corrective action as the responsibility for operation and maintenance of Conveyance system is of DJB/DSIDC.

Pressure gauges attached to DMF & ACF were found not in operational condition. 

· PGs are functional and are being checked fortnightly, problem if any is being rectified and re-calibrated.  PG have no impact on the operation of tertiary plant, it is merely an indication for backwash requirement.

No pretreatment for pH was being done at unit level. However, pH of in-effluent observed as 2.7. 

· pH after treatment at the outlet of CETP is well within limits as per DPCC analysis reports of lasts one and half years, however , the individual industries monitoring at present is being done by DPCC, for which we have repeated written  to the Appropriate Authority to transfer power to CETP Societies as decided in the EPCA meeting and written in the O&M agreement as promised by the Government of Delhi.  It would be in the interest of the CETP Societies and also make things functional better, necessary authority be vested with the management of CETP Societies so as to such situation does not arise. Hope DPCC will use its good office to facilitate this.

Vacuum filter (both), flush mixture (2 nos) were not in operation since last few days.

· As  the influent is only 3 MLD , we operate only vacuum filter at a time, other standby is in working condition. We operate only two units (flesh mixer) at a time, other are kept as standby.

As per DPCC analysis report, dt 09-04-07, TDS (4087) was not meeting the prescribed standards. 
· There is no provision of reducing TDS. It was pointed out in the meeting by NEERI as well CPCB that the Total Dissolved Solids in treated effluent from most of CETPs are high and not able to meet the TDS standard.

· CPCB and EPCA have also agreed to keep the fixing of standard of TDS at abeyance or to raise the standard to achievable value.

· Regarding value of BOD as 36 mg/I at the outlet on 13.9.2007 monitoring, it may be due to shock load from Domestic Waste Water entering CETP along with trade effluent.

Bank Guarantee
· The correction of deficiencies are being very seriously looked into for 100% service, whereas deficiencies due to design fault, lack of appropriate hardware / technology or lack of authority as vested with CETP Societies under direction with the Appropriate Authority, we would therefore very strongly recommend your intervention for setting write the thing instead of passing balance to the CETP Societies and irrelevantly imposing Bank Guarantee of Rs 10 lacs, for which we request to withdraw the condition for submission of Bank Guarantee as we are committed to operated  maintain CETP.

Inspection status:

Observation during inspection of CETP on 05.12.07 along with CPCB during training program is as follows:

Flow meter at inlet out of order & sent for repair as per documents shown.

Equalization tank found filled with significant quantity of silt/ sludge.

Conveyance system for WIA is yet to be completed.

No flow meter installed at outlet of CETP.

Vacuum filter & flash mixer found in operation.
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One tube settler is under cleaning.

Pressure gauges attached to ACFs & DMFs are found functional.

Average intake during month of Nov. 07 – 1.93 MLD.
Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Since the unit appears to have corrected some of the deficiencies, a fresh inspection may be done and report be submitted in next CMC (MSW) meeting. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 
Decision of Consent Management Committee in its 35th meeting of CMC (orange) dated 14.01.2008 :

On closed inspection of the file, in view of the representation made by the Wazirpur Industrial Association to Hon’ble CM 10.01.08 reveal that two out of the three deficiencies have been corrected. Since the CETP society is amending its ways, the committee felt that the Bank Guarantee of Rs. 3 Lakhs for a period of six moths may be taken from the society within one month in order to ensure that it corrects these three deficiencies consistently. 

Action Taken Report
As decided by CMC on 14.01.2008, Letter  issued on 12.02.2008 for seeking Bank Guarantee & affidavit. No reply received. 
Inspection status:

Observation during inspection of CETP on 22.01.2008 is as follows:

· New flow meter installs but found non operational.

· Equalization tank found filled with significant silt/sludge.

· No flow meter installed at out let of CETP.

· Pressure gauges attached to ACF & DMF found operational.

· pH at inlet (raw effluent sump) at CETP was 1- 1.5. 

· Vacuum pump, filter & flash mixer found operational 

· Total intake during month of Dec 07 was 57.65 ML at average of 1.85 MLD.

· CETP society is adding dosing of NaOH in the raw effluent sump to make pH about 3 before sanding effluent to grit chamber of CETP.
· Hazardous Waste/ sludge found stored in two sheds and in sludge holding tank. One new shed is under construction.
DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	pH- 1.8           Cr-24.64
	TDS-4940
	pH- 1.2         TSS- 468       Ni-4.1           Cu-6.6          Cr-24.0
	TDS-2790
	pH- 2.6         Ni-3.6           Cr-28.0   Cr+6- 2.8
	_
	pH- 2.6         Ni-3.2           Cr-12.44
	TDS-2501


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

1. Letter be issued to CETP to submit an affidavit, as to why TDS is exceeding at the outlet of CETP and parameters at inlet are fluctuating as per water analysis report. 

2. All deficiencies of 22 Jan 08 may be corrected by CETP within 1 month.

3. Individual connections to conveyance system must be ensured for all individual polluting units.
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Action Taken Report
Letter issued on   24.03.2008.  Reply to the notice dated 24.03.2008 not received so far.

A letter has been received from DSIIDC on 03.04.2008 regarding non functioning of pumps at Wazirpur Industrial Area due to low pH. As approved, Directions u/s 33 (A) of Water Act was issued to Wazirpur CETP Society on 15.04.2008 to ensure that all the members of CETP Society shall treat their trade effluent so as to meet the prescribed norms of parameter pH of 5.5 before discharging into the conveyance system to enable the operation of CETP, Wazirpur.

The society has submitted the reply to the directions u/s33(A) of Water Act on 15-04-2008 wherein it is mentioned that notice has been circulated to all the water polluting units/pickling units in the area and send another reminder to them on 28-4-2008, but there is no response from the units and there is no improvement in the pH at the inlet of CETP and requested to suggest as to how to get the needful done. The society has also submitted the list of the 201 water polluting units(150{pickling}, 12{Dyeing},14{Electroplating},9{Service Station} and 16{other category})

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	pH- 1.7       TSS- 260    Ni-3.6           Cr-30   Cr+6- 2.5
	TDS-4150
	Non operational
	Non operational


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
Dr.S. K. Gupta, Prof IIT has agreed to send one Associate Professor who will be provided transport and other facilities by DPCC to check the CETP plant and he will suggest  how TDS can be reduced substantially. 
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Jhilmil & Friends Colony Indl Area CETP ( 16.8 MLD)
Consent status of CETP

Consent to operate issued on 28.02.07 to CETP society for period of three years and valid up 07.01.2010.

Decision of Committee taken on 19.10.2007

Directions issued after Inspection on 16.4.07 have been responded by the society. However, the inspection of 11.7.07 still found certain deficiencies which should be communicated to the society by the SCN u/s 33 of Water Act. While the July and Aug. monitoring reports showed certain norms not in compliance, the September report finds the CETP functioning with in the norms. 

It was also found that against the installed capacity of 16.8 MLD, the CETP Society is operating it at only 5.0 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The Society may be asked to be cautious and correct all deficiencies by 31.12.07 and submit an affidavit, failing which a BG of Rs. 5 lakh may be imposed on the society.  

The copy should be sent to MD (DSIDC) and Comm. of Industries.  
Deficiencies mentioned in SCN issued & brief of its reply by CETP Society :

Both equalization tanks were found filled with significant quantity of  silt/sludge.

· Cleaning of the equalization tanks, two equalization tanks, each will take at least one month one month or so, as was done in 2006 after monsoon’s.

No settling was observed in grid chamber.

· Grit chamber is in operation as per design/ construction, done by DSIIDC and is regularly cleaned.

Large quantity of oil and grease was observed in both equalization tanks.

· Door to door notices were sent to individuals factories to operate their ETPs. In fitness of things DPCC can help us by ding surprise checks, rather than penalizing the society, who have their own limitations.

1 vacuum filter found was found non operational.

· Both vacuum pumps are in operation on alternate basis.

3 no receiving pumps (out of 6) were found under repair.

· Presently all the six receiving pumps are in operation.

Flow observed to be in the range of 1.5- 3.5 MLD against installed capacity of 16.8 MLD.

Individual connections with conveyance system

Notices for individual connections to conveyance system have already been sent & most of members have connected to conveyance system. For defaulters action to be taken by DJB/ DPCC. However we have again sent the reminders. Requested to help for enhancing the inflow by directing the nearby Patparganj Indl. Area & other area (Dilshad Garden/ Shahdara North Area) to bring effluent to Jhilmil CETP.        
As per DPCC analysis report some parameters  are not meeting the norms laid down.
· Regarding some of the parameters viz. TDS, Cl, CU, Cr, it was decided by EPCA to maintained only four parameters by CETP’s . Only on this ground the handing/ taken over of CETPs were done by the society and the society agreed to maintained parameters as maintained by DSIDC at that time. 
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· To Submit list of employees working at CETP.

· Some of the deficiencies which are practically possible for the society to remove have been started immediately.

Inspection status:

Observation during inspection of CETP on 19.12.07 is as follows:

Equalization tank are found filled with significant quantity of  silt/sludge.

Silt removed from grit chamber found lying near grit chamber on katcha floor in open for drying and as informed, after drying it will sore in shed.

Both vacuum filters found in operational condition.

No flow meter at outlet of CETP

Sludge thickner pump repairing work going on during inspection.

Average intake effluent during month of Nov. 07 –  4.54 MLD.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Since the unit appears to have corrected some of the deficiencies, a fresh inspection may be done and report be submitted in next CMC (MSW) meeting. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 

Action Taken Report
Letter issued on 25.01.08. CETP society has submitted letter on 12.02.08 informing that cleaning of silt in tanks is in progress, gird chambers are regularly cleaned, vacuum pumps and filters are in working condition.
Inspection status:

Observation during inspection of CETP on 18.01.2008 is as follows:

· One equalization tank is not in use, as kept for desilting of tank by using sludge pump.

· One vacuum filter & one vacuum pump were out of order. 

· Sludge thickener pumps (both) found out of order.

· effluent during month of Dec 07 was 108.35 ML (average-3.5 MCD)

· Flow meter of inlet found operational.
DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	_
	BOD-34       Cl-1880       TDS-3290
	TSS-684
	TDS-2250
	TSS-472      Cu-5.2              Cr-2.3
	_
	TSS-468        Cr-3.6
	BOD- 34          TDS-2867


Letter received from CETP society on 26-2-08 stating that in EPCA meeting it was decided that the TDS and Cl. Parameters will not be taken into account as these are the origin  of the groundwater.
· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Letter to be issued to CETP to submit an affidavit as to why the parameters are fluctuating as per water analysis report. Apart from this they will also submit the minutes of EPCA wherein it is decided that the parameters of TDS and Chloride will not be taken into account. Deficiencies of the inspection report of 18 Jan 08 should be corrected by the CETP within 1 month.

Action Taken Report
Letter issued on 24.03.2008.

CETP society has submitted reply on 17.04.08 and brief is under:

1. The DPCC analysis report indicate that some inlet parameters are not within the prescribed standards. In this connection it is highlighted that the individual ETP’s in the industrial area which discharge effluents into the sewer are being monitored by DPCC 
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2. The CETP society has a limited role and no teeth to control the individual ETP’s which are under the direct control of DPCC.

3. As regard the removal of CL and TDS at the outlet it is directed that the ground water being used in the industrial process is very heavily loaded with Cl- and TDS. DPCC while accepting the feasibility report of NEERI in the preliminary design technology has taken care of this fact and the CETP’s were designed under the direct/ indirect supervision of DPCC.

4. The CETP society are using the technology that was approved by DPCC and constructed by DSIIDC. The Society is controlling and maintaining the parameters as were done by DSIDC, before handing over.The society submitted the copy of agreement made for operation and maintenance of CETP.

5. The vacuum filter and vacuum pump were under maintenance and have been repaired.

6. Sludge thickener pump were out of order, but augmented with separate submersible pump. The necessary steps have been taken in this regard and the deficiencies have been removed. 

7. If DPCC has any objection on shutdown of equipment for maintenance, the society will  not carry out maintenance work and further consequence will be on DPCC.

8. The Minutes of meeting of EPCA can be obtained from the EPCA secretariat at CPCB.

9. The condition of submitting an affidavit in regard that parameters are fluctuating, is rejected with strong force on solid grounds that the requirement of an affidavit is not warranted in any of the environment, water or air act. DPCC is not a court for which an evidence is be recorded by an affidavit and technically a huge plant like CETP is going to have fluctuations in the inlet and out let parameters and a future fiction cannot be translated in present confirmation.

10. In the light of above mentioned facts and all surrounding factors, DPCC has to provide the guidance for removal of Cl and TDS within the economic means of the society and in case DPCC feels that the society has failed to carry out the responsibility it can take over the plant and run on its own to maintain Cl and TDS parameters.

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-340
	TDS-2810
	Cu-4.5
	BOD-32       Cl-1220       TDS-3060


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
DPCC is the regulatory body and under the Water Act. DPCC has full power to ask for any information to be authenticated through an affidavit. Society must therefore file an affidavit by 30.06.2008, without fail. 
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

DSIDC Nangloi Indl Area CETP ( 12 MLD)
Consent status of CETP

Consent application for consent to operate was submitted by the CETP Society on 27.06.2007. 

Decision of Committee taken on 19.10.2007

The deficiencies noted in the inspection of 18.7.07 may be communicated to the unit and time given up to 31.12.07 to correct the deficiencies. The latest inspection of sept. indicates that TDS parameters not meeting the  norms.

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 1.0 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the   connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

 The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The society will submit a Bank Guarantee of Rs. Two Lakhs Fifty Thousands (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done by 31.12.2007. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.  
Deficiencies mentioned in SCN issued & brief of its reply by CETP Society :

Flow at the inlet observed is very low (in the range of 2.75 MLD) against the installed capacity of 12 MLD.
· The DPCC very well knows that the CETP Nangloi has been designed over capacity by NEERI.

Pressure gauges attached to DMF & ACF were found in non operational condition.
· It hardly matters whether pressure gauges are operational or not till the designed standards are beings met. Still however as the plant is under 3 year warranty, the DPCC should have caught hold of DSIIDC/L&T to get the same replaced . 

Flow meter at outlet of CETP found non operational.
· It is well understood that the same quantity of effluent comes to the plant which would be treated before discharging and as such there should not be any objection in this matter.

As per DPCC analysis report dt 13.04.2007, BOD (42), Cl (2050) & TDS (4697) are exceeding the norms laid down.
· BOD level was marginally increased from the permissible range in that period but the same has been brought under control.

· We were handed over the plant in Oct, 05, wherein before the Bhure Lal Committee also, we were told that TDS can not be maintained as it depends on the quality of incoming water in the plant. TDS was never within the permissible range.

Bank Guarantee
· As such you would please appreciate that issuing Show Cause Notice and asking for a Bank Guarantee when the Society is already meeting its obligation is uncalled for and require immediate withdrawal. Request you to kindly issues the Consent to Operate at the earliest.
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Inspection status:

Observation during inspection of CETP on 19.12.07 is as follows:

Flow meter at inlet found in operation.

Pressure gauges attached to DMF & ACFs found out of order.

Flow meter at outlet found non functional.

Average intake during month of Nov. 07- 1.8 MLD

One oil & grease screamer at grit chamber found under maintenance.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Since the unit appears to have corrected some of the deficiencies, a fresh inspection may be done and report be submitted in next CMC (MSW) meeting. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 

Action Taken Report
 Letter issued on 28.01.2008.

Inspection status:

Observation during inspection of CETP on 21.01.2008 is as follows:

· CETP found in operation

· Pressure gauges of DMF & ACF found replaced/ repaired & found operational (4 DMF & 3 ACF are in operational).
· Oil & grease screamer of grit chamber repaired & found operational.
· Flow meter at inlet found operational 
· Total intake of effluent during Dec. 07 was 48.2 ML.
· Filter pump & filter found operational.
DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	TSS-460
	BOD-33          TDS-2070
	TSS-460
	TDS-2510
	TSS - 460
	BOD-25      Cl-1700   TDS-3210
	TSS-364
	BOD- 33          TDS-3172


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Letter to be issued to CETP to submit an affidavit as to why the parameters are not meeting the prescribed limit. 

Action Taken Report
Letter issued on 19.03.2008. society has submitted reply & stated as under:

1. The above plant was constructed under your guidance and expert opinion. The construction was carried out by L&T through DSIDC.

2. Every now and then it is observed that the BOD level of the effluents discharge goes up and we are not able to find out any equipment installed in the aforesaid plant to control the BOD at the desired limit. You are therefore requested to kindly guide us as to how the BOD level should be controlled within the permissible limits.
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3. If for any reason, any plant or machinery or part thereof  has not been installed in the plant please let us know the detail specifications for further action in the matter.

4. Our Operating Agency M/s Om Bio Chem System Pvt. Ltd., had submitted an affidavit duly Notarized, that there are no equipment/ any mechanism in the plant to control the BOD at the desired limit.

5. Some parameters were eliminated from pollution control Law Series: PCLS/4/2000-2001. TDS (Total Dissolved Solids) and Cl-No limit defined. [Limit defined in EPA for CETP Inlet and outlet]

6. The TDS & CL are increased in ground water i.e. because of non availability of sufficient surface water. The BOD level is increased some of our sample i.e. because of non availability of sufficient power supply.

7. We here by under take on behalf of DSIDC & UN CETP Society, we are operating & maintaining the above said plant as per designed efficiency of plant.
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-340
	TDS-2840
	TSS-484
	BOD-35  


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
In view of the parameter TDS & Cl are not meeting the prescribed standard at the outlet of CETP, as per monitoring conducted by DPCC laboratory in month of April, 2008, Bank Guarantee is reduced from Rs. 2.5 Lakh to Rs. One Lakh and confirmed to be submitted by 30.06.2008 by CETP Society.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

SMA Indl Area CETP ( 12 MLD)
Consent status of CETP

Consent to operate issued on 15.09.04 to DSIDC for period of three year and valid up 27.07.07. CETP society submitted application for consent to operate on 11.04.07.

Decision of Committee taken on 19.10.2007

The unit was inspected on 19.7.07 and gross deficiencies were found. Also the sept. report show TDS in excess of the norms . 

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 1.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The society will submit a Bank Guarantee of Rs. Five Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done by 31.12.2007. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.  
Deficiencies mentioned in SCN issued & brief of its reply by CETP Society :

Equalization tank was found filled with significant quantity of silt/sludge.

· DSIIDC At the time of handing over the plant at submitting undertaking to desilting the plant. 

Sludge kept in open. The existing storage facility was completely full. 

The sludge which is generated from the process is not being stored as per the guide lines of storage of Hazardous Waste Rules. At present it is being dumped in open raw land. 

· DSIIDC at the time of handing over the plant at submitting undertaking to create a new sludge house which is still pending. However initiative of the society for new sludge house is being created.

The existing conveyance system to CETP still choked. Due to that total quantity of Waste Water is not being coming / being received in CETP. 

· The conveyance system of CETP is maintained by DJB and it is working properly.

No flow meter installed at outlet of CETP. 

· This was decided in a meeting with EPCA that the flow meter will be installed by DPCC.

As per DPCC analysis report dt 10-04-07, BOD (38), Chlorides (2120) and TDS (3904) are not within the prescribed norms. 
· In this regard (TDS,CI) the CETP members are being perused not to use ground water for processing. Efforts have been made to control BOD.

During the inspection CETP was not in operation since last few days. 

During inspection it was observed that waste water is being thrown out side of the premises on public land along with silt / sludge. Due to that a pond has become in existence near railway line. 

CETP was under maintenance during the inspection and maintenance was being done by DSIIDC. Therefore it is the responsibility of DSIIDC.
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Individual connections with conveyance system

· We have made all sewer connections to the main conveyance system and letter from the DJB to this effect is being obtained very shortly.

Bank Guarantee
· In the background of clarifications & facts at site, we fail to understand that instead of empowering CETP Society and cooperating/ helping in removing deficiencies in the CETP hardware/ technology provided, DPCC is imposing a bank guarantee. We pray that if the Committee is not satisfied with our reply, a personal hearing may be given. Consent to operate to our CETP Society must be given, otherwise we presume that running of CETP is an offence.

Inspection status:

Observation during inspection of CETP on 27.11.2007 is as follows:

Equalization tank was found filled with significant quantity of silt/sludge.

Sludge kept in open. Work of construction of shed is going on & as reported work will be completed in 15 days.

No flow meter installed at outlet of CETP. 

Sludge dewatering system not in operational condition.

Pressure gauges for DMFs & ACFs are not in working condition (except 2 nos)

Display board wrt HW rules is not updated.

Average intake quantity of effluent during month of Oct. 07 – 1.26 MLD.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Since the unit appears to have corrected some of the deficiencies, a fresh inspection may be done and report be submitted in next CMC (MSW) meeting. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 

Action Taken Report
Letter issued on  28.01.08.

Inspection status:

Observation during inspection of CETP on 21.01.2008 is as follows:

- Equalization tank (both) found filled with significant quantity of silt/sludge. Agitators (both) are non operational due to silt. 

     - One equalization tank inlet stopped/ closed. As reported, society now starts work of                

        cleaning of tank for which it will be dried/closed & then sludge will remove. This work will take approx two months.

     - Pressure gauges of 2 DMF & 1 ACF not in working condition.

     - Sludge kept in sheds, however construction of 2nd shed is also going on.

     - Flow meter at inlet found operational. 

     - One sludge vacuum pump & filter found operational & 2nd in non operational condition.
     - No flow meter installed at outlet of CETP.

     - Total intake during Dec 07 was 48.6 MLD

     DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	TSS- 668                         Cr-4.24
	TDS-3290
	pH- 2.9         TSS- 620       Ni-4.0                     Cr-3.1
	TSS-112       BOD-34      Cl-1100   TDS-2990
	Ni- 3.1        C - 2.4
	BOD- 34          TDS-3666
	NIL
	TDS-2501
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· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Letter be issued to CETP to submit an affidavit, as to why TDS is exceeding at the outlet of CETP and parameters at inlet are fluctuating as per water analysis report. Deficiencies of inspection Report of 21 Jan 08 may be corrected by CETP within 1 month.

Action Taken Report
Letter issued on 24.03.2008.

The society submitted the reply on 23-4-2008 wherein it is stated that the individual ETPs are bring monitored by DPCC inspectors regularly and the inlet parameters fluctuates due to the effluent discharge through ETPs. The CETP society has a limited role and no teeth to control the individual ETPs which are under the direct control of DPCC.

Regarding TDS-ground water of industrial areas is heavily loaded with TDS, DPCC while accepting the feasibility report of NEERI has taken care of this fact and CETPs were designed under/indirect supervision of DPCC.Society is using the technology that was approved by DPCC and constructed by DSIDC.

Regarding deficiencies, the withdrawal of silt from equalization tank was one of the condition of taking over the plant by the society from DSIDC, DSIDC has not fulfilled the condition till date.Silt exclusion will be taken of by the society in the dry season by drying the silt. Agitators are not operational due to silt to safeguard the machinery and to prevent choking of the tube settler.Now the pressure gauges are fully functional. Vacuum pump and filter is under repair and is ready for use now.

The condition of submitting an affidavit in regard that parameters are fluctuating is not agreeable because the requirement of affidavit is not warranted on any of the Environment, Water or Air Act, Affidavit is a mean of recordings of evidence which can not be done for any future unpredictable event which is beyond any body’s control. 

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-380       Ni-3.2                     Cu-5.3     Cr-2.1
	TDS-2100
	TSS- 660       Ni-4.45                     Cu-6.9     Cr-3.2
	TDS-2872


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
In view of the parameter BOD & TDS are not meeting the prescribed standard at the outlet of CETP, as per monitoring conducted by DPCC laboratory in month of April, 2008, Bank Guarantee is reduced from Rs. 5 Lakh to Rs. One Lakh and confirmed to be submitted by 30.06.2008 by CETP Society.

The Society shall remove the silt from equalization tanks (one by one) & other deficiencies within a period of one month and confirm. 
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

GTK Road Indl Area CETP ( 6 MLD)
Consent status of CETP

 CETP Society has not applied for Consent to operate so far. 

A DO letter was issued on 17.07.07 to MD, DSIDC with a copy to Commissioner of Industries & President, CETP Society asking to apply for consent to operate within a month and remove the deficiencies observed. No reply received from CETP society and Commissioner of Industries regarding rectification of deficiencies. However, DSIDC has submitted a letter dated 03.08.2007 stating that the CETP has already been transferred under the CETP Act to CETP Society.
Decision of Committee taken on 19.10.2007

The unit was inspected on 19.7.07 and gross deficiencies were found. Also the Sept. report show TDS in excess of the norms . 

CETP society is also directed to submit application for Consent to Operate immediately.

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 2.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

 The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The society will submit a Bank Guarantee of Rs. Five Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done by 31.12.2007. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.  
Deficiencies mentioned in SCN issued & brief of its reply by CETP Society :

Flow at the inlet observed is very low (in the range of 2- 2.5 MLD) against the installed capacity of 6 MLD.

· We are surprised why you are writing to us as neither we are a party to construct nor to design. This is only a performance of DSIDC. How DPCC is concerned to such, this in neither to the purpose nor to the jurisdiction of DPCC.

Pressure gauges attached to DMF & ACF were found in non operational condition.
· From the day one, DSIDC provide the same as such & never support us. Further this is the question beyond the jurisdiction of DPCC as DPCC is suppose to check the quality of treated water and not the system.

The flow meter installed in the inlet of CETP was found out of order.

· From the day one , the meter is out of order. DSIDC always operated the system without any flow meter, which was never objected by you to DSIDC.

One floating aerator of equalization tank found out of order.

· DPCC team is very efficient only for inspections but is never concerned to support the society for joint inspections. However the floating aerators was repaired promptly as it is a routine wear & tear of the equipments and is maintained on regular basis.
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Sludge kept in open.

· This is unusual and un-imaginable that DPCC is concerned to such thing. Could you be kind to inform us where the sludge to be kept in & disposed off. We have no words to write on this issue as DPCC failed to provide ant site or support to us till date in spite our repeated submissions.

Poly tech as treatment chemical, is being used in place of Alum.

· DSIDC has permitted the use of polytech in place of Alum. DPCC should explain why such use of polytech is objectionable.

No flow meter installed at the outlet of CETP.

· In EPCA meeting, DPCC was announced that flow meter at outlet shall be supplied free of charge by DPCC to DSIDC as DSIDC was short of funds on this projects.

As per DPCC analysis report dt 10-04-07 TDS (2501) is not as per  prescribed norms. 
· Since the design of the plant are bad and can not perform to produce treated water as per EPA norms, it was decided during EPCA meeting and before DPCC officials that CPCB permits and exempted any limits of TDS otherwise we request DPCC to support us with their valued guidance how to deal with situation on the existing system.

Not applied for consent to operate under Air & Water Act
· Last consent obtained by DSIDC was conditional and no condition were ever fulfilled by DSIDC and plant was operated by DSIDC in complete connivance of DPCC. DSIDC should complete such conditions and apply for the same.

Individual connections with conveyance system

· This is the job of DJB. However society is ready to do the same, if inspectors are provided to us and also we should be authorized to issue consent to establish & operate to our members units jointly with your office.

Bank Guarantee 

· We will appreciate if you guide us how a society could be responsible to work for the jobs fixed for others agencies and you are initiating penalty proceedings under Delhi CETP Acts. Therefore, your demand for Bank Guarantee of Rs. Five Lacks is not only ultra virus but is no basis or with any jurisdiction. However we request you to support the society by joining us to issue permission to establish and to operate to our members units for a better coordination of members and control of quality  of water at inlet of CETP.  

Inspection status:

Observation during inspection of CETP on 18.12.07 is as follows:

The flow meter installed in the inlet of CETP was found out of order.

Pressure gauges attached to DMF & ACF are out of order & non functional condition.
Both aeration tanks are in use & motors of two aerators found removed. As reported, one motor was sent for repairing about 3-4 months back.

Sludge firstly kept in open & after drying (7-10 days) it will store in shed.

One vacuum filter is non functional condition.

Average intake in Nov. 07 – 2.1 MLD.
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Decision of Consent Management Committee in its meeting dated 09.01.2008 :

A fresh inspection may be conduced and put up in next CMC. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee.

Action Taken Report
Letter issued on 28.01.08.

Inspection status:

Observation during inspection of CETP on 07.02.2008 is as follows:

· Flow meter installed at inlet found out of order.

· Pressure gauges attached with ACFs & DMFs were found out of order & non functional condition.

· Two floating aerators (out of four) found non operational, motors of both orators (one in each tank) found removed.

· One vacuum filter found in non operational condition as filter cloth & cabinet found torned.

· Both waste water pumps installed (for lifting of waste water from thickener to equalization tank) found out of order. A sludge pump found installed as temporarily arrangement with loose pipes. 

· Total quantity effluent intake in month of Jan 08-48.41ML (Av-1.62MLD). Month of Dec08-63.65ML (Av-2.05MLD). 

DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	pH- 3.2         TSS- 482             Cu-3.6          
	BOD- 36          TDS-2990
	TSS-740
	NIL
	TSS-820              Cr-2.5
	_
	TSS-484        Cr-2.42
	_


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Letter to be issued to submit an affidavit as to why parameters are not meeting the prescribed limit. Deficiencies of inspection Report of 7 Feb 08 may be corrected by CETP within 1 month.

Action Taken Report
Letter issued on 25.03.2008. The society has submitted the reply on 16-4-2008 and stated as under :

The installed plant has no such mechanism to control the TDS and moreover the TDS of the ground water is very high so to maintain. TDS standard there is need to introduce new technology to the present system. Hence, to control the TDS standard it is beyond the control of the society due to non-effective system.

The flow meter is non- functional since its installation and have some manufacturing defect and no details of its warranty, guarantee or service centre has been provided by DSIDC till date.
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The Pressure gauges  attached to the ACF’s and DMF’s are non-functional since the trial run and have technically defective and cannot be made functional all the time. Moreover, it does not play an important role on treatment of the effluent.

The floating aerators- The plant is mechanically and electrically driven and at any point of time the fault may cause and the same is rectified without unreasonable delay.

One Vacuum Filter- There are two vacuum filters and at a time one remains functional and other is standby. Moreover, one of the vacuum filter was non-functional at the time of handing over and was repaired by the team of the society but it is only non-functioning only due to non-availability of the PVC cabinets fitted over the drum.

Waste Water Pumps- The waste water pumps got choked and stopped working due to the high depth & thick sludge in the waste water sump, so the pumps installed in the sump could not be repaired. The efforts and the steps taken by the society by installing an extra new pump should be appreciated and can not be listed under deficiency. 
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-640
	_
	TSS-412              Cr-2.7
	BOD-32  


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action.
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Lawrence Road CETP (12 MLD)

Consent status of CETP

· Consent to operate expired on 27-07-07. Applied for renewal of consent on 14.12.2007. 

Decision of Committee taken on 19.10.2007

Inspection of 12.7.07 gross deficiencies which have not been rectified the lab reports indicate several norms be flouted. 

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 2.0 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The society will submit a Bank Guarantee of Rs. Five Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done by 31.12.2007. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.  
Deficiencies mentioned in SCN issued & brief of its reply by CETP Society :

Flow observed to be in the range of 1- 1.75 MLD against installed capacity of 12 MLD.

· DSIIDC is not responsible for making individual connection by the industries to the main conveyance system leading to the CETP and has no statutory powers to issue any notice in this regard to individual industry for making the required connection. CETP Society has been advised by us for the same.

No flow meter is installed at outlet of CETP. 

· As per NEERI scheme vetted by DPCC & approved by Hon’ble Supreme Court, only one flow meter was required to be installed which has been installed by DSIIDC. In EPCA, DPCC was agreed to install the flow meter at the outlet of CETP on its own.. It is further stated that technically one flow meter is sufficient to measure the treated flow. 
One vacuum filter (out of 2) found in non operational condition.

· Since, the plant is receiving less quantity of effluent, only one vacuum filter is operated on rotational basis.

2 ACFs out of 6 nos. and 3 DMFs out of 9 nos. were found operational during the inspection.

· All the DMF & ACF are in operational condition and these are being used on rotational basis.

Small quantity of effluent going out of the premises, which is emanating from Grit Chamber, with out any treatment.

· Regarding the leak of effluent from grit chamber necessary action is being taken & the same shall be stopped soon. 
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Dosing of Bleaching powder not being carried out. Pre chlorination as well as post chlorination were found non operational.

· Pre chlorination shall be started soon. However, Post-chlorination is not done as the treated effluent is being put into drain.
· CETP doesn’t have any facility to treat the excessive BOD as it is Physico-Chemical Treatment Plant. Necessary consultation with the experts is being taken together with other treatment options by DSIIDC.

Bank Guarantee

· Submission of Bank Guarantee of Rs. 5 Lacs may please be waived off as DSIIDC is a responsible Govt. Undertaking and not a CETP Society.

Inspection status:

Observation during inspection of CETP on 18.12.07 is as follows:

The flow meter installed in the inlet of CETP was found out of order.

Vacuum filters both found operational condition.

Dosing of bleaching started from 11.12.07 for pre-chlorination

Presently 3 DMF & 2 ACFs are in use. As reported DEMF & ACFs are use on rotational basis as per the intake quantity. 

Pressure gauges attached to DMF & ACF are out of order.
As reported work of grit chamber leakage will be started within a week.

Average intake in Nov. 07 – 1.34 MLD.

High BOD Level at CETP, Lawrence Road

A meeting was taken by Chief Secretary on 29.08.2007 regarding the operation of Lawrence Road CETP. Follow up action taken was discussed in the meeting taken by Secretary (Env.) on 07.09.2007 and accordingly DO letters were issued to MD, DSIIDC on 26.09.2007. A detailed survey of the area was also conducted by SEE. A letter is received from Chief Engineer, DJB stating that the sewage of domestic area is not connected with sewage system for Lawrence Road Indl. Area. Cases of 30 unit of LRIA were discussed in the CMC (Orange) in its meeting held on 12.10.2007. As an immediate measure, at least septic tank may be installed for two Sulabh Shochalas establishments for reducing of BOD level by MCD, a letter was issued to the Commissioner of Industries on 26.12.2007 for taking up this matter with Slum Deptt., MCD under the CETP Act, 2000.

DSIIDC has submitted a letter on 05.12.07 regarding augmentation of CETP at LRIA for treatment of excessive BOD and submitted that DPCC conducted a detailed stud of the process and after which it was conveyed that the existing aeration system may be upgraded or diffuser system may be installed in the Equalization tank for treatment of BOD. The matter was referred to some consultants. DSIIDC have received the reaction from NEERI who have expressed their apprehension with the above suggestion which may not be a workable solution for this problem and instead has suggested BOD treatment though sequentional batch reactors. Matter is be examined for estimation & execution from other experts and waiting for reaction of other consultants.  

A letter has also been received from CETP Society of the area on 24.12.2007 stating that DSIIDC is considering  to modify some physical changes in the design of the plant and requesting to take the Society into confidence & provide full details of the change in process or modifications of the plant. 
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Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Certain deficiencies in the noted in the earlier inspection was communicated to DSIDC. DSIDC in its reply has stated that they have corrected the deficiencies mentioned. An another inspection of CETP was done on 03.01.2008 and following deficiencies were noted:-

The flow meter installed in the inlet of CETP was found out of order.

Pressure gauges attached to DMF & ACF are out of order.
As reported work of grit chamber leakage will be started within a week.

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during last two months are as under:
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet

	Non operational
	Non operational
	_
	BOD- 36,          TDS-2257


A letter from Member Secretary, DPCC may be issued to GM, DSIIDC for correction of deficiencies. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected. 

Action Taken Report
Letter issued on 25.01.08. However, no reply has been received.
DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	_
	BOD-33        Cl-1280          TDS-4150
	TSS-384
	TSS-108      BOD-54    TDS-3250       Sulphide-3.6
	Non operational
	Non operational
	NIL
	BOD- 36          TDS-2257


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Letter to be issued to submit an affidavit as to why parameters are not meeting the prescribed limit with a copy to the  Chairman & MD, DSIIDC. Deficiencies noted in inspection of 03 Jan 08 to be corrected by the CETP within 1 month.

Action Taken Report
Letter issued on 27.03.2008. DSIDC has submitted the reply on 29-4-2008 and stated as under 

Now the reading of the flow meter has been reset and the flow meter is working.

The defective pressure gauges have been got rectified and now all the pressure gauges of AOF & DMF are working. The pump has been installed below the Grit Chamber to take care of leakage of effluent of Grit Chamber.

DPCC awarded the work of designing CETPs in the N. C. T. of Delhi to NEERI and it was DPCC which approved the designed  parameter of the influent reaching to CETP recommended by NEERI including the influent parameter of CETP Lawrence Road DSIIDC took up the construction work of CETPs on the basis of design of NEERI which was duly approved by DPCC.

This issue of BOD has been discussed in various meetings of EPCA, Secretary  (Env.) & Chief Secretary but could not be resolved in spite of efforts put by DSIIDC. DPCC is requested to look into the options came out during these meetings made by various officials time-to-time.
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As the issue of high BOD pertains to DPCC there is no need of filing and affidavit by DSIIDC. Moreover, DSIIDC has no statutory powers as per law for issuing any direction to industries for controlling  BOD.DSIDC also requested that DPCC shall take necessary action to resolve the problem of high BOD so that the plant will be handed over to respective CETP society.

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-380
	BOD-52        Cl-1180          TDS-2310
	Non operational
	Non operational


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
In view of the parameter BOD, Cl & TDS are not meeting the prescribed standard at the outlet of CETP, as per monitoring conducted by DPCC laboratory in month of March & parameter i.e. BOD & TDS not meeting in April, 2008, Bank Guarantee is reduced from Rs. 5 Lakh to Rs. One Lakh and confirmed to be submitted by 30.06.2008 by CETP Society.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

OKHLA CETP  (24 MLD)

Consent status of CETP

· CETP Society submitted the consent application for renewal of  consent on 13-02-07.

Decision of Committee taken on 19.10.2007

The deficiencies found on inspection on 11.4.07 have not been rectified in full. The deficiencies noted on 23.7.07 may be communicated to the society. The lab report show BOD, TDS above the norms 

It was also found that against the installed capacity of 24 MLD, the CETP Society is operating it at only 3.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The society will submit a Bank Guarantee of Rs. Ten Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done by 31.12.2007. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.

Action Taken Report
As decided by the CMC , SCN was issued on 05.11.2007 and CETP Society has submitted its reply on 30.11.2007. Case of the CETP was taken up by the CMC in its meeting held on 13.12.2007.

Decision of Committee taken on 13.12.2007

CMC in its meeting on 09.10.2007 had noted certain deficiencies in the functioning of the CETP and had ordered correction of those deficiencies along with the Bank Guarantee of Rs. 10 lakh. After that, a meeting was sought by all the CETPs Societies with Chairman & Member Secretary, DPCC to air their grievances and to seek redressal. After hearing patiently and acquainting them with the need for running the CETPs efficiently and effectively, Chairman, and Member Secretary, DPCC had agreed that the case of Bank Guarantee may be reviewed if they substantially comply with the correction of deficiencies noted by CMC. In their letter received on 30.11.2007 they have informed in writing but not through an affidavit, that they have corrected the following deficiencies:-

(i) The defective aerator has been repaired.

(ii) Recorder of inlet flow meter has been repaired and now functional.

(iii) Equalization tank was under cleaning process when inspection team visited the CETP.

However, the following deficiencies are yet to be corrected for which they have given the following justification:-

Pressure gauge  

The suppliers of pressure gauge were contacted by the Society and they are of the view that pressure created in the pipe is too weak to operate the pressure gauge. Pressure gauges in ACF have not been fitted even by DSIDC. 

However, the view of the concerned CMC (MSW) is that the quantity of effluent received at CETP i.e. 2.0 to 2.5 MLD of waste water against the installed capacity of 24 MLD does not make any effect on the pressure.
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Flow meter at outlet

Regarding flow meter at outlet, in EPCA meeting it was decided that DPCC  will get it installed and cost will be borne by them. 

TDS

This plant has not been designed to treat TDS, so Society can hardly do anything on the subject. However, Prof. Gutpa, IIT feels that the plant has been designed by the NEERI for reduction of TDS which is evident from the flow chart given at figure 3.29 & 3.30 in the Phase-II report, volume –II of design of common effluent treatment plants for industrial estates in the NCT of Delhi, which shows that TDS of 234 mg/l has been reduced to 128 mg/l. 

Individual connection with conveyance system

CETP has issued public notice in English & Hindi newspapers on 17.11.07. Society has requested all units to produce documentary evidence & list of units who fail to produce this information shall be submitted to appropriate authority.

The CETP society has not submitted the Bank Guarantee of Rs. Ten lacs as sought vide SCN dated 05.11.2007. CETP has informed that they have tried to get it done and the list of defaulters may be submitted to DPCC. 

CMC feels that it is the job of CETP to influence its members and ensure individual connection with the conveyance system. It must, therefore, be done accordingly. 

In view of the fact that the partial deficiencies which are of the serious nature have been corrected, and one deficiency needs to be corrected by DPCC as ruled by EPCA, there is still some work to be done by the CETP Society for pressure gauges and individual connection to the conveyance system and containing the TDS.  The committee is of the view that the intention is to control pollution and if CETP is sincere in its efforts the Bank Guarantee may be reduced to Rs. 5 Lakh along with an affidavit indicating correction of all the deficiencies. Time may be extended up to 31st January, 2008. 

Action Taken Report
 As decided by CMC, letter was issued and reply is yet to be received.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Since time allowed to 31st January, 2008, unit may be inspected in the 1st week of February, 2008 and case may be put up next CMC. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 

Action Taken Report
Letter issued on 28.01.08. CETP society has submitted a letter on 29.01.08 informing that pressure gauges have been replaced and now functional, advised all members to ensure that they are connected to conveyance system leading to CETP, plant is well maintained but yet DPCC has not issued consent and imposed a penalty for the deficiencies / defective instruments installed by DSIDC and society is contemplated to hand over the CETP back to DSIDC/COI.
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Inspection status:

Observation during inspection of CETP on 08.02.2008 is as follows:

· All the four agitators /aerators of both equalization tanks found in operation

· Inlet flow meter found non operational condition, as informed display card of it has been send for repair about one month back. 

· DMFs (6Nos) & ACFs (7Nos) found in operation & pressure gauges found functional. As informed, DMF & ACF operate on rotational basis as per intake effluent quantity. 

· Total quantity of intake effluent during month of Jan 08 was106.87 ML & in month of Dec 07 was 88.52ML.

DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	TSS-260
	_
	TSS-424
	TDS-2390
	TSS-748
	BOD- 42          TDS-2294
	NIL
	TDS-2501


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

To be put up in next CMC (MSW) meeting.
Action Taken Report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-675
	BOD- 40          TDS-2810
	TSS-930
	BOD- 38          TDS-2152


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
In view of the parameter BOD & TDS are not meeting the prescribed standard at the outlet of CETP, as per monitoring conducted by DPCC laboratory in month of Feb., March & April 2008, Bank Guarantee is reduced from Rs. 5 Lakh to Rs. One Lakh and confirmed to be submitted by 30.06.2008 by CETP Society.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

NARELA CETP (22.5  MLD)
Consent status of CETP

Consent to establish granted on 20.01.04 for a period one year. DSIDC applied for consent to operate on 03.03.06. 

Decision of Committee taken on 19.10.2007

While the unit showed compliance of the norms in the Sept. In the inspection 13.7.07 some deficiencies were found. The unit may correct all its deficiencies by 31.12.2007, failing which a BG of Rs. 5 lakh will be impose on the unit. 

It was also found that against the installed capacity of 22.5 MLD, the CETP is operating it at only 1.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the DSIDC to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The DSIDC discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The copy should be sent to MD (DSIDC) and Comm. of Industries. 

Deficiencies mentioned in SCN issued & brief of its reply by CETP Society:

Individual connections with conveyance system

· DSIDC has already advised all industrial units to connect to the conveyance system. Since action against individual units in this regard is to be taken under Water, EP Act etc and DPCC is the competent authority for the same.

· There is no CETP Society to run the plant & in our view the provisions of CETP Act can not be implemented in this CETP. Deficiencies as described in SCN have been rectified.

Flow meter installed at inlet of CETP found out of order. 
· A new flow meter has been procured and shall be installed within 15 days at the inlet.

No chemical dosing being done due to non-availability of chemical.
· Chemical dosing has been started and being done regularly.

Significant quantity of silt/sludge found in grit chamber, equalization tanks, tube settler & aeration tank.
· Silt/ sludge accumulated in various tanks i.e. grit chamber, equalization tank, tube settler & aeration tank etc has been removed. 

Only two aerators (out of 6 nos.) found in operational condition.
· All aerators have been made functional.

All ACF (14 nos.) found not in operational during the inspection.
· Now all the ACFs are put to use as asked.

No flow meter installed at outlet of CETP. 
· Technically the flow meter at the outlet is not required.

The deficiencies mentioned are the part of routine maintenance and rectified as and when required on need basis. 

The effluent analysis report reveals that some parameters are not meeting the prescribed standard. 

· No comment given on this issue. 

Regular testing of the effluent is not being done in the laboratory situated in the CETP.
· No comment given on this issue. 
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Inspection status:

Observation during inspection of CETP on 03.01.08 is as follows:

One air blower of aeration found out of order.

Pipes for chemical dosing are chocked & manual dosing is being carried out.

Sludge pipe between tube settler & thickner found chocked.

Flow meter at inlet found out of order. A new flow meter shown during inspection & reported to be installed within 10 days.

Two aerators (out of 6) found out of order.

Pressure gauges of ACFs & DMFs found non working condition.

No flow meter installed at outlet of CETP. 
Most of sludge drying beds are completely filled with sludge.

All ACF found not in operation during the inspection and effluent is being discharged after DMF..
Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Certain deficiencies in the noted in the July inspection was communicated to DSIDC. DSIDC in its reply has stated that they have corrected the deficiencies mentioned. An another inspection of CETP was done on 03.01.2008 and following deficiencies were noted:-

One air blower of aeration tank was found out of order.

Pipes for chemical dosing are chocked & manual dosing is being carried out.

Sludge pipe between tube settler & thickner found chocked.

Flow meter at inlet found out of order. A new flow meter shown during inspection & reported to be installed within 10 days.

Two aerators (out of 6) found out of order.

Pressure gauges of ACFs & DMFs found non working condition.

No flow meter installed at outlet of CETP. 
Most of sludge drying beds is completely filled with sludge.

All ACF found not in operation during the inspection and effluent is being discharged after DMF..
As per DPCC analysis report of the sample collected in the month of Nov. 07, BOD (40mg/l) at the outlet of CETP was found exceeding the prescribed norms .

A letter from Chairman, DPCC may be issued to MD, DSIIDC for correction of deficiencies. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected. 

Action Taken Report
Letter issued on 25.02.2008.

DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	_
	_
	TSS-252
	NIL
	TSS - 288
	BOD-40
	TSS-292
	_


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Reminder letter to be issued with all deficiencies found during new inspection. 

Action Taken Report
Letter issued on 27.03.2008. DSIDC submitted the reply on 04-04-2008 and stated as under :

· There are two air blowers and being used on alternate basis. Air blower has been got  rectified. It is added that it is a routine maintenance work. Pipe for chemicals dosing are cleaned and now the chemical dosing is being done through these pipes.
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· Choking of pipes is taking place because a lot of plastic pieces are being put by the industries into the conveyance system leading to CETP. It is also added that these plastic pieces are not only choking these pipes but also creating problem in various unit operations i.e. ACF & DMF. 

· Keeping in view the quantum of effluent four nos. of aerators are sufficient enough to take care of biological treatment. 

· Regarding pressure guage of ACF’s and DMF’s found non-working condition, it is a routine maintenance problem and getting rectified day to day basis.

· Technically there is a requirement of only one flow meter which is installed. It is also mentioned that the plant doesn’t have any system for bypassing the effluent and one flow meter is sufficient enough to measure the quantum of effluent.

· The sludge shall be transferred to the sludge disposal facility whenever it will be available. Activated carbon columns are not operated in order to avoid the choking of these columns because of high receipt of plastic pieces sometimes. However these activate4d carbon columns are being operated as and when required.

· For the improvement of  BOD of the treated water efforts are being made  and hopefully the desired made and hopefully the desired BOD as per law shall be maintained continuously. Above deficiencies are the routine deficiencies which are like to happen in such a huge plant. Moreover, these deficiencies are not affecting the operation of the process as the plant is being operated at its 25%-35%.
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-320
	_
	_
	_


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action. 
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Najafgarh Road Industrial area, CETP ( 9.6 MLD)
Consent status of CETP

· DSIDC has submitted a letter dated 03.08.2007 in respect of DO letter 17.07.2007, that the EPCA has already directed not to go for further construction in view of spare capacity in other functional CETPs. As regards settling the dispute with the contractor, DSIDC looking into it as per the terms of the contract separately.

· DSIDC applied for Consent to Establish on 03-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

Report was examined by Dr. B.K Guha Committee and recommended that this area should have separate CETP, since there is no surplus capacity in the CETP in the nearby vicinity.

Decision of Committee taken on 19.10.2007

Member Secretary, DPCC to study Dr. BK Guha Committee report and discuss with Prof. S.K. Gupta. Committee will be taken up this matter in next meeting.

Action Taken Report
Report of Dr. BK Guha Committee dated 03.08.2007 examined.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Member Secretary, DPCC to write a letter to GM, DSIDC to expedite the work of CETP of the area along with B.K. Guha’s Committee report. 

Action Taken Report
Letter issued on 12.02.08. No reply.
· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Reminder letter be issued.
Action Taken Report
 Letter issued on 24.03.2008. DSIDC has submitted the reply on 29-4-2008 and stated that  EPCA has directed that the necessity of Najafgarh Road CETP should be examined with respect to the available capacity of the CETP in the neighborhood area. It is presumed that the DPCC has accepted the report of Guha Committee regarding essentiality of the CETP at Najafgarh Road. In the Minutes, which have been forwarded, the quantity and quality of the effluent to be available at the Najafgarh Road CETP for treatment has not been identified. Since it is an essential requirement , the information on this account may kindly be forwarded for taking further action. It is also pertinent to mention that the quantity and quality mentioned by NEERI in their report have been at variance with the actual site conditions and therefore, before moving further, this information is essential.  
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action.
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Naraina Industrial Area, CETP ( 21.6 MLD)

Consent status of CETP

· DSIDC applied for Consent to Establish on 02-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

·  EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and it was appraised by the representative of DSIDC that CETP is under installation and it is at final stage of construction and after commissioning of the same may be handed over to CETP Society of the area. 

Inspection of CETP was carried out by DPCC officials on 23.07.2007 and following were  observed:

· CETP was under construction.

· Most of the units of CETP mentioned in layout plan have been completed.

· With regards to civil work most of the work have been completed except road and drainage work.

· With regard to electrical work cabling & lighting work are yet to be done. Same is under progress.

· Pipe fitting under progress in chemical dosing system, sludge thickener & DMF/ACFs.

· Electrical panel was also found under installation.

· There are so many machinery are yet to be installed and also lots of works are pending as observed at site.

· The representative of the construction agency i.e. M/s. SPML told that due to non availability of funds the work is not being done fastly.

Decision of Committee taken on 19.10.2007

The CETP is reported under construction for a long time. MS may write to MD (DSIDC) to complete this work by 31.12.07 and handover to CETP society by 31.12.07.

Action Taken Report
Letter issues to DSIIDC. A letter dated 08.11.2007 has been recd from COI w.r.t. status of CETPs in Delhi wherein it was stated that   the CETP at Naraina is at final stage of construction, the same will be handed over to the CETP Society after commissioning & trial run.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

A reminder letter from Member Secretary, DPCC may be issued to GM, DSIIDC

Action Taken Report
Reminder letter issued on 07.02.08. No reply.
· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Reminder letter be issued.
Action Taken Report
 Reminder letter issued on 24.03.2008 wherein they were directed to complete the work and hand over the CETP to CETP society. . No reply is received.

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action.
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Okhla Industrial Estate CETP ( 1.2 MLD)
Consent status of CETP

· DSIDC applied for Consent to Establish on 06-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and recommended that an independent CETP may be installed for this industrial area.

Decision of Committee taken on 19.10.2007

Member Secretary, DPCC to study Dr. BK Guha Committee report and discuss with Prof. S.K. Gupta. Committee will be taken up this matter in next meeting.

Action Taken Report
Report of Dr. BK Guha Committee dated 03.08.2007 examined.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Based on B.K. Guha’s Committee report, Member Secretary, DPCC may write to EPCA for reconsideration of its decision so that necessary action can be taken w.r.t the Okhla Industrial Estate CETP. Copy of the letter may be sent to MD, DSIDC. 

Action Taken Report
Letter issued on 12.02.08.
· Decision of Consent Management Committee in its meeting dated 28.02.2008:

No action.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action.
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Anand Parvat  CETP ( 24 MLD)

Consent status of CETP

· DSIDC applied for Consent to Establish on 05.08.02.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP. 

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and recommended that an independent CETP may be installed for this industrial area.

Decision of Committee taken on 19.10.2007

Member Secretary, DPCC to study Dr. BK Guha Committee report and discuss with Prof. S.K. Gupta. Committee will be taken up this matter in next meeting.

Action Taken Report

Report of Dr. BK Guha Committee dated 03.08.2007 examined.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Based on B.K. Guha’s Committee report, Member Secretary, DPCC may write to EPCA for reconsideration of its decision so that necessary action can be taken on the Anand Parbat CETP. Copy of the letter may be sent to MD, DSIDC. 

Action Taken Report

Letter issued on 12.02.08.

Decision of Consent Management Committee in its meeting dated 28.02.2008:

Letter approved for EPCA in a different file, be issued.

Action Taken Report

 Letter issued on 13.03.2008 from the file of EPCA report & copy placed in file. 

· Decision of Consent Management Committee in its meeting dated 17.04.2008:

“There appears to be no reason to form a Society when there is no CETP in APIA. Taking this stand, we must return all the petition and applications received from CETP Society in APIA to Commissioner of Industries to windup all such Societies. The logic of such Society without CETP is totally unclear and only leads to unnecessary confusion and alleged misuse of funds of members of the Society.”
Action Taken Report

 Letter issued to the commissioner of Industries on 06.05.2008.

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action.
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Mohan Co-operative Industrial Estate CETP (1.8 MLD)
Consent status of CETP

· DSIDC applied for Consent to Establish on 06-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and recommended that the effluent from the Mohan Co-op. Industrial Estate may be treated in the CETP at Okhla Industrial Area.

Decision of Committee taken on 19.10.2007

Member Secretary, DPCC to study Dr. BK Guha Committee report and discuss with Prof. S.K. Gupta. Committee will be taken up this matter in next meeting.

Action Taken Report
Report of Dr. BK Guha Committee dated 03.08.2007 examined.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Member Secretary, DPCC to write to EPCA highlighting the recommendations of B.K. Guha’s Committee report for linking the area to the existing CETP system at OKhla. Copy of the letter may be sent to MD, DSIDC. 

Action Taken Report
Letter issued on 12.02.08.
· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Follow up. 

Action Taken Report
 Letter issued on 15.04.2008 to EPCA highlighting the recommendations of B.K. Guha’s Committee report for linking the area to the existing CETP system at OKhla. Copy of the letter sent to MD, DSIDC. No response received so far.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action.
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Udyog Vihar (Bawana) Industrial Area CETP ( 35 MLD)

Consent status of CETP

· DSIDC applied for Consent to Establish on 05.08.02.

· Consent to Establish was granted on 20.01.2004 for a period of one year.

DSIIDC has not applied for extension of consent to establish or consent to operate. 

Present status of CETP not available.   

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Member Secretary, DPCC to write a letter to GM, DSIDC to expedite the work of CETP of the area and for compliance of provisions of the Air & Water Acts.

Action Taken Report
Letter issued on 28.01.08. No reply.
· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Reminder letter to be issued.

Action Taken Report
 Reminder letter issued on 25.03.2008  to the GM, DSIDC to expedite the work of CETP of the area and for compliance of provisions of the Air & Water Acts. No reply received so far.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008
Dr. Sen Nursing home Nallah STP  (10 MLD)

Consent Status 

Consent valid up to 25-02-08. Not applied for renewal.
Decision taken  

Issue SCN for deficiencies observed during the inspection.
Action taken report

Plant was inspected on 04.12.06.

SCN issued on 02.01.2007 for the deficiencies observed during the inspection.

No reply has been received. 
As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.
Decision of CMC taken on 19.10.2007

Member Secretary, DPCC to inspect.

Action taken report

STP was inspected on  05.01.2007 and some deficiencies were observed during inspection.
Decision of CMC taken on 09.01.2008

Inspection done on 05.01.2007. Issue notice for rectification of deficiencies within 30 days time, failing which Bank Guarantee of Rs. 2 lakh will be imposed. 

Action taken report

SCN issued on 12.2.2008. Reply awaited.
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 17.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 22.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Case to be taken up in April CMC along with the reply of the unit. 

Action Taken Report

No reply received from the unit in response to SCN issued on 12.02.2008 in pursuance of decision taken on 09.01.2008.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.20008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 11.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Ask him to apply for renewal of consent under Air & Water Act and authorization under HWM Rules. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008
Delhi Gate Nallah STP, (2.2 MGD)

Consent Status 

Consent to operate issued on 15.2.2007 & valid upto 11.10.09.

Decision taken  

Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days and also to maintain the log book properly

Action taken report

Consent Issued. As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

No action. 

Action taken report

-
Decision of CMC taken on 09.01.2008

No action.
Action taken report

No action.
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 17.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 22.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

No action. 
Action Taken Report

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.20008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 11.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

KONDLI STP , Ph-I (10MGD)
Consent Status 

Applied for consent to operate on 19.04.06.

Decision taken on 16.01.2007  

Issue SCN giving last opportunity to remove the deficiencies observed during inspection
Action taken report

SCN issued on 15-02-07. Reply received on 23-02-07. The following submissions have been made:-

· Power back up system, with flow meters, is being provided in due course of time.

· All aerators and PST are in working condition now. 

· Presently, treated effluent is being used for horticulture purpose within the premises of plant. Further reuse of treated effluent is under consideration with DDA.

· Work order has already been placed for renovation of digester and gas holders. 

· Plant has submitted required information as per consent application along with an affidavit.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Consent to operate will be granted once the deficiencies noted in SCN are finally implemented and confirmed to DPCC.
Action taken report

Letter issued on 06.11.2007. Reply recd on 07.12.07. The following submissions have been made:-

The flow meter installed at inlet & outlet are working properly. Case of providing power backup to the flow meter is under process.

All aerators &PST are in working order.

Treated effluent is being used for horticulture within premises, DDA laid pipes to take 2.6 lac Gallon per day, proposed to supply 8 MLD to IL&FS for proposed Gazipur MSW complex. Requested for grant of consent.
Decision of CMC taken on 09.01.2008

The unit has complied with the deficiencies but not filed an affidavit. STP may be inspected and case may be put up in next CMC.
Action taken report

Inspected on 20-2-2008. The observation are as follows : 

· Flow meter at inlet and outlet of STP found installed and operational, work of providing of UPS as power backup going on.

· all aerators found functional however one aerator was found closed as standby.

· All the digesters (three) and gas holder(one) of phase-1 are under refurbishment and work to be awarded shortly as informed. 

· As reported DDA has laid their network for reuse of approximate 2.6 Gallon per Day for horticultures purposes, pump house has been installed by DDA. 

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 31.12.2007), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), except BOD (35 mg/l) other parameters are within the prescribed standard.
Contd..2..

..2..

KONDLI STP , Ph-I (10MGD)
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Ask the unit to file an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

Letter issued on 24.03.2008. Unit has submitted reply on 29.04.08 (without affidavit) and stated that flow meters with power & back up installed at inlet and outlet are working properly, all aerators & PST are in working order, for renovation of digester & gas holders tender is under process for award the work to the lowest tenderer, DDA has laid their network for horticulture and 8 MLD will be supplied to M/s IL&FS for proposed MSW complex at Gazipur. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008),  parameters BOD (32 mg/l) is exceeding the prescribed standard (30 mg/l).
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 19.03.2008), STP found non operational during monitoring.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

The unit may be asked to explain why the STP was non operational and how is the waste water getting disposed off  as observed during inspection by DPCC Laboratory on 19.03.2008, for conducting monitoring. STP to file reply by 30.06.2008. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

KONDLI STP, Ph-II  (25 MGD)

Consent Status 

Applied for consent to operate on 19.04.06.

Decision taken on 16.01.2007  

Issue SCN giving last opportunity to remove the deficiencies observed during inspection.
Action taken report

SCN issued on 15-02-07. Reply received on 23-02-07. The following submissions have been made:-

· Power back up system, with flow meters, is being provided in due course of time.

· All aerators are in working condition now. 

· Work order has been placed for renovation of five sludge digesters and 2 gas holders.

· Presently, treated effluent is being used for horticulture purpose within the premises of plant. Further reuse of treated effluent is under consideration with DDA.

· Work order has already been placed for renovation of digester and gas holders. 

· Plant has submitted required information as per consent application along with an affidavit.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Consent to operate will be granted once the deficiencies noted in SCN are finally implemented and confirm to DPCC.
Action taken report

Letter issued on 06.11.2007. Reply recd on 07.12.07. The following submissions have been made:-

The flow meter installed at inlet & outlet are working properly. Case of providing power backup to the flow meter is under process. All aerators &PST are in working order. Treated effluent is being used for horticulture within premises, DDA laid pipes to take 2.6 lac Gallon per day, proposed to supply 8 MLD to IL&FS for proposed Gazipur MSW complex. Requested for grant of consent.
Decision of CMC taken on 09.01.2008

The unit has complied with the deficiencies but not filed an affidavit. STP may be inspected and case may be put up in next CMC.
Action taken report

Inspected on 20-2-2008. The observation are as follows :

Flow meter at inlet and outlet of STP found installed and operational, work of providing of UPS as power backup going on.

All aerators found functional however one aerator was under maintenance.

All the digesters (five) and gas holder(two) of phase-II are under refurbishment and work to be awarded shortly as informed

As reported DDA has laid their network for reuse of approximate 2.6 Gallon/day for horticultures purposes, pump house has been installed by DDA. 

Work of renovation of sludge drying beds was going on and will be completed within 2 months.
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 31.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Ask the unit to file an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Contd..2..

..2.. 
KONDLI STP , Ph-II (10MGD)
Action Taken Report

Letter issued on 24.03.2008. Unit has submitted reply on 29.04.08 (without affidavit) and stated that flow meters with power & back up installed at inlet and outlet are working properly, all aerators & PST are in working order, for renovation of digester & gas holders tender is awarded and likely to be completed by September, 2008, DDA has laid their network for horticulture and 8 MLD will be supplied to M/s IL&FS for proposed MSW complex at Gazipur. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 19.03.2008), STP found non operational during monitoring.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

The unit may be asked to explain why the STP was non operational and how is the waste water getting disposed off  as observed during inspection by DPCC Laboratory on 19.03.2008, for conducting monitoring. STP to file reply by 30.06.2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

KONDLI STP, Ph-III , (10 MGD)
Consent Status 

Consent issued on22.09.05 and valid up to 02-12-07.Applied for renewal of Consent on 16.11.2007.
Decision taken  

Issue SCN to the plant with a copy to CE, DJB
Action taken report

SCN issued on 13-03-07.

Reply received on 03-04-07. The following submissions have been made:-

Power back up system, with flow meters, is being provided. 

All aerators are in working condition now. Report is being submitted month wise. 

Sludge analysis is being carried out in the lab of DJB at STP Kondli and same is being forwarded to Director (T & QC) DJB. However, a copy of report from July 06 to Feb 07 is enclosed herewith. 

Record is being maintained at Laboratory under the supervision of ACWQA Kondli plant.  

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Consent to operate will be granted once the deficiencies noted in SCN are finally implemented and confirm to DPCC.
Action taken report

Letter issued on 06.11.2007. Reply recd on 07.12.07. The following submissions have been made:-

The flow meter installed at inlet & outlet are working properly. Case of providing power backup to the flow meter is under process.

All aerators &PST are in working order.

Treated effluent is being used for horticulture within premises, 

DDA laid pipes to take 2.6 lac Gallon per day, proposed to supply 8 MLD to IL&FS for proposed Gazipur MSW complex. Requested for grant of consent.
Decision of CMC taken on 09.01.2008

The unit has complied with the deficiencies but not filed an affidavit. STP may be inspected and case may be put up in next CMC.

Action taken report

Flow meter at inlet and outlet of STP found installed and operational, work of providing of UPS as power backup going on.

All aerators found functional, Digesters (three) and gas holder(2) of phase III found functional. 

Bio-gas generated is burnt at site. As informed, a generator is purposed to install in near future at Phase-IV STP (45 MGD) to generate electricity by bio-gas for operation of said phase-IV STP.

As informed the work of phase-IV STP will be awarded shortly and schedule time for construction is 2 years. 

DDA has laid their network for reuse of approximate 2.6 Gallon per Day for horticultures purposes and pump house has been installed by DDA. 

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 31.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), except TSS (54 mg/l) other parameters are within the prescribed standard.
Contd..2..

..2..

KONDLI STP , Ph-III (10MGD)
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be issued to the unit for submitting an affidavit as to why the parameters are not meeting the prescribed limit and also to file an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

Letter issued on 24.03.2008. Unit has submitted reply on 29.04.08 (without affidavit) and stated that flow meters with power & back up installed at inlet and outlet are working properly, all aerators & PST are in working order, the digesters and gas holders are working properly, DDA has laid their network for horticulture and 8 MLD will be supplied to M/s IL&FS for proposed MSW complex at Gazipur. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 19.03.2008), STP found non operational during monitoring.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

The unit may be asked to explain why the STP was non operational and how is the waste water getting disposed off  as observed during inspection by DPCC Laboratory on 19.03.2008, for conducting monitoring. STP to file reply by 30.06.2008. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Nehru Vihar, Oxidation Pond STP (13.5 MLD)

Consent Status 
Consent issued on21.09.05 and  valid up to 28.11.07. Applied for renewal of consent on 25.10.2007.

Decision taken  

-
Action taken report

· Plant was inspected on 15.11.06.

· SCN issued on 26.12.2007 as number of deficiencies were observed during the above said inspection.

· Plant has not submitted any reply. 

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.
Decision of CMC taken on 19.10.2007

SEE  to inspect.
Action taken report

Inspected on 03.01.2008.  Applied for renewal of consent on 25.10.2007.
Decision of CMC taken on 09.01.2008

The unit was inspected on 03.01.2008 by SEE & deficiencies were noted. Issue letter to DJB that if the STP will correct the deficiencies within 30 days, application for consent for renewal will be considered accordingly.
Action taken report

Letter issued on 12-2-2008. No Reply received.
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 17.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Reminder letter to be issued to the unit for submitting an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

 Letter issued on 25.03.2008.

Unit has submitted reply on 03.04.08 (without affidavit) and submitted that approach road to the outlet point has been cleared and are being maintained properly, photographs of the site enclosed, after the de-silting of oxidation pond no. 9 the DJB has provided the bio-remediation treatment of the sewage water at the inlet channel of the oxidation pond and de-silting of the oxidation ponds is not felt necessary at this stage. However, the result of the final effluent of the outlet of the oxidation pond are within the prescribed limit and requested to grant the consent.  

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard.
Contd..2..

\

..2..

Nehru Vihar, Oxidation Pond STP (13.5 MLD)

As per DPCC Analysis report, dated 09.04.2008 (sampling done on 17.03.2008), all parameters are within the prescribed standard.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

The de-silting of oxidation pond should be done in a phased manner for better treatment. A time bound program is to be submitted in this regard within period of one month. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Keshopur STP (72MGD (40+20+12)

Consent Status 

Consent issued on 21.09.05 & expired on 24-09-07 for 60 MGD. 
Applied for renewal of consent on 7-1-2008.
Decision taken  

-
Action taken report

· Plant inspected by DPCC officials on 5.12.2006.

· SCN issued on 02.1.2007 as number of deficiencies     were observed.

· Plant has not submitted any reply.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

· However, no consent application for the STP of 12 MGD capacity. DPCC lab reported that said STP was found abundant during sampling in Sept 2007. 

Decision of CMC taken on 19.10.2007

Ask for renewal of consent. Unit may also be asked to rectify the deficiencies as communicated vide SCN dated 2.1.07. STP may give time of one month to do so.
Action taken report

Letter issued on 07.11.2007.  Submitted application for renewal of consent by post, (ID No. 24675 dated 07.01.2007) & as decided, letter for deficiencies issued on 08.01.08. No comments about the deficiencies mentioned in the letter.

Decision of CMC taken on 09.01.2008

Letter was issued on 07.11.07 for correction of deficiencies. No reply received. If the unit does not file an affidavit within 30 days, Bank Guarantee of Rs. One Lakh under Water Act will be imposed & further action will be taken.
Action taken report
Letter issued on 7-2-2008. Reply awaited.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 01.01.2008), all parameters are within the prescribed standard for phase-I & Phase-II. Phase-III STP (12 MGD) found non operational during operational.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 23.01.2008), all parameters are within the prescribed standard for phase-I. For Phase-II, TSS964mg/l) & BOD ( 40 mg/l) are exceeding the prescribed norms. Phase-III STP (12 MGD) found non operational during operational.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be issued to the unit for submitting an affidavit as to why the parameters are not meeting the prescribed limit and also to file an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

 Letter issued on 24.03.2008. No reply has been received from the unit. 

A letter received from National River Conservation Directorate, MOEF, Govt of India dated 25.04.2008 regarding construction and augmentation of treatment capacity (72 MGD) of STP at Keshopur under YAP-II in Delhi. DJB has submitted a DPR for treatment of sewage in order to meet standards of 20 mg/l and 30 mg/l for BOD and SS respectively.  However, there is inadequate provision for disinfection of Faecal Coliform. NRCD has requested that details of standards and specific guideline issued by DPCC to DJB with regard to improve the water quality of Yamuna may be intiamated to the NRCD so that they can consider their proposal. 
Contd..2..

..2..

Keshopur STP (72MGD (40+20+12)

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard for phase-I & Phase-II. Phase-III STP (12 MGD) found non operational during operational.
As per DPCC Analysis report, dated 09.04.2008  (sampling done on 18.03.2008), all parameters are within the prescribed standard for phase-I & Phase-II. Phase-III STP (12 MGD) found non operational during operational.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

The unit may be asked to explain why the STP Phase-III (12 MGD) was non operational and how is the waste water getting disposed off  as observed during inspection by DPCC Laboratory on 18.03.2008 for conducting monitoring. STP to file reply by 30.06.2008. 

An appropriate reply for MOEF will be drafted by SEE for this STP and put up on file for approval before issue. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Mehrauli  STP (5 MGD)
Consent Status 

Consent issued on 20.03.2007 & valid upto 15.12.09.

Decision taken  

Issue consent to operate subject to the following consent conditions as well as comments:

1. Install mechanical sludge dewatering system.

2. Ensure proper storage of dry sludge.                

3. Examination of the issue related to low capacity utilization and quick resolution of the problem in consultation with related agencies.                                  

Comments:-

 a. DPCC would appreciate if DJB takes steps to generate gas form the STP.                                                                                                   
b. DJB would make all efforts to reuse the treated effluents in the nearby parks and farm houses.                                              

Action taken report

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Mehrauli STP has not replied to the consent conditions imposed on 20.3.07. STP may be asked to reply within one month positively. 

Action taken report

Letter issued on 06.11.2007. Reply received on 28.12.2007 and submitted the action taken report w.r.t. compliance of consent conditions.  
Decision of CMC taken on 09.01.2008

The matter of low intake quantity of sewage at STPs will be taken up in next CMC (MSWM) Meeting with the DJB & MCD.
Action taken report

Meeting notice issued to invites DJB and MCD Officials.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 24.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be Member (Drainage) with a copy to Sh. V. K. Jain, SE (E&M), DJB who have  attend the meeting) by Member Secretary, DPCC for seeking reasons of low intake quantity of sewage & under utilization of STP capacity.   

Action Taken Report

 Letter issued on 31.03.2008. No reply received so far.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 24.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

MS to issue reminder to Member (Drainage), DJB on last decision of CMC dated 29.02.2008 for seeking reasons of low intake quantity of sewage & under utilization of STP capacity.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Yamuna Vihar Phase –I STP (10 MGD)

Consent Status 

Consent issued on 28.2.2007 & valid upto 16.11.07. Applied for renewal of consent on 25.10.2007.  
Decision taken  

Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days.
Action taken report

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

STP has not replied to consent conditions imposed on 28.02.07. STP may be asked to reply within one month positively. 

Action taken report

Letter issued on 06.11.2007. Reply received on 28.12.2007 and submitted the action taken report w.r.t. compliance of consent conditions. Applied for renewal of consent on 25.10.2007.  
Decision of CMC taken on 09.01.2008

SEE to inspect and to submit report in the next CMC (MSW) Meeting.
Action taken report

Inspected on 19-2-2008. The observation are as follows: 

All aerators found in operation. 
Ultrasonic flow meters installed at inlet and outlet of STP. As informed magnetic flow meter van not be provided being open channel discharge.
Bio-gas generated in plant is burnt at site, however as informed DJB has plant to install generators(3 nos. x 1000 KVA) for generation of electricity from bio-gas of phase-I&II and same will be installed in next two months. 
All 12 SDBs were found filled with Sludge as reported STP is facing problem w.r.t lifting of sludge/manure. 
Regarding reuse of treated effluent, an effluent pump house is under installation near the STP.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 31.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be issued to the unit for submitting an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

 Letter issued on 25.03.2008. No reply received.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 27.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 19.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Yamuna Vihar Phase –II STP  (10 MGD)

Consent Status 

Consent issued on 28.2.2007 & valid upto 28.12.09.

Decision taken  

Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days.
Action taken report

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), plant is not meeting the prescribed standard.

Decision of CMC taken on 19.10.2007

The unit has not replied to consent conditions imposed on 28.2.07. The unit is also not meeting with the prescribed standards. SCN may be issued u/s 33 A of Water Act for remedial action within one month. 

Action taken report

Letter issued on 07.11.2007. Reply received on 28.12.2007 and submitted the action taken report w.r.t. compliance of consent conditions.  
Decision of CMC taken on 09.01.2008

SEE to inspect and to submit report in the next CMC (MSW) Meeting.
Action taken report

Inspected on 19-2-2008. The observation are as follows : 

Ultrasonic flow meters installed at inlet and outlet of STP, commissioning is expected within a week. 

All aerators found operational. 

A new fine screen installed after primary screen section. 

Bio-gas generated in plant is burnt at site, however as informed DJB has plant to install generators(3 nos. x 1000 KVA) for generation of electricity from bio-gas of phase-I&II and same will be installed in next two months. 
SDBs were found filled with Sludge as reported STP is facing problem w.r.t lifting of sludge/manure. 
Regarding reuse of treated effluent, an effluent pump house is under installation near the STP.
Acoustic enclosures installed with the DG sets of 7.5 KVA and 160 KVA.
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 31.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be issued to the unit for submitting an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

Letter issued on 24.03.2008. No reply received so far. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 27.02.2008), parameters BOD (34 mg/l) is exceeding the prescribed standard (30 mg/l).
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 19.03.2008), parameters BOD (33 mg/l) is exceeding the prescribed standard (30 mg/l).
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Ask the unit to file explanation why BOD is exceeding the standard in the month of March & April, 2008 by 30.06.2008. Call on July, 2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Rithala STP– Ph-I, (40 MGD)

Consent Status 

Previous Consent valid upto 04.05.06. Applied on 29.06.2006 for renewal of consent.
Decision taken  

Issue SCN giving last opportunity to remove deficiencies observed during inspection.

Action taken report

SCN issued on 15.02.07.Reply received on 09.03.2007 & following submissions have been made:-
Necessary action initiated for rectification of flow meter. Repair of 3 aerators is underway.
Secondary settling tanks have been operational after rectification. Gas holders are under repair. 5 MGD of treated effluent is being given to DDA for horticulture purpose. In addition to some quantity being lifted by DDA through tankers. Gas collection improved. 1200 m3 gas is being generated per day and sent to Phase – II for power generation.
As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Unit was given last opportunity to correct deficiencies. A reply received on 9.3.07 indicates that some remedial action has been taken. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 

Action taken report

Letter issued on 07.11.2007. Reply received on 26.12.2007 and submitted affidavit to confirm correction of deficiencies. Further requested for exemption of Bank Guarantee as all defects/ deficiencies attended.  
Decision of CMC taken on 09.01.2008

MS, DPCC  to inspect  and submit the report in next CMC (MSW) Meeting.
Action taken report
Inspected on 21-2-2008. The observation are as follows :

Ultrasonic flow meters found operational. 

18 Aerators (out of 24) found operational, as informed aerators are operated on rotational basis as per requirement. 

Gas generated in phase-I is transferred to phase-II for operation of generators. 

One sludge digester found under maintenance. 

Approximate 1200 cubic meter gas is generated per day. 

Average intake effluent intake in jan,’2008 was 17.1 MGD.

One gas holder found not in use and as informed it is to be reconstructed /refurnished. Treated effluent (5MGD) is used by DDA for horticulture. It is purposed that 25 MGD treated effluents will be supplied to Proposed Pragati Power Projects, Bawana and 2 MGD to NDPL.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007) except TSS (62 mg/l), other parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 29.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to the Member (Drainage) for seeking reasons of low intake quantity of sewage & under utilization of STP capacity. Letter to be issued to the unit for submitting an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Contd..2..
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Rithala STP– Ph-I, (40 MGD)

Action Taken Report

 Letters issued on 26.03.2008. 
Reply received on 31.03.2008 stating that DJB has rectified all its deficiencies. DJB has requested that exemption may be granted to submit Bank Guarantee as DJB is running the STP for public service purpose and have no profit motive unlike other private installation where these norms are generally applicable.  DJB has already submitted an affidavit regarding rectification of deficiencies. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 28.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 17.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Rithala  STP– Ph-II, ( 40 MGD)

Consent Status 

Previous Consent valid upto 21.01.06. Applied for renewal of consent on 20.01.2006. 

Decision taken  

Issue SCN giving last opportunity to remove the deficiencies observed during inspection

Action taken report

SCN issued on dated 15-02-07. Reply received on 22-03-07. The following submissions have been made:-

The defective flow meter at treated effluent channel made operational. Both sludge thickeners are in working condition now. Sludge de-watering unit is operated only during monsoon season. Matter wrt reuse of treated effluent is under planning stage. Electricity is being generated as per    raw sewage availability. As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Unit was given last opportunity to correct deficiencies. A reply received on 22.03.07 indicates that some remedial action has been taken. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 

Action taken report

Letter issued on 07.11.2007. Reply received on 26.12.2007 and submitted affidavit to confirm correction of deficiencies. Further requested for exemption of Bank Guarantee as all defects/ deficiencies attended.  
Decision of CMC taken on 09.01.2008

MS, DPCC  to inspect  and submit the report in next CMC (MSW) Meeting.
Action taken report

Inspected on 21-2-2008. The observation are as follows :

Ultrasonic flow meters operational. 

Primary Settling Tanks and Final Settling tanks found operational. 

One aeration tank out of four found not in use and as informed tank is under cleaning and not in use from last six months. 

Three generators (each 890KWH) installed for generation of electricity from bio-gas and found operational.

Total power requirement per day for phase-II is approx. 34000 KWH/ day (for 40 MGD effluents) and average power generation from bio-gas was 14000 KWH/ day. As informed actual requirement for power is 20,000 to 25,000 KWH/ day as per the average intake.  

Approximate 8000 cubic meter gas is generated per day. 

Average intake effluent intake in Jan, 2008 was 23.64 MGD. 

Treated effluent (5MGD) is used by DDA for horticulture. It is purposed that 25 MGD treated effluents will be supplied to Proposed Pragati Power Projects, Bawana and 2 MGD to NDPL.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 29.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be Member (Drainage) for seeking reasons of low intake quantity of sewage & under utilization of STP capacity. Letter to be issued to the unit for submitting an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Contd..2..
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Rithala STP– Ph-I, (40 MGD)

Action Taken Report

Letters issued on 26.03.2008. 

Reply received on 31.03.2008 stating that DJB has rectified all its deficiencies. DJB has requested that exemption may be granted to submit Bank Guarantee as DJB is running the STP for public service purpose and have no profit motive unlike other private installation where these norms are generally applicable.  DJB has already submitted an affidavit regarding rectification of deficiencies. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 28.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 17.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Pappankalan STP ( 20 MGD)

Consent Status 

Previous Consent valid upto 09.12.04. Applied for renewal of consent on 10.12.2004. 

Decision taken  

Issue SCN to SE, a copy to Chief Engineer giving last opportunity to rectify the deficiencies

Action taken report

SCN issued on 15.02.07. No reply received. 

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

While the unit is applied for consent he has not corrected deficiencies. Unit was given last opportunity to correct deficiencies. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 

Action taken report

Letter issued on 07.11.2007. Reply received on 26.12.2007 and submitted affidavit to confirm correction of deficiencies. Further requested for exemption of Bank Guarantee being a Govt. deptt. Under GNCTD. Submitted application for renewal of consent by post, (ID No. 24674 dated 07.01.2007) & as decided, letter for deficiencies issued on 08.01.08.
Decision of CMC taken on 09.01.2008

EE to inspect and report submit in next CMC (MSW) Meeting.
Action taken report

Aerators 22 nos  found in operation and 2 are under maintenance. 

Ultrasonic flow meter found operational. 
Sewage intake is low (14-15MGD) compared to installed capacity, as reported by Sh. Katakwal, EE DJB, this is due to the no population in the catchment area i.e. Dwarka. Presently they are taking sewage from Najafgarh drain also. 
All the digester found under use, however biogas generated is burned in the plant through burners as the provision of supply of  biogas is not provided so far due to less occupancy in the nearby vicinity of  STP. 
Acoustic enclosure provided with the DG set of 125KVA. 
As reported, DDA has constructed for reservoirs for reuse of treated effluent.     

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 23.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

To ensure the maximum capacity utilization of the installed STP near Najafgarh nallah, STPs may be identified and accordingly letter may be written to CEO, Delhi Jal Board for taking the required quantity of water from Najafgarh Drain. 

Letter to Member (Drainage) for seeking affidavit for the reasons of low intake quantity of sewage & under utilization of STP capacity after inspection of the STP personally. Case to be taken up in April CMC.

Action Taken Report

Letters issued on 26.03.2008. 

Unit has submitted its reply along with an affidavit on 15.04.2008 stating that the reason for low intake quantity of sewage and under utilization of 20 MGD STP after inspection along with Member (Draining) are as under :-

Contd..2..
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Pappankalan STP ( 20 MGD)

(i) The encatchment area of this 20 MGD STP is not fully developed, as and when area is fully developed, the capacity of STP would full be utilized.

(ii) Presently, they are lifting approx. 10 MGD sewage water from Palam Drain / Nalah for this STP and treating about 16 MGD sewage at this STP.
As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 26.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Najafgarh STP, ( 5 MGD
Consent Status 

Applied for consent to operate on 29.11.2004. 

Decision taken  

Issue SCN to SE, a copy to Chief Engineer giving last opportunity to rectify the deficiencies.

Action taken report

SCN issued on 15.02.07. No reply received.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

While the unit is applied for consent he has not corrected deficiencies. Unit was given last opportunity to correct deficiencies. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 

Action taken report

Letter issued on 07.11.2007. Submitted affidavit on 09.01.2008 to confirm correction of deficiencies. Deposited fee on 08.01.08 for conducting effluent analysis by DPCC lab.

Submitted application for renewal of consent by post, (ID No. 24673 dated 07.01.2007) & as decided, letter for deficiencies issued on 08.01.08.
Decision of CMC taken on 09.01.2008

EE to inspect and report submit in next CMC (MSW) Meeting.
Action taken report

All 16 aerators found operational. 
Average sewage in take is 1.5MGD to 2.0MGD. 
As reported Sewer lines are yet to be installed in catchment area of STP and presently they are taking sewage from Najafgarh and Dhrampura Drain. 
One DG Set found installed in dismantled conditions and of no use. 
Only single power supply line provided and power failure is approx. 100-125hr/ month, as per logbook. 

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 23.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

To ensure the maximum capacity utilization of the installed STP near Najafgarh nallah, STPs may be identified and accordingly letter may be written to CEO, Delhi Jal Board for taking the required quantity of water from Najafgarh Drain. 

Letter to Member (Drainage) for seeking affidavit for the reasons of low intake quantity of sewage & under utilization of STP capacity after inspection of the STP personally. Case to be taken up in April CMC.

Action Taken Report

Letters issued on 26.03.2008. No reply received so far.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 26.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Ask the unit to file reply sought by CMC on 29.02.2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Nilothi STP (40 MGD)

Consent Status 

Consent expired in 02-12-06. Applied for renewal of consent on 26-11-2007.
Decision taken  

-
Action taken report

Plant was inspected on 17.11.2006.

SCN was issued on 26.12.06, as numbers of deficiencies were observed.

Plant has not submitted consent application for renewal of consent.

As per inspection by DPCC laboratory dated 19.09.2007 it reveals that the plant was non operational during the monitoring. 

Decision of CMC taken on 19.10.2007

The unit was issued SCN on 17.11.2006 and the reply received indicates that some deficiencies have been corrected. SEE to inspect and submit a report on file for necessary action.  The unit may ask to apply for renewal of consent immediately.
Action taken report

Letter issued on 07.11.2007. no reply received. Inspected on 04.01.2007 and some deficiencies were observed during inspection. Not applied for renewal of consent.
Decision of CMC taken on 09.01.2008

Inspection was done by SEE on 04.01.2007 and the points were noted which may be communicated to the STP to follow up the points.  
Action taken report

Letter issued on 7-2-2008. No reply received.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 21.11.2007), Except TSS (64 mg/l) & BOD (34 mg/l) others parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 24.01.2007), Except BOD (33 mg/l) others parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

To ensure the maximum capacity utilization of the installed STP near Najafgarh nallah, STPs may be identified and accordingly letter may be written to CEO, Delhi Jal Board for taking the required quantity of water from Najafgarh Drain. 

Reminder letter to be issued to the unit to apply for consent, for submitting an affidavit as to why the parameters are not meeting the prescribed limit and also to file an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

Letters issued on 26.03.2008. No reply received so far.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 28.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 18.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Ask the unit to file reply sought by CMC on 29.02.2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Rohini STP (15 MGD)

Consent Status 

Plant has submitted application on 01-05-07 for consent to operate. 

Decision taken  

CE, DJB was asked to apply for consent, who agreed to do the needful.
Action taken report

As per DPCC laboratory report, during the last several occasions, plant found non operational. Hence, no monitoring report available with DPCC. However plant has submitted analysis report of its own. Treated effluent quality is as per norms laid down.
As per inspection by DPCC laboratory dated 21.09.2007 it reveals that the plant was non operational during the monitoring. 

Decision of CMC taken on 19.10.2007

SEE to inspect and report on file.
Action taken report

Inspected on 04.01.2007.

Decision of CMC taken on 09.01.2008

Inspection was done by SEE on 04.01.2007 and the points were noted which may be communicated to the STP to follow up the points.  
Action taken report

Letter was issued on 12-2-2008. No reply received.

As per DPCC Analysis report, dated 11.01.2008 STP was found non operational during inspection on 21.09.2007.
As per DPCC Analysis report, dated 25.02.2008 STP was found non operational during inspection on 29.01.2007.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Sh. Aditya Narayan Singh, Scientist, Deptt of Env., will inspect the STP & submit report on file. Based on that, decision will be taken to write letter to Member (Drainage), DJB. Case to be taken up in April CMC.

Action taken report

Inspected by Sh. A. N. Singh.

As per DPCC Analysis report, dated 18.03.2008 (visited on 28.02.2008), STP was found non operational during inspection on 21.09.2007.
As per DPCC Analysis report, dated 09.04.2008 (visited on 17.03.2008), STP was found non operational during inspection on 21.09.2007.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

The STP is not getting adequate water as per the installed capacity. As per the inspection report it was found that there is lack of coordination between DJB and DDA for getting adequate water at STP. Issue letter to both DJB and DDA that they make best possible efforts to ensure that the capacity of the STP plant is better utilized in pubic interest. Call Ex. Engineer of Rohini Zone from DJB & DDA in next CMC (MSW) meeting. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Coronation Pillar STP (40 MGD)

Consent Status 

Consent to operate issued on 28.2.2007 valid upto 12.03.2009.

Decision taken  

Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days and also to maintain the log book properly.

Action taken report

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

No action. 

Action taken report

-
Decision of CMC taken on 09.01.2008

No action. 

Action taken report

No action

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 17.12.2007), all parameters are within the prescribed standard. Phase-III (10 MGD) found non operational during sampling.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be Member (Drainage) for seeking affidavit for the reasons of low intake quantity of sewage & under utilization of STP capacity (only 10 MGD). 
Action Taken Report

 Letter issued on 25.03.2008. 
Unit has submitted its reply along with an affidavit on 11.04.08 & informed that the commo0n area SPS of NSTP are Jahangirpuri, Nehru Vihar, Adarsh Nagar, Model Town, R.U. Nagar. Out of these trunk sewers i.e. UTS & NTS and Jahangirpuri Trunk Sewers are settled resulting into less flow of sewage. The rehabilitation of UTS/WTS is in progress which may increase sewer flow. Also the tenders on rehabilitation of Jahangirpuri Trunk Sewer have been called for which work will be awarded in near future. However, all the sewage coming to the STP is fully treated without by-passing any sewage. 
As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard for Phase-I, II,III and old clarifier.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 18.03.2008), all parameters are within the prescribed standard for Phase-I, II,III. BOD (32 mg/l) is exceeding the prescribed norms for old clarifier.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Let the unit file reply by 30.06.2008, why the BOD is exceeding the prescribed norms in the monitoring conducted by DPCC Laboratory on 18.03.2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Vasant Kunj STP (5.2 MGD)

Consent Status 

Consent issued on 22.09.05 & valid up to 11-12-07.Applied for renewal on 29-1-2008.

Decision taken  

-

Action taken report

Plant was inspected on 14.11.06.

SCN issued on 26.12.2007 as number of deficiencies were observed during the above said inspection.

Plant has not submitted any reply. 

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Unit was given last opportunity to correct deficiencies. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 

Action taken report

Letter issued on 06.11.2007. No reply received.
Decision of CMC taken on 09.01.2008

EE to inspect and put up in next CMC (MSW) meeting.
Action taken report

Inspected on 22-1-2008 and observations are as under: 

Flow meter installed for 2.2. MGD plant found operational, however flow meter of 3 MGD found non-operational condition. 

4 aerators (out of 8) for 2.2 MGD and 4 aerators (out of 10) found out of order.

Logbook maintained for operation of pumps etc.

Treated effluent discharge in drain leading to Sanjay Ban as reported.

Representative of DJB not shown the records wrt removal of sludge/ manure from the plant.

Applied for renewal of consent on 29.01.2008.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007), all parameters are within the prescribed standard for phase-I (2.2 MGD) plant. However for phase-II (3.0 MGD) plant TSS (65 mg/l) & BOD (34 mg/l) are exceeding the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 24.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue notice for non operation of flow meter & aerators, to file an affidavit w.r.t. correction of deficiencies within one month & reason for non submission of Bank Guarantee. Case to be taken up in April CMC.
Action Taken Report

 Letter issued on 25.03.2008. Reply received on 24.04.2008 without affidavit. 
As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (visited on 18.03.2008), STP was found non operational.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

The unit may be asked to explain why the STP was non operational and how is the waste water getting disposed off  as observed during inspection by DPCC Laboratory on 18.03.2008, for conducting monitoring. STP to file reply by 30.06.2008. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Narela STP (10 MGD)

Consent Status 

Previous Consent valid upto 14.01.2005. Applied for renewal of consent on 14.01.2005 and issued on 7-11-2007 and valid up to 13-1-2008.Applied for renewal of consent on 3-1-2008.
Decision taken  

Issue SCN giving last opportunity to remove the deficiencies observed during inspection.
Action taken report

SCN issued on 20-03-2007. Reply received on 18-05-07 The following submissions have been made:-

Flow meter at inlet & outlet of STP are in working condition.                            

Treated effluent is being used for irrigation at the plant and possibility is being explored for its use by DDA or other Civil Agency.

Possibility is being explored for installing mechanical sludge dewatering system at the plant.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Renewal of the consent granted with clear condition that the plant shall operate properly and efficiently.
Action taken report

Consent issued on 07.11.2007.
Decision of CMC taken on 09.01.2008

No action.
Action taken report

No action. Applied for renewal of consent on 3-1-2008.
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 17.12.2007) except BOD (33 mg/l), other parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 24.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be Member (Drainage) for seeking affidavit for the reasons of low intake quantity of sewage & under utilization of STP capacity (only 10 MGD). 
Action Taken Report

Letter issued on 26.03.2008. 

Unit has submitted its reply along with an affidavit on 11.04.08 & informed that the supply of clear water in the area is less due to non commissioning of Bawana Water Treatment Plant. Moreover, there is less habitat in the area further decreasing sewage in the catchment area. Nearby villages sewer is also un-trapped due to non availability of sewage systems. However, all the sewage coming to STP is full treated without by-passing any sewage. It is not proposed to lay sewer system in nearby villages. Also laying of sewerage system in nearby colonies is in progress. All about efforts may increase intake flow  to the STP  and will improve utilization capacity of STP.

Contd..2..

..2..

Narela STP (10 MGD)

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 25.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

OKHLA STP , [Phase- I, II, III & IV, (12+30+37+45), Total 124 MGD) ]

Consent Status 

Consent to operate was granted by CPCB on 23.01.1987 (valid upto 31.12.88), 

Applied on 03.04.1998 issued by DPCC on 14.06.99 (valid upto 31.05.2000), 

Applied on 10.05.2000 issued by DPCC on 18.04.2001 (valid upto 17.04.2002).

Applied on 08.10.2002 issued by DPCC on 20.01.2004 (valid upto 17.04.2005).

Applied for renewal on 10.03.2005 for Phase I, II, III & IV Plant (124 MGD) and yet to be decided. 

Applied for renewal on 10.03.2008 for phase-I (12 MGD) plant (ID No. 25118).

Applied for renewal on 10.03.2008 for phase-II (30 MGD) plant (ID No. 25120).
Applied for renewal on 10.03.2008 for phase-III (37 MGD) plant (ID No. 25117).
Applied for renewal on 10.03.2008 for phase-IV (45 MGD) plant (ID No. 25119).
Decision taken  

Issue SCN giving last opportunity to remove the deficiencies observed during inspection
Action taken report

SCN issued on 15.2.2007. Reply received on 26-03-07. The following submissions have been made:-

· Magnetic flow meter is not feasible. Ultrasonic flow meter also did not work due to deposition of sludge /plastic floating material on probes of the meter.

· Wrt renovation of sludge drying beds, necessary action is being taken by construction division.

· The issue, of trapping of effluents flowing in the two drains passing through the plant, has not been addressed in the reply.

· The supply of effluents for irrigation after primary treatment suspended. The matter is under examination.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Unit has applied for renewal of consent but has not corrected all the deficiencies pointed out vide SCN issued on 15.2.07. Unit may be reminded to correct all deficiencies and only then consent will be granted.
Action taken report

Letter issued on 07.11.2007. No reply received.
Decision of CMC taken on 09.01.2008

SEE to inspect and put up in next CMC (MSW) meeting.
Action taken report
Inspected on 19-2-2008. 

No flow meters were installed with any of the four STPs. Aerators found operational. 

Bio-gas generated in STPs supplied to south Delhi area i.e. Lajpat Nagat, New friends colony, sukhdev Vihar etc. 

Effluents from different pump houses which is to STPs, no open drain carrying raw effluents seen in the premises. 

As enquired storm water drain(Harkesh Nagar Drain) is passing through STP, the said drain being storm water drain is not connected with STP. The drain leading to Madanpur Khadar is closed, being area is acquired by DDA. 

No bypass observed.  All the four STPs are connected to a common channels within the premises before discharge. 

As Informed about 10-15 MGD treated effluents is used for horticultures by CPWD. About 5MGD treated effluent to the also used by Jaitpur village for agriculture purposes. 
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 18.12.2007) all  parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 22.01.2007), all parameters are within the prescribed standard.
Contd..2..

..2..

OKHLA STP , [Phase- I, II, III & IV, (12+30+37+45), Total 124 MGD) ]

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter for installation of flow meter and TOC analyzer.

Sh. Aditya Narayan Singh will study the file & decision will be taken accordingly.  

Action Taken Report

 Letter issued on 03.04.2008. As decided on file, note of Sh. A. N. Singh is to be putup in next CMC. 
Now DJB has submitted separate application (4 applications) for renewal of consent for each phase of STP. 

Applied for renewal on 10.03.2008 for phase-I (12 MGD) plant (ID No. 25118).

Applied for renewal on 10.03.2008 for phase-II (30 MGD) plant (ID No. 25120).
Applied for renewal on 10.03.2008 for phase-III (37 MGD) plant (ID No. 25117).
Applied for renewal on 10.03.2008 for phase-IV (45 MGD) plant (ID No. 25119).
As per DPCC Analysis report, dated 18.03.2008 (sampling done on 03.03.2008), all parameters are within the prescribed standard. for Phase I, II, II & IV STPs.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 20.03.2008), all parameters are within the prescribed standard for Phase I, II, II & IV STPs.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Consent is renewed for all the four applications. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
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   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Okhla STP, (16 MGD)

Consent Status 

Consent issued on 21.09.05 & valid up to 02-12-07. Applied for renewal of consent on 17.012.07.
Decision taken  

_
Action taken report

Plant was inspected on 06.12.06. SCN dated 02.1.2007 was issued as number of deficiencies were observed. Plant  submitted reply with the following submissions:-

· Magnetic flow meter is not feasible in such type of STP’s. Ultrasonic flow meter also did not work due to deposition of sludge /plastic floating material on probes of the meter.

· Fourteen to sixteen aerators at a time are sufficient for generating effluent of desired quantity .However, all digesters and aerators have been made operational.

·  Presently, part of treated effluent is being used for horticulture purpose from this unit. 

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.
Decision of CMC taken on 19.10.2007

Unit has applied for renewal of consent but has not correct all the deficiencies pointed out vide SCN issued on 02.01.2007 

Unit may be reminded to correct all deficiencies and only then consent will be granted.

Action taken report

Letter issued on 06.11.2007. No reply received.
Decision of CMC taken on 09.01.2008

SEE to inspect and put up in next CMC (MSW) meeting.
Action taken report

Inspected on 19-2-2008. 

Ultrasonic flow meters installed at inlet and outlet of STP found of functional. 

Aerators found operational and sludge digesters are in use.

TOC analyzer installed at outlet of STP however found non-operational condition as informed TOC analyzer is not in use for last few moths due to non-availability of its chemicals and non-maintenance by supplier of TOC analyzer. 

Bio-gas generated in STPs supplied to south Delhi area i.e. Lajpat Nagat, New friends colony, sukhdev Vihar etc. 

This STP is connected with other four STPs to a common channels within the premises before discharge. 

As Informed about 10-15 MGD treated effluents is used for horticultures by CPWD. About 5MGD treated effluent to the also used by Jaitpur village for agriculture purposes. 

Applied for renewal of consent on 17.12.07
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 18.12.2007) all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 22.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter for non functioning of TOC analyzer.
Sh. Aditya Narayan Singh will study the file & decision will be taken accordingly.  

Action Taken Report

 Letter issued on 01.04.2008. Submitted reply on 21.04.08 in response to our letter dated 01.04.08, informing that TOC Analyzer is in working order and copies of reports are enclosed.  

Contd..2..

..2..

Okhla STP, (16 MGD)

As decided on file, note of Sh. A. N. Singh is to be putup in next CMC. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 03.03.2008), all parameters are within the prescribed standard for Phase V STPs.

As per DPCC Analysis report, dated 09.04.2008 (sampling done on 20.03.2008), all parameters are within the prescribed standard for Phase V STPs.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Consent is renewed. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

STP at C-DOT Campus, Chattarpur, Mehrauli, New Delhi-30. ((125 KLD)

Consent Status 

Consent to operate expired on 12.4.2007.

 Applied for renewal of consent on 11.03.2008 vide ID No. 25144. 

Decision taken  

-
Action taken report

A letter was issued on 26.06.2007, to  submit the consent application, but no reply/consent application received.

Decision of CMC taken on 19.10.2007

Unit may be asked to apply for renewal of consent. 

SEE to inspect. 

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Inspected on 04.01.2007. Sewage of office complex is being treated in STP. Most of the treated effluent is being used for horticulture purposes in complex. Flow meter at inlet not installed. Chlorination not done as feeding pump is out of order. Requested for one month time for submission of desired details.(i.e. consent application)
Decision of CMC taken on 09.01.2008

A letter for deficiencies be sent to unit and put up in next CMC (MSW) meeting.
Action taken report

Letter issued on 12.02.08. Reply received on 28.02.08.

Analysis report not received from DPCC laboratory so far.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue letter to apply for renewal of consent & to submit affidavit w.r.t. correction of deficiencies with in one month.

SSO(Water) to ensure that she will do the monthly monitoring of all CETPs & STPs and submit the test report before the CMC(MSW) meeting.

Action Taken Report

 Letter issued on 26.03.2008. Unit has submitted reply on 24.04.208. Applied for renewal of consent on 11.03.2008 vide ID No. 25144. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.2008), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 09.04.2008 (sampling done on 28.03.2008), all parameters are within the prescribed standard.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

Consent is renewed. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Holambi Kalan STP, (2 MLD)
Consent Status 

Consent issued on 14.05.04 & valid upto 08.10.06.Not applied for renewal of consent.
Decision taken  

Copy o f the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-07 to instruct the officials concerned to apply for the renewal of consent.
Action taken report

Copies of the letters/SCN issued on 01-11-2006 & 29-11-2006 handed over during CMC meeting held on 21-02-07. Consent issued on 14.05.04 & valid upto 08.10.06.

Decision of CMC taken on 19.10.2007

Unit may be asked to apply for renewal of consent. 

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Letter issued on 07.11.2007. No reply received . 

Not applied for renewal of consent.
Decision of CMC taken on 09.01.2008

Issue reminder letter.
Action taken report

Letter issued on 12.02.08. No reply received.

Analysis report not received from DPCC laboratory so far.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue final reminder letter to concerned EE with the copy to Addl. Commissioner (MCD) to applying for renewal of consent. 

SSO(Water) to ensure that she will do the monthly monitoring of all CETPs & STPs and submit the test report before the CMC(MSW) meeting.

Action Taken Report

 Letter issued on 25.03.2008. Ex. Engineer (S) DDI, MCD has submitted reply on 04.04.08, informing that the STPs at Tikri Khurd and Holambi are non-operational due to some administrative reasons and he is  making all his efforts to make it operational and to hand over these STPs to DJB. Further, requested for three months time for this process.

As per DPCC Analysis report dated 18.03.2008, STP was non operational.
As per DPCC Analysis report, dated 09.04.2008 STP was non operational.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

To take up with DJB in July, 2008 and ask the unit to apply for renewal of consent. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Bakkarwala STP, (3 MLD)
Consent Status 

Consent issued on 12.02.08 and valid up to 20.05.2010.
Decision taken  

Copy of the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-07 to instruct the officials concerned to apply for the renewal of consent.

Action taken report

Copies of the letters/SCN issued on 01-11-06, 29-11-06 handed over during CMC meeting held on 21-02-07.  Previous Consent valid upto 12.06.06. 

Plant has submitted consent application for renewal of consent on 21-05-07 with self analysis report.

Decision of CMC taken on 19.10.2007

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Inspected on 04.01.2008.
Decision of CMC taken on 09.01.2008

Consent granted.
Action taken report

Consent issued on 12.02.08.

Analysis report not received from DPCC laboratory so far.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

SSO(Water) to ensure that she will do the monthly monitoring of all CETPs & STPs and submit the test report before the CMC(MSW) meeting.

Action Taken Report

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 28.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 31.03.2008), all parameters are within the prescribed standard.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Molar Band STP (3 MLD)
Consent Status 

Consent issued on 12.02.08 and valid up to 20.05.2010.
Decision taken  

Copy of the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-2007 to instruct the officials concerned to apply for the renewal of consent.
Action taken report

Copies of the letters / SCN issued on 01-11-2006 & 29-11-06 handed over during CMC meeting held on 21-02-2007.  Previous Consent valid upto 12.06.06. 

Plant has submitted consent application for renewal of consent on 21-05-2007 with self analysis report.

Decision of CMC taken on 19.10.2007

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Inspected on 04.01.2008.
Decision of CMC taken on 09.01.2008

Consent granted.
Action taken report

Consent issued on 12.02.08.

Analysis report not received from DPCC laboratory so far.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

SSO(Water) to ensure that she will do the monthly monitoring of all CETPs & STPs and submit the test report before the CMC(MSW) meeting.

Action Taken Report

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 19.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 28.03.2008), all parameters are within the prescribed standard.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

 Tikri Khurd STP (2 MLD)
Consent Status 

Consent expired on 12.06.06. Not applied for renewal.

Decision taken  

Copy o f the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-07 to instruct the officials concerned to apply for the renewal of consent.

Action taken report

Copies of the letters/SCN issued on 01-11-2006 & 29-11-06 handed over during CMC meeting held on 21-02-07. Previous Consent valid upto 12.06.06. Letter issued on 29.11.06 for seeking consent application for renewal. No application for renewal of consent received.

Decision of CMC taken on 19.10.2007

Unit may be ask for apply to renewal of consent. 

SEE to inspect. MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Visited on 03.01.2008. Premises of STP found locked. As per information gathered from nearby residents, STP is non operational & locked from last 8-10 months.
Decision of CMC taken on 09.01.2008

MS may write to Dy. Commissioner, MCD Narela Zone asking for reasons of closing and details about when STP will restart. Copy to Slum & JJ Deptt, MCD
Action taken report

Letter issued on 12.02.08. No reply received.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to Sh. Naresh Kumar, Addl. Commissioner (MCD) through Chairman, DPCC giving details of previous letters.

Action taken report

Letter issued on 25.03.2008. Ex. Engineer (S) DDI, MCD has submitted reply on 04.04.08, informing that the STPs at Tikri Khurd and Holambi are non-operational due to some administrative reasons and he is  making all his efforts to make it operational and to hand over these STPs to DJB. Further, requested for three months time for this process.

As per DPCC Analysis report dated 18.03.2008, STP was non operational.
As per DPCC Analysis report, dated 09.04.2008 STP was non operational.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

To take up with DJB in July, 2008 and ask the unit to apply for renewal of consent. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Ghitorni STP,  (5 MGD)
Consent Status 

Not applied for consent.

Decision taken  

CE, DJB was asked to apply for consent, who agreed to do the needful.
Action taken report

No application for consent received.

As per DJB, plant will be commissioned by Dec. 2007. 

Decision of CMC taken on 19.10.2007

Unit may be ask for apply to renewal of consent. 

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs..
Action taken report

Visited on 08.01.2008. Premises of STP found completely dry & non operational. As per information gathered from nearby residents & security person of STP, it  is non operational from last many years. A letter recd from DJB informing that Gitorni STP is yet to be commissioned by DJB after the raw sewage is made available by DDA at the plant. Consent will be submitted to DPCC after operation of plant.

Decision of CMC taken on 09.01.2008

MS to write Member (drainage), DJB to give reason for not operating the STP for a long time even the sewage is generated from the surrounding area.
Action taken report

Letter issued on 12.02.08. No reply received.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue reminder letter to Member (Drainage) by Member Secretary, DPCC.  
Action Taken Report

 Letter issued on 26.03.2008. A letter received oj 26.03.08 from S.E., DJB informing that this STP is not working due to non availability of raw sewage for which the network is to be laid by DDA and requested that matter may be taken up with DDA for laying of network, so that this STP is made functional.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

The STP is not getting adequate water as per the installed capacity. As per the inspection report it was found that there is lack of coordination between DJB and DDA for getting adequate water at STP. Issue letter to both DJB and DDA that they make best possible efforts to ensure that the capacity of the STP plant is better utilized in pubic interest. 
Call the Ex. Engineer of South Zone from DJB & DDA in next CMC (MSW) meeting. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

STP at National Bureau of Plant Genetic Resources ICAR, Pusa Campus, (80 KLD)
Consent Status 

Consent expired on 07.06.07. Not applied for renewal of consent.

Decision taken  

-
Action taken report

Consent to operate expired on 07.06.2007, and not applied for renewal of consent.

A letter was issued on 26.06.2007 to submit the consent application, but no reply/consent application received.

Decision of CMC taken on 19.10.2007

Unit may be ask for apply to renewal of consent.

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Inspected on 03.01.2008. During inspection it was found that sewage of institute received at STP is directly goes to the final sump though screen. Sewage was not passed through other units of STP. From the final sump, sewage is pumped out in the near by outlet drain for discharge. No dry/wet sludge observed at site.

Neither applied for renewal of consent nor submitted reply of letter.

Decision of CMC taken on 09.01.2008

MS to write Director General,  PUSA regarding non operation of STP and that the effluent be discharge only after proper treatment.
Action taken report

Letter issued on 12.02.08. Reply awaited.

Analysis report not received from DPCC laboratory so far.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to Joint Secretary, ICAR with copy to Director General, PUSA through Chairman, DPCC.

SSO(Water) to ensure that she will do the monthly monitoring of all CETPs & STPs and submit the test report before the CMC(MSW) meeting.

Action taken report

Letter issued on 04.04.2008. As desired by Chairman, matter was discussed with Dir. General of PUSA by Member Secretary, DPCC and asked to apply for renewal of CTO and Compliance report before 12.5.08 .  He told that STP is looked after by CPWD but he will instruct them  for compliance.    
As per DPCC Analysis report dated 18.03.2008, STP was non operational.
As per DPCC Analysis report, dated 09.04.2008 STP was non operational.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Ask the unit to give reasons for non operation of STP by 30.06.2008 positively. 
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

STP at BSNL, CTO Project, Mathura Lane, Janpath, New Delhi.
Consent Status 

Not applied for consent.

Decision taken  

-
Action taken report

Plant has submitted a letter dt 30-05-2007 & requested to provide acceptable standard.

A letter was issued on 03.07.2007 to submit application for consent to establish/operate. But no reply received in this regard
Decision of CMC taken on 19.10.2007

Unit may be ask for apply to renewal of consent.

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

STP found non operational condition. Filter press found dry. No dry or wet sludge found. STP is installed only for office complex. As reported, office has no canteen & STP is yet to be commissioned. However all pipe fittings etc found installed. No flow meter installed at inlet/ outlet of STP. Sewage collected in STP is being pumped outside without any treatment.

A reply has been received on 07.01.08 informing that the process for submitting the consent application of STP is in process & it is likely to be submitted within one month time.

Decision of CMC taken on 09.01.2008

MS to write a letter MD, BSNL for rectification of deficiencies and to ensure the operation of STP.
Action taken report

Letter issued on 12.02.08. No reply received.

Analysis report not received from DPCC laboratory so far.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

MS to speak with MD, BSNL & sort out the matter. 

Action Taken Report

MS has talked to Sh. Goel, MD, BSNL on 02.04.2008 and . 

Unit has submitted reply, however, Consent application not received so far.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

EE, MSWM to inspect and report by 30.06.2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Wazirabad Water Treatment Plant, Wazirabad

Consent status:

Not applied for consent under Air & Water Acts. 

Decision of Committee taken on 19.10.2007

Committee has also decided that other two units i.e Wazirabad Water Works & Chandrawal Water Works be also asked to apply for consent to operate under Air & Water Acts.

Action Taken Report

Letter for seeking consent to operate under Air & water Acts issued on 07.11.2007. No reply received so far.

DPCC analysis report
As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water.
Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Reminder letter may be issued.

Action taken report

Letter issued on 12.02.2008. No reply received.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue final reminder letter. 

Action Taken Report

Final reminder letter issued on 27.03.2008. Reply received on 11-4-2008 wherein it is mentioned that the matter is under process for submitting the application under Air& Water Act.

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:

Ask the unit to apply for consent to Establish under Air & Water Act. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
     Member (Env. Deptt.)
MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Chandrawal  Water Treatment Plant, Chandrawal

Consent status:

Not applied for consent under Air & Water Acts. 

Decision of Committee taken on 19.10.2007

Committee has also decided that other two units i.e Wazirabad Water Works & Chandrawal Water Works be also asked to apply for consent to operate under Air & Water Acts.

Action Taken Report

Letter for seeking consent to operate under Air & water Acts issued on 07.11.2007. No reply received so far.

DPCC analysis report
As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Reminder letter may be issued.

Action taken report

Letter issued on 12.02.2008. No reply received.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue final reminder letter. 

Action Taken Report

Letter issued on 27.03.2008. Reply not received.

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:

Ask the unit to apply for consent to Establish under Air & Water Act. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Haiderpur  Water Treatment Plant, Haiderpur

Consent status:

Applied for consent to operate on 13.02.2008.

Decision of Committee taken on 19.10.2007

Unit may be ask for apply for consent to operate.  MS to direct lab officials of DPCC to do regular monthly lab testing for drinking water standards.
Action Taken Report

Letter for seeking consent to operate under Air & water Acts issued on 07.11.2007. No reply received so far.

DPCC analysis report
As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Reminder letter may be issued.

Action taken report

Letter issued on 12.02.2008. Applied for consent to operate on 13.02.2008.
As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Member Secretary, DPCC to inspect & report in April CMC(MSW). 

Action taken report

Plant was inspected on 08-05-2008 by Member Secretary.

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:

Ask the unit to apply for consent to Establish under Air & Water Act for both its old & new units. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Nangloi Water Treatment Plant, Nangloi

Consent status:

Not applied for consent under Air & Water Acts. 

Decision of Committee taken on 19.10.2007

Unit may be ask for apply for consent to operate.  MS to direct lab officials of DPCC to do regular monthly lab testing for drinking water standards.
Action Taken Report

Letter for seeking consent to operate under Air & water Acts issued on 07.11.2007. No reply received so far.

DPCC analysis report
As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Reminder letter may be issued.

Action taken report

Letter issued on 12.02.2008. No reply received.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue  reminder letter for reply. 

Action Taken Report

Letter issued on 27.03.2008. Received application for consent to operate through Post on 29-4-2008 which is not complete(less consent fee, trade effluent generated but no treatment method mentioned), Demand Draft is yet to be detatched.

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:

Ask the unit to apply for consent to Establish under Air & Water Act at Enquiry Counter of DPCC and application for Consent to operate to be returned back to the unit in original with fee draft. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Sonia Vihar Water Treatment Plant, Sonia Vihar

Consent status:

Consent to operate granted on 13.03.2007. 

Decision of Committee taken on 19.10.2007

Ask the unit to compliance report of consent condition. MS to direct lab officials of DPCC to do regular monthly lab testing for drinking water standards.  

Committee has also decided that  other two units i.e Wazirabad Water Works & Chandrawal Water Works be also asked to apply for consent to operate under Air & Water Acts.

Action Taken Report

Letter for seeking compliance report of consent to operate under Air & water Acts issued on 06.11.2007. 

Reply received on 02.01.2008.

DPCC analysis report
As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water except Hardness ( as CaCo3-360mg/l ).

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

No action.

Action taken report

No action. 

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

No action. 

Action Taken Report

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Bhagirathi Water Treatment Plant, Near Waziradad, Delhi   

Consent status:

Not applied for consent under Air & Water Acts. 

DPCC analysis report
As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water).

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Issue letter for asking to apply for consent under Air & water Acts.

Action taken report

Letter issued on 13.02.2008. No reply received. 

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue  reminder letter. 

Action Taken Report

Reminder letter issued on 27.03.2008 to apply for consent to operate. Submitted reply on 22.04.2008, that this office shall formally apply for consent shortly and also raise the query that the fee for Air Act is required to be paid or not. 

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:

Ask the unit to apply for consent to Establish under Air & Water Act at Enquiry Counter of DPCC and clarify his point for fee. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Remarks:
A letter has been received from Central Pollution Control Board (Copy enclosed) regarding installation of Continuous online TOC analyzer for bulk monitoring of CETP /STP. 

Letters have also been sent to the Member Secretaries of Andhra  and Tamil Nadu  Pollution Control Pollution Board wherein they were requested to mention the cost of the TOC analyzer being installed at STPs and to clarify the standards prescribed for TOC of STP treated waste water. However no reply has been received from the concerned officials.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Member Secretary, DPCC may write to Member Secretary, CPCB for the financial assistance of TOC analyzer which shall be installed at the CETP/STP as the TOC analyzer will be installed first time in the case of CETP. 

Action Taken Report

Letter issued on 20.02.2008. 

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to Chairman, CPCB through Chairman, DPCC.

Action Taken Report

 Letter issued on 15.04.2008. In response of letter dated 20.02.08, Additional Director, CPCB vide his letter dated 02.04.08, has informed that there is no provision in CPCB funds for providing such a support.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

A letter may be made by MS to Member (Drainage) to TOC analyzer costing about Rs. 14 Lakh.

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
     Member (Env. Deptt.)
MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Representation received from M/s Sanjay Enterprises regarding re-generation and reuse of activated carbon in CETPs.

M/s Sanjay Enterprises has submitted the representation on behalf of M/s Industrial Carbon (P) Ltd. regarding technology available for re-generation and reuse of activated carbon for the CETPs installed in Delhi. The brief of the proposal is as under:

1. Normal life of activated carbon in ACF of CETP is approximate 21 days. The re-generation facility is not established in Delhi so far.

2. All over the world, activated carbon is re-generated and reuse and fresh carbon is used only for topping up.

3. Why need of re-generation:

Cost of fresh activated carbon is very high i.e.

60 MT (in 1 CETP) x Rs. 55000 (Per MT) + Taxes = approx 40 Lacs for every 21 days for each CETP

660 MT carbon is not made in India in every 21 days and we have to import and spend our foreign currency

Space is required for storing all the exausted carbon in dry cool place for 20 years or spend money for its incineration.

4. A facility of re-generation should be established as joint venture with Delhi state or we shall set up the total unit but land is to be provided by you in any of the CETPs or any other suitable place, land and building with electrification and water connection shall be your scope

5. Only after such facility is established successful use of ACF becomes economical a perfectly treated water which meets pollution control norms is as pure as ground water and can be used for all practical purposes except human drinking application 

6. By selling treated water and income of approximate 3 crore can be generated from which only 10% may go for cost and saving of Rs. 2.7 crore/ day is  visualized. 

7. They have already submitted their proposal for re-generation plant to Chief Engineer DSIIDC, Commissioner (Plg.), DDA etc.  

Sh. J. M. Chaturvedi & Sh. Rohit Kumar Madhavji visited this office on 16.04.08 and explain the proposal before the SEEs and other officials.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

Ask the unit to go to concerned CETP for marketing. 
Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
     Member (Env. Deptt.)
MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

The cases pending before Hon’ble Supreme Court commonly known as Maily Yamuna,  

This file contains some copies of the orders passed by HSC as well as affidavits filled by some govt. authorities. Chairman, DPCC vide note dated 11.04.08 directed to put up the matter in CMC (MSW) this month.

Hon’ble Supreme Court on the basis of one newspaper clipping published in HT times on 18.07.94 Ceased of the matter wrt water quality of river Yamuna. 

Hon’ble Supreme Court time and again directed to all the govt. authorities to make the water quality of at least ‘C’ level. i.e. useful for bathing. 

During pursuance of the various orders, the order dated 13.09.99 and 27.08.99 the Hon’ble court has ordered that “with effect from 1st Nov. 1999, no industrial effluent would be allowed to discharge directly or indirectly into the river Yamuna” may be referred and needs to be examine. 

As per the note of ALO dated 09.04.08 as such there is no directions for implementation is pending on part of DPCC, however Hon’ble court was not satisfied with implementation of various orders despite promises and assurances given to the court for improving the quality of water of river Yamuna.

Subsequent, to the filing of the affidavit by the Principal Secretary (UD) in pursuance of order dated 12.04.05 Hon’ble court has directed to set up the STP at the mouth of he drains meeting the river Yamuna so as to clean it like river Thames. 

The next date of hearing is 08.07.08. 

Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
     Member (Env. Deptt.)
MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Inviting proposal for establishment of Common Effluent Treatment Plants
A letter dated 15.04.2008 has been received from the Joint Secretary, Ministry of Env. & Forest, Govt. of India inviting proposal for establishment of Common Effluent Treatment Plants along with necessary documents after coordinating with State Environment Department, so that proposal  may be considered for senction of Central subsidy during the financial year 2008-09, for which funds have been provided. 

A letter dated 16.08.2007 on the same matter has also been received from MoEF (copy enclosed). As decided, reply was sent to the Jt. Secretary, MoEF on 11.10.07  (copy enclosed) informing that out of 15 proposed CETPs, at present 10 CETPs are in operation in different industrial areas of Delhi. DSIIDC was the agency for construction of all the 10 CETPS installed so far. Industries Department, Govt of Delhi is the nodel agency for the implementation of CETP Act. Hence DSIIDC may be asked to submit the proposal of setting up of CETP as per the scheme of the MoEF, Govt. of India. 

Decision of Consent Management Committee in its meeting dated 12.05.2008:

There are 10 industrial areas which are still do not have CETP. The letter can also be forwarded to the DSIDC for writing to MOEF. Accordingly draft to JS, MOEF may be put up. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
     Member (Env. Deptt.)
MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

6th quarterly review meeting convened by the Chief Secretary, Delhi in compliance of the order of the hon’ble Supreme Court in case No. CWP/725/1994Captioned “AND QUIET FLOWS THE MAILY YAMUNA Vs. CPCB & ORS was held on 10.03.2008. The discussion held with various stakeholders is as under:-
(A) Delhi Jal Board

Action Taken/ Target:-

· In so far as rehabilitation of trunk sewers is concerned, presently the main trunk sewers carrying sewage to the Sewage Treatment Plants are choked due to siltation and settlement at some locations. Due to this, the entire sewage is not reaching the Sewage Treatment Plants. Due to mal functioning of these trunk sewers, there is back flow of sewage in the area. To give relief to the residents, dewatering pumps (trolleys) have been installed temporarily at required locations which pump out the sewage into the drains. Hence, some quantity of sewage is flowing into the drains which should have been flowing into the sewerage network Hence, no sewage will be flowing into the drains after rehabilitation of these sewers. This exercise will be done by Consultant within 6-9 months. Hence for design purpose the scenario of 2009 when the entire reach of trunk sewers will be desilted and set right, will be considered while designing the size of the sewer i.e. part of para 38 (a), (b) & (c) of the Expert Committee report. This analysis does not have to wait till the completion of the actual rehabilitation work of trunk sewers. 
· The interceptor sewer concept comprises the following components:-

a. Laying of interceptor sewers along three major drains of Irrigation & Food Control Department (i.e. Najafgarh, Supplementary and Shahdara).

b. Augmentation of the existing capacity of Sewage Treatment Plants at the mouth of Delhi Gate drain and Dr. Sen Nursing Home Drain.

c. Intercepting 13 small drains into Bela Road and Ring Road Trunk sewer after rehabilitation. 

d. Construction of additional Sewerage Treatment Plants after utilization of full capacity of existing plants.

Out of above 4 components, EIL has been entrusted the first component only whereas remaining 3 components shall be done by DJB and completed by 2009.

· EIL will prepare the schemes in various phases. There are 3 major drains; Najafgarh, Supplementary and Shahdara which carry part of untreated sewage and discharges into river Yamuna. Supplementary and Najafgarh drain meet with river Yamuna just on the down stream of Wazirabad barrage and thus, river Yamuna carries water mixed with sewage through entire reach of Delhi of 22 Kms. The Shahdara drain meets river Yamuna down stream of Delhi.

· It is proposed to target these 2 drains in phase-I so that entire reach within Delhi is improved in terms of quality of river water before the Commonwealth Games. Delhi Jal Boards’s works in respect of component No. 2, 3 & 4 above are also to be completed before 2010. Thus the maximum improvement in river quality will be achieved by 2010. However, the work of Shahdara drain will be concurrently done and efforts will be made to complete the work of Shahdara drain latest by 2012. M/s EIL has assured of necessary feedback by 15th June, 2008 so that revised affidavit could be filed in the Hon’ble Supreme Court. M/s EIL has submitted the timeline which are enclosed with the minutes of the meeting dated 10.03.2008.

Contd..2..

..2..

1. Work related to Abatement of Pollution in River Yamuna:
(a) Laying of Interceptor sewers comprising following components :

The Project Management Consultancy work has been awarded to M/s Engineers India Ltd., The work is scheduled to be completed by December 2012 which includes planning work to be completed within 12 months. The work has been divided into two phases :-

Phase-I :  Laying Interceptor sewer along Najafgarh & Supplementary drain, shall be completed by 2010.

Phase-II :  Laying of Interceptor sewer along Shahdra drain, shall be completed by 2012.

The tenders on Design Build, Operate basis shall be invited after getting assessment of quantum of flow into Delhi Gate & Dr. Sen Nursing Home drains and quality parameters of the sewage flowing into the drains. The work shall be completed by Dec. 2009

Balance 13 drains shall be intercepted into Bela Road and Ring Road Trunk sewers which are being rehabilitated and completed by December 2009. The sewage shall be conveyed to Okhla Sewage Treatment Plant.


The capacity of the existing plants shall be augmented after their full utilization.
(b) Refurbishment of Sewage Treatment Plants, Pumping Stations and Trunk sewers.

Delhi Jal Board has already awarded the works of Rehabilitation of 50 kms Trunk Sewers which will be completed by December 2009. Simultaneously, existing identified Sewage Pumping Stations and Sewage Treatment Plants are also being rehabilitated.

(c) Augmentation of Capacity of existing Sewage Treatment Plants to meet the demand of the growing population.

Capacity of Kondli, Yamuna Vihar & Okhla Sewage Treatment Plants is being augmented by 45, 25 & 30 MGD respectively by December 2009.

(d) Sewering of unsewered area:
i. All the 44 resettlement colonies have been sewered. 

ii. Out of 567 U/A-regularized colonies, sewers laid in 523 colonies. In the remaining colonies, work is in progress in a phased manner.

iii. Out of 135 urban villages, sewers laid in 107 villages. Work in progress in the remaining urban villages in phased manner. 
iv. Administrative approval for laying sewerage system in 27 villages has already been accorded. Allotment of land for construction of STP/WSP/SPS is being processed by Revenue & Land & Building department. Lands at 15 locations of Gram Sabha have been finalized. The work has been awarded for laying sewerage system in sixteen villages and in future villages tenders are under process of award for work.. 
Contd..3..
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Irrigation & Floor Control Department :
Action taken/ Target

1. The work of construction of around 34 Kms boundary wall on both sides of Najafgarh drain within the habitation area is in its full swing. The boundary wall on upstream side of Kakrola is not being constructed as there is hardly habitation area. The work shall be completed by August 2008.

Similarly, 30 Kms stretch of boundary wall along Supplementary drain shall be completed by August 2009.

Boundary wall along Shahdra drain is already constructed. 

2. The joint inspection of MCD & Irrigation & Floor Control was carried out at all outfall structures ….

It was decided that all the outfall structures shall be revamped / maintain by Irrigation & Flood Control department as a deposit work on behalf of MCD.

3. The list of 85 bridges and action plan for providing M.S. nets shall be provided by them.

4. The work of Forestation along major drains shall be got done with the help of Ministry of Environment & Forest, Govt. of NCT of Delhi. 

5. It was further emphasized upon to do regular desilting and channelizing the drains to maintain the flow. The cunnette must also be provided in all the drains to take care the dry weather flow. The plantation / a forestation on the banks of major drains must be encouraged to prevent the scouring during rains. 
 MCD

1. Joint Inspection of MCD drains and their out fall structures. 

The joint inspection had already carried out with Irrigation & Flood Control Department and report submitted with Urban Development department. MCD requested to get revamped and channelize all the out fall structures by the department of Irrigation & Flood Control department.

2. Construction of Boundary walls along 16 drains under their jurisdiction. 
MCD has identified the vulnerable locations for construction of boundary wall within habitation area where chances of garbage dumping is more. However, after constructing boundary wall, the difficulty in desilting of drains will arise.

3. Plantation along drains 

It was emphasized to take similar action by MCD as that of Irrigation & Flood Control department.

4. Legal Action against defaulters
Challans have been done against the defaulters who were caught littering or dumping garbage into drains.

5. Awareness Program
MCD intimated that they are launching awareness program to educate the people not to through garbage into drains and Yamuna River.
The Chief Secretary directed to submit the photographs of such points where MCD is doing the work in respect of cleaning River Yamuna. 

Contd..4..

..4..

Slum & J.J. Department of MCD
Action taken/ Target

1. It was intimated that Slum and J.J. department is implementing plan scheme of Relocation of J.J. Clusters on the request of various departments like DDA, PWD, GAIL etc.

2. They intimated that no fresh formal request has been received from any of the department to remove jhuggis from the bank of drains.

3. They are requesting Govt. to  allot more land for shifting of Jhuggis.

DDA
Action taken/ Target

The representative of DDA informed that they have already removed the clusters from the bank of River Yamuna except for Batla house, Bodh Vihar and Majnu Ka Tilla where the matter is pending in the Court. However, the Chief Secretary directed to submit the latest status in this respect.

 DSIIDC

Action taken/ Target

· 10 CETPs constructed and 9 handed over to respective societies for operation.

· 1 CETP at Naraina Industrial Area is under construction and completed by July 2008.

· Balance four CETPs at Anand Parbat, Mohan Cooperative, Okhla Industrial Estate and Najafgarh Road are kept in abeyance as per the directions given in EPCA report submitted to the Hon’ble Supreme Court. The decision of the Hon’ble Supreme Court is still awaited.

· Treated water from these CETPs is meeting with the EPA standards and being discharge into drain. But Secretary (Env.) intimated that some Plants are not meeting the standard. 
Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 
Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
     Member (Env. Deptt.)
MSWM Cell

Table Agenda: 

General Decision on the study of CETPs in Delhi

Dr. A. K. Neema, IIT may kindly be requested to file his report on CETPs by 30.06.2008 positively. Dr. Neema may be asked to inspect those CETPs also which were stopped by EPCA orders so that latest update is received on each of these CETPs. For this additional work one month additional time is granted to file supplementary report. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
     Member (Env. Deptt.)
MSWM Cell

Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
Compost Plant of Municipal Corporation of Delhi at Okhla
Name of the agency: Municipal Corporation of Delhi, O/o the Engineer in Chief, Town Hall, Delhi-6

Particulars of the project: 

Revival of the Compost Plant of Municipal Corporation of Delhi at Okhla, Delhi (The compost plant at Okhla is existing plant of MCD which stopped operation in 1994 and MCD now has handed over this plant to IL & FS for revival of up gradation).   

Status of Consent: 

Consent to establish has been issued on 29.01.08. 

Status of authorization under MSW Rules: 

Applied for authorization for setting up and operation of waste processing facility on 20/11/07 (C/1 to 67).

Details of the project: 

· Processing technology is composting through open
air aerobic window composting method.

· Quantity of waste to be processed is 200 TPD.

· Investment on the project is Rs.6.2 crores.

· Quantity of waste to be disposed per day is 40 TPD.

· Plot Area is 29000 sq m and Built up area- 4000 sq m 

· Sanctioned Power Load – 280 KW

· Revival period the compost plant will be start on 1 March, 2008.

· Water consumption for domestic is 2000LPD &  for processing  is  20,000 LPD

· Quantity of domestic waste generated is 1500 LPD and leach ate to be recycled in composition process

· 100 KVA DG Set proposed to be installed.

· Concession Agreement between MCD and IL & FS is placed at (C/71 to 103).

Decision taken in meeting held on 09.01.08:

· Consent to Establish granted.

· As regard the authorization under MSW Rules, the letter will be sent to the other bodies as mentioned in MSW Rules for their views/NOC and for site clearance to the concerned land owning agency and the copy of these letters will be sent to the project proponent also.
Action taken/ Status after the meeting held on 09.01.08:

· Consent to establish has been issued on 29.01.08. 

· As decided letter was also issued on 29.01.08.  
· Decision taken in meeting held on 28.02.2008:

No action at present.

Status:
Comments have been received from Town & Country planning Organisation, UD, Govt. of India. They suggested 7 modifications in the project (C/126).

Decision of Consent Management Committee in its meeting dated 12.05.2008:
Comment received from Town & Country Planning Organization, UD, Govt of India be forwarded to IL&FS and a reminder should go to others. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM
Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
Compost Plant at Tikri Khurd/ Khampur 
Name of the agency: M/s Spiral Services, New Sabzi Mandi, Azad Pur, Delhi
Particulars of the project: 

Up-gradation of the A.P.M.C. Compost Plant at Tikri Khurd/ Khampur, G.T. Karnal Road, Delhi-40 (Existing plant inaugurated by Delhi C.M. on 17.01.02)
Status of Consent: 

· Consent to establish has been issued on 29.01.08. 

· Applied for consent to operate on 04.03.08.

Status of authorization under MSW Rules: 

Applied for authorization for setting up and operation of waste processing facility on 20/11/07 (C/1-27 and C/30-34).

Details of the project: 

· Processing technology is composting through open air aerobic window composting method.

· Quantity of waste to be processed is 200 TPD.

· Investment on the project is Rs.1.6 crores.

· Quantity of waste to be disposed per day is 30 TPD.

· Plot Area is 24000 sq m.

· Built up area- 1000 sq m

· Sanctioned Power Load – 5 KV

· Proposed to be commissioned from March, 2008 (earlier unit exist since 17.01.02).
· Water consumption for domestic is 1440 LPD &  for processing  is  5000 LPD

· Quantity of domestic waste generated is 1000 LPD & having 2 septic tanks and leach ate to be recycled in composition process.
· No DG Set proposed to be installed.

· Agreement between APMC and Spiral Services is placed at (C-/3 to 11).

Decision taken in meeting held on 09.01.08:

· IL&FS has sent the letter by Fax wherein it is mentioned that IL&FS is working with M/s. Spiral Services in managing the compost facility at Tikkri. In the same letter they have also mentioned that they would provide the following to the existing compost plant i.e. facilitate expansion of plant, purchase and supply of equipment, finance and facilitate accrual of CDM benefit, provide technical assistance in operation of plant and off take composite produced in the plant. In view of this, consent to Establish granted.

· As regard the authorization under MSW Rules, the letter will be sent to the other bodies as mentioned in MSW Rules for their views/NOC and for site clearance to the concerned land owning agency and the copy of these letters will be sent to the project proponent also.
Action taken/ Status after the meeting held on 09.01.08:

· Consent to establish has been issued on 29.01.08. 

· As decided letter was also issued on 29.01.08.  
· Decision taken in meeting held on 28.02.08:
No action at present.

Status:
· Applied for consent to operate under Orange category on 04.03.08. 
· Views/ Comments/ NOC were received only from Town and Country Planning Organization, Ministry of U.D. (C/44- 45) asked before issued of authorization under MSW, Rules. Views/ Comments/ NOC are still awaited from Air Force, DDA and Central Ground Water Board.
Contd…2
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Decision of Consent Management Committee in its meeting dated 12.05.2008:
Comment received from Town & Country Planning Organization, UD, Govt of India be forwarded to M/s Spiral Services / IL&FS and a reminder should go to other. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM
Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
Modern Poultry & Egg market at Ghazipur, New Delhi.

Name of the agency: M/s Delhi Agriculture Marketing Board, 9, Institutional Area, Pankha Road, Janakpuri, New Delhi-110058.
Particulars of the project: Modern Poultry & Egg market at Ghazipur, New Delhi.
Status of Consent: 

Applied for consent to establish under Air & Water Acts vided ID. No. 24811 dt. 24.01.08 (C/1-98)

Details of the project: 

· Product is dressing of Poultry birds- 48 lakhs birds/ month. 

· Raw material is Poultry birds- 576 lakhs/ annum. 

· Proposed Investment on the project is Rs.133.5 crores.

· Quantity of waste to be disposed per day is 30 TPD.

· Total Plot Area is 60200 sq m and Built up area- 48160 sq m

· Sanctioned Power Load /power required– 2925 KW
· Proposed to be commissioned from March, 2010.
· No of workers: 

a) During construction phase – 100 b) During operational phase-   25

· Water consumption:

Domestic - 91000 LPD, 
Industrial cooling/ boiler feeds - 92000 LPD processing   - 1120000 LPD,
Other (Gardening) – 108000 LPD
· Quantity of domestic waste generated is 80000 LPD and Industrial is 1100000 LPD

· Proposed Effluent Treatment Plant of 1200 KLD with tertiary treatment & UV Irradiation and reuse in flushing, HVAC, DG, Horticulture (C/52 of the file). A STP of 200KLD is also proposed (C/58 of the file). 
· DG Sets proposed to be installed – 2 X 1000 KVA + 2 X 625 KVA.
· Land allotted by DDA for this purpose (allotment letter at C/4-6)  
Remarks:

As per the provisions of EIA notification dated 14.09.06 the following construction projects are to be required Environmental Clearance from MoEF:

c) Building and Construction Projects having built up area ≥ 20000 sqm and < 150000 sqm of built up area. 

d) Townships and Area Development Projects having covering an area ≥ 50 ha and or built up area ≥150000 sqm.   
· Decision taken in meeting held on 28.02.08:
Letter to be sent for EIA clearance indicating that if they have any doubt they may contact the EIA cell of MOEF and the copy of this letter will be sent to EIA Cell of MOE&F.

Action taken/ Status after the meeting held on 28.02.08:

Letter issued for Environmental Clearance on 24.03.07. Environmental clearance/ reply are still awaited from the unit or MOEF.

Decision of Consent Management Committee in its meeting dated 12.05.2008:
Issue reminder letter for Environmental Clearance. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM
Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008
Municipal Waste Complex at Gazipur Bio-gas Plant Site

Name of the agency: M/s New Delhi Waste Processing Company Ltd.
Particulars of the project: 

· Setting up of integrated Municipal Waste Complex at Gazipur Bio-gas Plant Site, Gazipur. 

· The capacity of the project would be 1200TPD. The treatment/ processing of the MSW would be based on DST-TIFAC technology of mixed municipal waste to RDF Fluff preparation and bio-gas generation from the organic waste. The power generation would be 10-12 MW.

 Status of Consent: 

Applied for consent to establish under Air & Water Acts on 22-06-07 & Consent to establish has been issued on 03.07.07.
Status of authorization under MSW Rules: 

Applied for authorization under MSW Rules on 30.03.07 and Authorization under MSW Rules was also issued on 03.07.07.
Action regarding clearance from other departments: 

Letter issued on 10.05.07 to the operator of the facility to submit:

· Detailed project report.

· Site clearance certificate from the land owning agency.

· EIA clearance from Ministry of Environment & Forests, Government of India.

· View of Air Force Base Station, Town and Country Planning, Department of UD, Govt. of India etc.

Status:
· Detailed project report is not received.

· Site clearance certificate from the land owning agency is not received.

· EIA clearance from Ministry of Environment & Forests, Government of India is not received.

· View of Air Force Base Station, Town and Country Planning, Department of UD, Govt. of India etc are not received.
· Decision taken in meeting held on 26.06.07:

During the meeting it is decided that conditional Consent to Establish under Air and Water be issued as done in case of Timarpur Incineration Plant site and similarly conditional Authorization under MSW Rules be also issued. 

Action taken/ Status after the meeting held on 26.06.07:

· Consent to establish has been issued on 03.07.07. 

· As decided Authorization under MSW Rules was also issued on 03.07.07.  

Other remarks:

· Reminder letter has been issued on 25.02.08 to the operator for desired information.

· Reminder letter has also been issued on 25.02.08 to Hindon Air Force Station Base, Palam Air Force Station Base, Department of Town and Country Planning, Central Ground Water Board and Deputy Commissioner (East) for obtaining views/ comments /NOC regarding the project. 
· The comments has been received from Department of Town and Country Planning, UD vide letter dated 19.02.08 (C/337).

· Air Headquarter has issued NOC vide letter dated 26.07.07 (C/431).

· As per letter dated 24.04.08 of Deputy Director (LL), DDA addressed to General Manager, Delhi Power Company Ltd., The matter has been examined it is informed that as per MPD-2021, utility is permitted in all land use zones as intimated by Planning Department of DDA (C/436).

Contd..2/-

Municipal Waste Complex at Gazipur Bio-gas Plant Site 

--2--
· Public hearing for Environmental Clearance has been conducted on 04.03.08 & proceeding is placed at (C/429). A copy of the proceeding has been forwarded to MOEF on 10.03.08 by EIA Cell.  
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Comment received from Town & Country Planning Organization, UD, Govt of India be forwarded to IL&FS and a reminder should go to others. 
Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM
Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
Delhi Food Processing Complex (Meat) at Ghazipur, Delhi

Name & Address: Municipal Corporation of Delhi, Delhi Food Processing Complex (Meat) at Ghazipur, Delhi 

Correspondence Address: MCD Department of Veterinary Services, Room No. 56, Town Hall, Delhi-06
Status of Consent: 
Applied for consent to establish under Air & Water Acts on 02-06-2005

Activity: Slaughter House (1.75 MLD)

Status: 

Applied for consent to establish under Air & Water Act on 02-06-05 EIA report not submitted alongwith the application.  The case was earlier dealt by EIA Cell and matter was sent to Ministry of Environment & Forest, since issues related to EIA notification and Hon’ble Supreme Court Orders are also involved in this case, letter was also issued on 30-08-07 by EIA Cell regarding seeking information about the Environment clearance by MOEF however reply to the said letter has not been received so far. As directed inspection was conducted by a team comprising of DPCC officials and Dr. T.K.Joshi, Head, CEOH on 24-08-07(Copy enclosed).  During the inspection the civil construction work as well as fixation and erection of machineries was going on.  The work of construction of ETP was also going on. In the vicinity the rendering plant is also coming up and an ETP was also seen.  The inspection of the facility could not be done since no responsible person at the site.  Details of the ETP submitted with the project report mentions about Physico Chemical Treatment.  Since waste water generated from both the section (i) Slaughter House (ii) Rendering Plant has mainly organic waste which is biodegradable, therefore Physico Chemical Treatment should be avoided since as per HW Rules it will be generating Hazardous Waste.  Besides above unit should also go for better sludge handling mechanism Letter was issued followed by the reminder letter as decided by the BMW Committee & Reply along with Report on ETP/ Rapid EIA Report received. MOEF Clearance yet to be received.

Decision Taken by the Committee on 04.10.07: 

Report of the inspection team was perused by the Committee. A letter may be issued to concerned officer in M.C.D. for furnishing detailed information on the construction of E.T.P. and its likely completion date and copy of letter to be sent to Sh. Ravi Das Engineer-in-Chief in M.C.D. 

Action Taken Report
w.r.t. meeting on 04.10.07:

Letter issued. Reply not received.

Decision Taken by the Committee on  15.11.07: 

Reminder Letter to be issued.

Action Taken Report w.r.t. meeting on 15.11.07:


Reminder letter issued, Reply along with Report on ETP/ Rapid EIA Report received. MOEF Clearance yet to be received.

Decision Taken by the Committee on 15.01.08: 

MS to Speak to MOEF & Expedite EIA clearance. To be taken up in the next meeting.
· Decision taken in meeting held on 28.02.2008:

Fresh inspection is to be conducted. 
Action taken/ Status after the meeting held on 28.02.08:

Proposed Slaughter House has been inspected on 26.03.08. During the visit Dr. Om Prakash (Manager) and Sh. Alok Tiwari (AE) were also present from Municipal Corporation of Delhi. The following are the observations:

12. The erection and installation of plant & machinery was in progress. As informed that the work of the Slaughter House will be completed & handed over to MCD by 20.05.08, as assured by the contractor in the court.  
Contd…2

Delhi Food Processing Complex (Meat) at Ghazipur, Delhi

--2--

13. Work of installation of ETP for the Slaughter House was under progress and civil & mechanical work is almost completed.  

14. The effluent treatment plant consisting of Physico-chemical, Anaerobic followed by Aerobic processes. 

15. Alum, Poly-Electrolyte, NaOH, HCl, & Sodium Hypo-Chloride will be used in treatment process and dosing tanks have been provided near the reaction tanks. Hence, the sludge generated from the ETP will be in hazardous nature in view of the inspection team. 

16. In the project report, the unit has mentioned that the dewatered sludge will be collected in tractors & disposed off suitably. During inspection it was found that the unit has not taken any steps for compliance of HWM Rules.

17. A sump is constructed in the Slaughter House premises, to collect the effluent and same will be pumped through pipe lines to the ETP, located about 300m away from the Slaughter House. 

18. As informed that the treated effluent will be discharged into the open drain leading to Hindon drain, however, in the later stage it is also proposed to use the treated effluent for gardening and other greening purpose, after closing of adjacent Gazipur Municipal Solid Waste Disposal site. 

19. A rendering plant is also installed near the Slaughter House for processing of dead animal to prepare fish food etc. The rendering plant was found non operational condition; however, as informed that this rendering plant was earlier operated for around 15 days for trial run. 

20. A separate ETP is installed for this rendering plant and found filled with waste water in septic condition. ETP was not in operation. 

21.  Bio gas will be generated from the anaerobic process of ETP and same will be burned in the complex. There is no provision for utilization of biogas.  

22.  As also informed that the application for Environmental Clearance for this Slaughter House & rendering plant is under consideration by Ministry of Environment & Forest. Environmental Clearance will be submitted to DPCC after obtaining it.  
Decision of Consent Management Committee in its meeting dated 12.05.2008:
(i) Inform the unit about point no. 5. The ETP will be based on physiochemical process therefore there will be generation of hazardous waste. Unit may be asked to apply for authorization under HWM Rules. (ii) Unit to submit Environmental Clearance as soon as they obtained. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM

Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
Badarpur Thermal Power Station
Status of Consent: Consent issued on 27.07.2007 and valid up to 21.03.2010.

Action Taken:

This power station was also inspected by Zonal office Lucknow of CPCB on 23.08.07 & observed that particulate matter emission from unit II & V was within the limit. They recommended:

· BTPS should install ash pond effluent recirculation system.

· BTPS should install dedicated fly ash collection system.

· Ash dyke should be designed to withstand the hydraulic load of ash while raising its height, since area downstream of ash pond is densely populated.

- CPCB has desired that BTPS takes majors to implement the above recommendations within a time frame agreed mutually and asked to submit time targeted Action Plan & ATR.
Decision taken in meeting held on 19.10.07:

A letter may be issued to General Manager to comply with CPCB directions given during inspection by CPCB on 23.8.07. This compliance must be done by 31.12.07. 

Action taken/ Status w.r.t. the meeting held on 19.10.07:

· Letter issued on 5.11.07 communicating above decision. 

· No reply received so far.

Decision taken in meeting held on 09.01.08:

MS to speak to the concerned General Manager. The deficiencies noted by the inspection team of CPCB have not been corrected and not replied to. Letter be issued with the last opportunity giving to the unit to comply with the CPCB directions during inspection and complied with it fully.

Action taken/ Status w.r.t. the meeting held on 09.01.08:

A last opportunity letter issued on 31.01.08. A reply dated 28.01.08 was received from the power plant (C/327-328 of the file). Power Plant submitted that:

1. Regarding ash pond overflow recycling:

Corporate Engg., NTPC has been conducted for exploring and conducting a techno-economic feasibility study regarding the installation of this system.

4. Installation of dry ash collection system at plant:
The Dry Ash Extraction and Transportation System (DAETS) for 2X 210 MW of BTPS has already been awarded and is in execution stage. For 3X 95 MW units also there is a proposal of DAETS and for that the talks are going on with NTPC Vidyut Vyapar Nigam (NVVN) Ltd.

5.  Regarding ash dyke design aspect to withstand the hydraulic load while raising its height:
All the necessary precautions have already been taken by Corporate Engg., NTPC in the design aspect of ash dyke raising.

The above said reply has been forwarded to CPCB vide letter dated 11.02.08 after necessary approval on file. 
· Decision taken in meeting held on 28.02.2008:

Letter to be issued bearing the directions for meeting the standard of Particulate Matter of 50 mg/Nm3 along with the copy of the minutes wherein it was decided that the standard for Particulate Matter has been made stringent of 50 mg/Nm3. In case high emission is caused due to high ash content in coal, the ash content may be reduced in the fuel (coal).
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Action taken/ Status w.r.t. the meeting held on 28.02.2008:

· Letter issued to BTPS on 24.03.08 to meet the standard of 50 mg/Nm3 for Particulate Matter. 

· They informed that-  “Comprehensive renovation and modernization package specification for improvement in ESP efficiency to achieve emission <50 mg/Nm3 in 2X210 MW units has been finalized at an estimated cost of Rs 40 crores and expected date of NIT for this package is by the end of June, 2008. Further to meet the MOEF guidelines to use coal having ash less than 34% on annualized average basis, the following action have been taken:-

Use of imported coal having very ash ~8% started at BTPS since Jan. 2008. This low ash imported coal is being blended with high ash coal of BCCL/ CCL. The quantity of low ash coal has been imported till date is around 1.00,000 MT”.

· BTPS has not submitted any Comprehensive renovation and modernization package specification for improvement in ESP efficiency to achieve emission <50 mg/Nm3 in 3X95 MW units.

· BTPS has also not submitted any time bounded programme to achieve emission <50 mg/Nm3.

Decision of Consent Management Committee in its meeting dated 12.05.2008:
In case of two units considered for upgradation, let them confirm the status in next CMC. As regard three remaining units, issue reminder for their response. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               
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 Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
I.P. Thermal Power Station

Status of Consent: 
· Consent issued on 19.03.07 and valid up to 27.04.08.

· Applied for Renewal of consent on 17.04.08
Action Taken:

This power station was also inspected by Zonal office Lucknow of CPCB on 20.08.07 & observed that particulate matter emission from unit 3 & 5 was exceeding the limit. They recommended:

· IPTPS should adopt better ESP maintenance practices and ash evacuation system for controlling the emission of particulate matter.

· IPTPS should also take necessary action for better ash pond management to maintain the concentration of suspended solids within the prescribed limit.

· IPTPS should improve over all housekeeping immediately.

· CPCB has desired that IPTPS takes majors to implement the above recommendations within a time frame agreed mutually and asked to submit time targeted Action Plan & ATR.

Decision taken in meeting held on 19.10.07:

A letter may be issued to General Manager to comply with CPCB directions given during inspection by CPCB on 20.8.07.This compliance must be done by 31.12.07. 

Action taken/ Status w.r.t. the meeting held on 19.10.07:

· Letter issued on 5.11.07 communicating above decision. 

· No reply received so far.

Decision taken in meeting held on 09.01.08:
MS to speak to the concerned General Manager. The deficiencies noted by the inspection team of CPCB have not been corrected and not replied to. Letter be issued with the last opportunity giving to the unit to comply with the CPCB directions during inspection and complied with it fully.
Action taken/ Status w.r.t. the meeting held on 09.01.08:

Replies dated 07.01.08 was received from the power plant (C/243-252 of the file). Power plant submitted that:

1. Thermal Power Station should adopt better ESP maintenance practices and Ash evacuation system for controlling the emission of particulate matter:-



DGM (Opr.) IPS stated that the test results of online monitoring/stack (ESP results) unit wise as furnished by Mgr (ESP) are well within the prescribed limit of 50 mg/Nm3. The test results unit-wise are attached as Annexure-I at C/247-249. On examination of these results the stack emission for unit no. 3 was not meeting the prescribed limit of 50 mg/Nm3. In the results sheet it is mentioned that only old ESP was an operation and new ESP installed accidentally failed down and under reconstruction yet. The methods/Practices adopted for ESP maintenance, submitted by the power plant may be seen at Annexure-II(C/246). He has also submitted that Segregating valves are installed on ESP Hoppers of Unit No. 5 and will be installed gradually on other units. MoU with Cement manufacturers were signed for dry ash collection directly from ESP Hoppers.

2. Thermal Power Station should also take necessary actions for better ash pond management to maintain the concentration of suspended solids within the prescribed limit:-


DGM (Opr.) IPS stated that the test results in respect of TSS of the effluent of Ash Pond as furnished by Mgr (Civil) are well with in the prescribed limits. The ATR enclosed as Annexure-III(C/245). He has also stated that in view of closing of I.P. Station by the year 2010, the action for zero discharge at Ash pond has been dropped being costly affair.
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3. Thermal Power Station should improve overall housekeeping:-

The Power Plant submitted that:
d. The area wise house-keeping in respect of water channel/Drain cleaning of B-Channel for maintaining proper flow of sludge / Ash slurry up to DW water tank, cooling water channel, coal mill channel, Ash slurry channel are being regularly maintained through Annual Maintenance Contract for reusing the decanted water for ash transportation.

e. The housekeeping for cleaning of operation floor area at ash pond, Boiler furnace bottom, coal mill reject is also being carried out through separate Annual maintenance contract for suppression of the fugitive dust.

f. Besides above, the activities for disposal of old scrap / waste material from the I.P. site are also being perused with D&R Department and the disposal of old/scrapped cooling towers Units No. 1 are already in hand to keep up the good housekeeping at the plant.
The above said reply has been forwarded to CPCB vide letter dated 11.02.08 after necessary approval on file.

· Decision taken in meeting held on 28.02.2008:

Letter to be issued bearing the directions for meeting the standard of Particulate Matter of 50 mg/Nm3 along with the copy of the minutes wherein it was decided that the standard for Particulate Matter has been made stringent of 50 mg/Nm3. In case high emission is caused due to high ash content in coal, the ash content may be reduced in the fuel (coal).

Action taken/ Status w.r.t. the meeting held on 28.02.2008:

· Letter issued to IPTPS on 24.03.08 to meet the standard of 50 mg/Nm3 for Particulate Matter. 
· A reply dated 01.05.08 received from IPTPS along with data of online monitoring w.e.f. 15.02.08 to 16.03.08. This data is not for all the days between this period and meeting the prescribed limit of 50 mg/Nm3 except a result of unit for on 14.03.08, which is 57 mg/Nm3. The power plant also informed that “in case of new ESP of Unit# 3 which fell accidentally is still under re-erection, ash evacuation system of new ESPs are also under final commissioning stage to get  improved results, stack emission with 50 mg/Nm3 in all Units”. 
· Noise monitoring report for DG set is not meeting the prescribed standards.
· DPCC monitoring reports show that all the operational ducts of this power station are not meeting the standard of 50mg/Nm3 for particulate matter except in duct of unit no. IV on 12.12.07. The Particulate matter in the stacks as per last six DPCC monitoring report are as under:
	S. No.
	Date of monitoring
	Particulate matter in duct of (in mg/Nm3  )

	
	
	Unit No.- II
	Unit No.-III
	Unit No.-IV
	Unit No.-V

	1
	03.10.07
	#
	#
	86
	#

	2
	16.11.07
	96
	89
	51
	#

	3
	12.12.07
	82
	69
	45
	#

	4
	28.01.08
	#
	103
	78
	#

	5
	26.02.08
	80
	101
	124
	#

	6
	19.03.08
	142
	76
	82
	#


# Shut down/ under maintenance.
Contd…3

I.P. Thermal Power Station

--3--

Decision of Consent Management Committee in its meeting dated 12.05.2008:

Due to installation of new ESP with unit no. 3, after commissioning the result will improve for unit no. 3 only. There is no proposal to improve efficiencies of other three remaining units. Reminder should be issued. Noise monitoring of D.G. Set is also not meeting the prescribed limit. Therefore, they may be asked to take adequate measures to have noise emissions within the limit. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM
Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
Rajghat Power Station

Status of Consent: Applied for “Consent to Operate” on 30.06.2004.

Action Taken:

· Letter issued to Pr. Secretary (Power) on 17.07.2007.

· The unit has replied that Ministry of Power, GNCTD has taken a decision for closing the coal based power plants in near future. A request has been made that as huge funds are required for installation of ETP, permission may be given that water is used for transporting fly ash to ash ponds. 

· This power station was also inspected by Zonal office Lucknow of CPCB on 21.08.07 & observed that untreated effluent (TSS- 198 mg/l) is being discharge into to river. They recommended:

· Adequate waste water treatment plant should be provided.

· An interrupted access to ash pond area should be provided.

· CPCB has desired that RTPS take measures to implement the above recommendations within a time frame agreed mutually and be asked to submit time targeted Action Plan & ATR.

Decision taken in meeting held on 19.10.07:

A letter may be issued to General Manager to comply with CPCB directions given during inspection by CPCB on 21.8.07. This compliance must be done by 31.12.07. 

Action taken/ Status w.r.t. the meeting held on 19.10.07:

· Letter issued on 5.11.07 communicating above decision (C/353). 

· Though reply is awaited, a letter dated 29.12.07 (C/355) received indicating that revised proposal for installation of low cost water treatment plant to utilize waste water in ash handling plant is under consideration. RPH has also initiated the following works : 

· Cleaning of existing station drain pit about 6m diameter and 6m deep which was already available for treating the station drain water for decantation and action have been initiated for new pipes to connect and pumping the decanted water to ash pump water tank to reuse for transporting ash slurry to ash pond meeting the proposal of DPCC in the letter of the year 2004. 

· Submersible pump installed to reuse backwash water of the filters at WTP and going to drain also reduced.

· Piping connection is almost in final stage for sending the sludge slurry water from WTP (neutralization pit) to ash pond. Thus the discharge at station drain will be further reduced substantially.

· RPH has not submitted their compliance report in respect to the letter dated-5.11.07.  However requested for issuing consent to operate.

Decision taken in meeting held on 09.01.08:

MS to speak to the concerned General Manager. The deficiencies noted by the inspection team of CPCB have not been corrected and not replied to. Letter be issued with the last opportunity giving to the unit to comply with the CPCB directions during inspection and complied with it fully.
Action taken/ Status w.r.t. the meeting held on 09.01.08:

Replies dated 07.01.08 and 08.01.08 were received from the power plant (C/365-367 of the file). Power plant submitted that:

5. Regarding adequate treatment  to the effluent through station drain into the river, the action taken are;

d. One pump alongwith its discharge line are laid and already started reusing back wash water of he gravity filters as inlet to the Aerator (Clarifier) and thus reduced consumption of water and consequently effluent quantity in station drain. Procurement action for one additional pump is also in process to have permanent arrangement.
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e. Needful discharge line piping has been laid from sludge slurry water pumps (clarifier) and connected to the Ash Surry Line and sludge being discharged to the Ash pond thus reducing also the effluent quantity to the station drain.

f. The installation of pumps and lying of discharge pipelines up to the ash pump water tank will be completed by the end of March, 2008. The decanted water of the station drain pit will be utilized for transportation of fly ash in slurry form to the ash pond as per advice of DPCC.


In the meantime time, the above said station drain pit having diameter of 6 meter and depth of 6 meter meant for decantation have been cleaned after removing sludge deposited.


The effluent from various plants including balance effluent from WTP (Neutralization Pit) will be collected in this cleaned station drain pit from where the decanted water be reused for transportation of ash slurry to the ash pond and thus virtually there will be no effluent discharge to river through station drain.

6. Un- interrupted access to ash pond-area – Reg.

The grass/ wild bushes grown in the area during monsoon has been cut and the needful repair of the roads has been done to remove the interruption.
Recommendation of CPCB for dry ash collection –Reg.

Ash Silo Systems have been revived and dry fly ash collection is being done by the cement manufacturer (about 1000 MT/month).

7. Regarding bringing down the particulate matter emission;

Regulation of Bapcon Control System and Auto Rapping System is being done regularly for better operation of ESP fields; attending nozzles of hydro vector and leakages etc. in the ash evacuation system; scheduling have been planned to wash/ clean the ESP insides; straightening/ adjustment of gaps between emitting electrodes and collecting plates as per the recommendation of OEM; replacement of segregating valves & solenoids are being done during shut down to get the maximum efficiency of the combustion of fuel also regulated and use of furnace oil is being minimized to bring down the particulate matter emission through stack well within the permitted limit.

8. Regarding Zero discharge by reusing ash pond overflow water:
The scheme for reusing decanted water from ash pond overflow was initiated but kept in abeyance for some period with the instructions received from Ministry of Power, GNCTD to avoid excess O&M expenditure for the coal based power station like RPH and IPStn. Which are to close by 2010 of so in due course.

However, with the expected running of RPH beyond 2010, this case has been taken up again on the basis of CPCB’s / DPCC’s recommendation for recirculation of ash pond water for making ash slurry to conserve water. This work is expected to be completed by the end of the year 2008.

The above said replies have been forwarded to CPCB vide letter dated 11.02.08 after necessary approval on file.

· Decision taken in meeting held on 28.02.2008:

Letter to be issued bearing the directions for meeting the standard of Particulate Matter of 50 mg/Nm3 along with the copy of the minutes wherein it was decided that the standard for Particulate Matter has been made stringent of 50 mg/Nm3. In case high emission is caused due to high ash content in coal, the ash content may be reduced in the fuel (coal).

Contd..3/-

Rajghat Power Station

--3--
Action taken/ Status w.r.t. the meeting held on 28.02.2008:

· Letter issued to RTH on 24.03.08 to meet the standard of 50 mg/Nm3 for Particulate Matter. 

· A reply dated 02.05.08 received from RPH. They submitted that “in order to achieve the SPM level of 50mg/Nm3, they have taken up the matter with M/s. Bharat Heavy Electrical Limited, the OEM, M/s. Alstom Projects India Limited along with other concerned agencies. All these agencies have opined that the SPM level cannot be reduced directly to 50mg/Nm3 from 150mg/Nm3. The desired level can be achieved in phases. In the first phase the same will be reduced to 80mg/Nm3 by upgradation of the existing controllers of ESPs and in second phase either by increasing the volume of the collecting area of the ESP hoppers or by flue gas conditioning”.

· RTPS has also not submitted any time bounded programme to achieve emission <50 mg/Nm3.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

The unit should reduce the emissions in a phase wise manner as submitted by them. In the first phase they must reduce to 80 mg/Nm3 by upgradation of the existing ESPs. A time bound programme may be submitted to achieve the emissions up to 80 mg/Nm3.
Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               
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Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
Pragati Power Station, ITO
Status of Consent: Applied for renewal of the Consent vide ID. No. 24530 dated 18.12.07 (Earlier Consent to operate issued on 21.12.05 and valid up to 12.01.08).

Action Taken:

· Letter issued on 20/8/2007. No reply received so far.

· A letter dt 27.08.07 received from Manager (T) Environment, IPGCL-PPCL, informing that-

- MCD is not allowing to dump the Water Treatment Plant (WTP) sludge at Compost Plant /SLF site of MCD.

- The sludge is being dumped at the side of RTPS ash pond to be used by fly ash manufacturer because it contains more than 50% CaO and it is non hazardous.

- Part of this sludge gets mixed with wet ash in the ash pond as the less quantity required for bricks manufacturing.

- Requested to instruct MCD to accept the sludge.

- If it is not materialized, the disposal in ash pond / fly ash brick manufacturer stockyard will be continued and requested to moderate suitably the Terms & Conditions of the consent issued. 

Decision taken in meeting held on 19.10.07:

In response to letter received from Manager (T) Environment, IPGCL-PPCL be informed that the sludge may be used for brick manufacturing by using available technology and with the help of NGOs like Development Alternative. 

Action taken/ Status w.r.t. the meeting held on 19.10.07:

· Letter issued on 5.11.07 communicating above decision. 

· No reply received so far.

Decision taken in meeting held on 09.01.08:
MS to speak to the concerned General Manager and reminder letter to be issued. 

Action taken/ Status w.r.t. the meeting held on 09.01.08:

A reply was received from the power plant (C/339-351). The reply was not with concrete step taken for utilization of sludge. Reminder letter has been issued on 15.02.08.

· Decision taken in meeting held on 28.02.2008:

To be put up in next CMC (MSW) Meeting.

Status of monthly monitoring conducted by DPCC laboratory:
· Noise monitoring report for DG set is not meeting the prescribed standards. Stack monitoring report is also not submitted as having DG set of 1250 KW.
· Monitoring reports for the month of January and Feb. 2008 were meeting the prescribed standards. However, monitoring could not be conducted in March, 2008 as the plant was found under maintenance/ shutdown on 19.03.08.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

Deficiencies may be informed to the unit, for expeditious action for their rectification. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               
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Decision of  CMC (MSW) taken in its 9th meeting held on 12.05.2008

[ Review of ATR of decision of CMC (MSW) dated 28.02.2008]
I.P. Gas Turbine Power Station

 Status of Consent: Applied for renewal of the Consent vide ID. No. 24589 dated 27.12.07 (Earlier Consent to operate issued on 23.03.07 and valid up to 04.01.08).

Action Taken: A letter dt 27.08.07 received from Manager (T) Environment, IPGCL-PPCL, informing that-

- MCD is not allowing to dump the Water Treatment Plant (WTP) sludge at Compost Plant /SLF site of MCD.

- The sludge is being dumped at the side of RTPS ash pond to be used by fly ash manufacturer because it contains more than 50% CaO and it is non hazardous.

- Part of this sludge, get mixed with wet ash in the ash pond as the less quantity required for bricks manufacturing.

- Requested to instruct MCD to accept the sludge.

- If it is not materialized, the disposal in ash pond / fly ash brick manufacturer stockyard will be continued and requested to moderate suitably the Terms & Conditions of the consent issued. 

Decision taken in meeting held on 19.10.07:

In response to letter received from Manager (T) Environment, IPGCL-PPCL be informed that the sludge may be used for brick manufacturing by using available technology and with the help of NGOs like Development Alternative. 

Action taken/ Status w.r.t. the meeting held on 19.10.07:

· Letter issued on 5.11.07 communicating above decision. 

· No reply received so far.

Decision taken in meeting held on 09.01.08:
MS to speak to the concerned General Manager and reminder letter to be issued. 

Action taken/ Status w.r.t. the meeting held on 09.01.08:

A reply was received from the power plant (C/440-452). The reply was not with concrete step taken for utilization of sludge. Reminder letter has been issued on 15.02.08.

· Decision taken in meeting held on 28.02.2008:

To be put up in next CMC (MSW) Meeting.

Status of monthly monitoring conducted by DPCC laboratory:
· Noise monitoring report for DG set is not meeting the prescribed standards.
· Last three months monitoring reports for the months of January to March, 2008 were meeting the prescribed standards. However concentration of NOx was found beyond the prescribed limit of 75ppm in GT1, GT5 and GT6 which were 90ppm, 90ppm and 80ppm during monitoring on 17.12.07.
Decision of Consent Management Committee in its meeting dated 28.02.2008 :

Deficiencies may be informed to the unit, for expeditious action for their rectification. 

Chairman       MS          Dr. S. K. Gupta         SEE            Dr. Chetna Harjai       EE              AEE               

DPCC            DPCC      Member (Acad.)       MSWM      Members (Env.)           MSWM      MSWM
Decision of Committee (MSWM) taken in its meeting dated 12.05.2008
MAYAPURI CETP  (12 MLD)

Consent status of CETP

· Consent application for consent to operate was submitted by the CETP Society on 07.05.07
Decision of Committee taken on 19.10.2007

The case of Mayapuri CETP was examined by the Committee and it was found that TSS (at inlet), BOD & TDS (at outlet) are well above the norms. 

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 4.2 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The CETP society will submit a Bank Guarantee of Rs. 5 lakh (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.

Deficiencies mentioned in SCN issued & brief of its reply by CETP Society :

Flow at the inlet observed is very low (in the range of 4-5 MLD) against the installed capacity of 12 MLD.

· Average effluent being received at CETP is 4 to 5 MLD from the date of its operation by DSIDC in year 2002.

· Pressure gauges were non-operational from the time of taking over of CETP from DSIDC, now we have calibrated and all are in functional 

No flow meter installed at outlet of CETP. 

· There is no such provision has been given at outlet for installation of flow meter by DSIDC. 

As per DPCC analysis report dated 09-04-2007 BOD (43) Cl (1030) are not as per the norms.

· Submitted copies of daily analysis reports conducted at plant laboratory wef July to Oct 07.  

Significant quantity of silt/sludge found in equalization tanks & pre chlorination tanks. However, one equalization tank was found without effluent/dry for desilting of silt/sludge. 
· There is no mechanism system were provided by constructing agencies for removal of sludge. However, one equalization tank totally desilted w.e.f. 22.07.07 to 07.08.07.

Pressure gauges attached to DMFs & ACFs found in non operational condition.
· The same were mentioned in the deficiencies to DSIIDC at the time of taking over of CETP from DSIDC. Now we have calibrated the pressure gauges and all are in functional.
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As reported, CETP not being received effluent from REPS- II due to blockage/blocking in pipe line/rising main for one month.
· DSIIDC has carried out work of maintenance of RESP-II in Oct 07 and now effluent is being again received from RESP-II w.e.f. 22.10.07.

Individual connection with conveyance system

· Details of individual connections should be obtained from DJB authorities as they are maintaining the whole conveyance system of the industrial area. There is no such separate conveyance system provided for trade effluent.

Bank Guarantee

· As regard submission of Bank Guarantee of Rs. 5 Lacs, the matter will submitted in the next meting of AGM of CETP Society and confederation of CETPs Societies Delhi for suitable decision.

At present there is no such deficiency at plant and plant is being maintained & operated by the CETP Society efficiently.

Inspection status:

Observation during inspection of CETP on 26.11.07 is as follows:

· Equalization  tank No 1 found empty and cleaned (except sump portion) As reported cleaning/ de silting work completed on 7th Aug 07, approx 25 MT sludge was removed & stored in shed.

· Grit Chamber & Screens are not having proper cleaning mechanism and  clean manually. Removal from screen & grit chamber found lying on katcha floors near it. After drying it will transfer in shed.

· Flocks removed manually from the portion of tank between tube settler & flash mixer & found lying on Katcha floor near the flash mixer & after dying transfer it in shed. 

· Pressure gauges attached to DMFs (12 nos) & ACFs (8 nos) found in non operational condition.
· Flow meter not installed at outlet of CETP. 

· Level meters of equalization tank & final treated tank found in non operational condition.

· Average intake effluent in Oct. 07 was 2.54 MLD.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Member Secretary, DPCC to check whether the then Chairman, DPCC has confirmed the installation of flow meter at outlet of CETP in EPCA meeting through its minutes. 

Since the unit appears to have corrected some of the deficiencies, a fresh inspection may be done and report be submitted in next CMC (MSW) meeting. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 

Contd..3..
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Action Taken Report
Letter issued on 28.01.08. CETP society has submitted letter on 13.02.08 informing that the deficiencies pointed out has been corrected and requested for issue of consent.
Inspection status:

Observation during inspection of CETP on 18.01.2008 is as follows:

· One equalization tank (from which silt removed earlier) found in use.

· Another equalization tank found empty & silt removed,found stored in shed. 

· Pressured gauges attached to DMFs& ACFsfound in non operational condition.

· During inspection 6 DMF found operational. As reported they operate DMF on rotation basis.

· Level meter of equalization tank & final treated tank found functional.

· As reports work of flooring near grit chamber & flesh mixer is going to start with in 15 days.    

DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	TSS-296
	_
	TSS-332
	BOD-38          TDS-2200
	TSS-336
	BOD-40
	Non operational
	Non operational


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

To be put up in next CMC (MSW) Meeting.
Action Taken Report
 In response to our letter dated 10.03.08 society has submitted that they have not obtained any analysis report from DPCC for the month of Dec. 07 so far and as per analysis report of Jan. 08, received from DPCC final outlet quality is well within the prescribed norms and requested to issue necessary consent.

A copy of letter dated 04.04.08 addressed to DSIIDC received from CETP society mentioning that the peripheral Sewer/ Rain Water Piper lines laid by DSIIDC are not properly inter- connected  and now CETP society has completed this work. Society has requested to make necessary recovery from the then constructing contractor and amount incurred shall be paid to CETP society.

Vide letter dated 24.04.08 CETP society has submitted point wise counter reply of the affidavit filed by Commissioner of Industries in the Hon’ble Supreme Court mentioning as under:  

9. CETP society have already provided list of the members to the appropriate authority on 24.09.07 

10. The defaulter lists provided to the appropriate authority on 03.03.08, 12.02.08, 02.04.07, 31.11.04 & 26.02.04.

11. Mayapuri CETP society already contributed 50% apportionment cost amounting to Rs. 21809000/- to DSIIDC in time. 

12. Managing Committee of Mayapuri CETP society comprising of elected members of four major Indl. Welfare Association of the area and unanimously re-elected again in its adjourned general body meeting held on 26.04.05 and resolved to work continuously till next AGM. Next meeting of AGM will be scheduled in the month of June 2008.

13. The general body on 26.04.05 resolved that M/s Manmohan & Associated will continuously work as C. A. for society. 
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14. CETP society has already appointed qualified technical staff at CETP as per criteria given by appropriate authority and necessary list have already been sent to Appropriate Authority & Member Secretary, DPCC vide our letter dated 02.01.08 & 15.03.08. 

15. The Bank Account of society are maintained only in 2 nos. banks i.e. HDFC Bank and Canara Bank in Mayapuri Indl. Area and informed to Appropriate Authority in the quarterly returns duly filled up proformas of all information required by the appropriate authority time to time.

16. Apart form this CETP society have sent no. of additional document/ information to the appropriate authority.

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-440
	BOD- 36          TDS-2200
	TSS-368
	BOD-37


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
In view of the parameters BOD & TDS are not meeting the prescribed standard at the outlet of CETP, as per monitoring conducted by DPCC laboratory in month of March, 2008, Bank Guarantee of Rs 5 lakh is confirmed and CETP Society shall submit the Bank Guarantee by 30.06.2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

MANGOL PURI CETP (2.4 MLD)

Consent status of CETP

Consent to operate issued with conditions on 27.07.2007.

Decision of Committee taken on 19.10.2007

A letter issued to CETP society to correct the deficiencies noted during the inspection on 18.07.07and to comply with the earlier conditions which were imposed when the consent to operate was granted. 

It was also found that against the installed capacity of 2.4 MLD, the CETP Society is operating it at only 1.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

 The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The society will submit a Bank Guarantee of Rs. Fifty Thousands (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.

Deficiencies mentioned in SCN issued & brief of its reply by CETP Society:

Pressure gauges attached to DMF & ACF found not in operational condition.

· New pressure gauges have been installed.

No flow meter installed at outlet of CETP.

· There was no flow meter installed at the outlet ever since the plant was constructed and accordingly we have informed the DSIDC. There is no such provision provided by the DSIDC in this matter.

Bank Guarantee

· The matter has been discussed at the confederation level and we shall act in accordance with the other CETP Societies as when it is decided. 

Consent to Operate to was granted on 27.07.2007 with the following conditions: 

4. To increase the effluent quantity.

We ca not import extra effluent from outside the industrial area. Each and every unit is connected to DJB common sewer line with the CETP inflow pipe.

5. To install mechanical dewatering system.

We have already arranged for the submersible pump and this has been installed already in plant.

6. To modify the acoustic enclosure with DG set to achieve the insertion loss.

Our acoustic enclosure with DG et is in sound position ever since it was installed and there is no scope of any further improvement.
Inspection status:

Observation during inspection of CETP on 05.12.07 along with CPCB during training program is as follows:

No flow meter installed at outlet of CETP.

DG Set with acoustic enclosure installed.

CETP Society has shown new pressure gauges during inspection & as reported same shall be installed within 2-3 days.

Average intake effluent during the month of Nov. 07 -  MLD

Flow meter at inlet found operational.
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Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Since the unit appears to have corrected some of the deficiencies, a fresh inspection may be done and report be submitted in next CMC (MSW) meeting. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 

Action Taken Report
Letter issued on 25.01.08.
Inspection status:

Observation during inspection of CETP on 21.01.2008 is as follows:

· Acoustic enclosure installed with DG Set.
· New pressure gauges installed with ACFs & DMFs.

· Flow meter at inlet found operational.
· Total intake during Dec 07 was 34.11 MLD (Average-1.1MLD).

· One aerator (out of four) of aeration tank found under maintenance. 

DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	TSS-268
	Cl-1080      TDS-3900
	TSS - 268
	Cl-1830   TDS-5070
	TSS - 980
	Cl-1040   TDS-3946
	TSS-366
	Cl-1800   TDS-6954


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Letter to be issued to CETP to submit an affidavit as to why there is  fluctuation in the parameters of water analysis report compared to the standards. 

Action Taken Report
Letter issued on 19.03.2008. 

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-480
	Cl-2080      TDS-6700
	TSS-380
	Cl-2153      TDS-5020


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
In view of the parameters Cl & TDS are not meeting the prescribed standard at the outlet of CETP, as per monitoring conducted by DPCC laboratory in month of March and April, 2008, Bank Guarantee of Rs 50,000 is confirmed and CETP Society shall submit the Bank Guarantee by 30.06.2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008
Badli Industrial Estate CETP ( 12 MLD)

Consent status of CETP

Consent to operate issued on 28.02.07 to CETP society for period of three years and valid up 28.12.09.

Decision of Committee taken on 19.10.2007

This CETP was inspected on 17.4.07 and again on 11.7.07 the following deficiencies were noted in first time and the second time as under: -

The CETP society has neither corrected the deficiencies nor sent the reply. In view of the above, issue SCN for revoking of consent u/s 27 of the Water Act.  

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 1.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

 The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The Society will submit a Bank Guarantee of Rs. Five Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.  
Deficiencies mentioned in SCN issued & brief of its reply by CETP Society:

Flow meter sent to repair 

· repaired flow meter again found faulty & now order for new flow meter has been placed & same will is likely to be operational well before 31.12.2007.

No flow meter installed at outlet of CETP.  

· Flow Meter at the outlet was not installed in the plant by DSIIDC. It was agreed by DPCC that the flow meter at the outlet of CETP shall be installed by them only.

Grit chamber, Equalization tank work field with significant quantity of silt/sludge.

· Slit / sludge is accumulated in these tanks inspite of regular cleaning due to presence of solid waste / dust /building material malba in the domestic sewage / storm water carrying road washings/ kacha muddy drain carrying mud into the effluent going into the CETP.

· No arrangement has been provided in the plant to ensure proper cleaning of the tanks. We have already started the process of cleaning of various tanks in the plant by using a borrowed sludge pump.

· No arrangements have been provided by the authorities so far the disposal of the sludge generated in the plant. The tank cleaning activity, therefore, is getting affected due to this problem.

· We are fully committed to follow every rule in letter and sprit and have never allowed any slit / sludge to be kept outside the plant premises.

Pre chlorination as well as post chlorination were non-operational.

· Pre and post chlorination is being done in the plant as per requirements the effluent under treatment.
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Dosing of Alum and Bleaching not being carried out due to defective pipe line.

· Dosing of Alum and bleaching powder too is being as per requirements of the effluent under treatment. In a plant such as ours, it is quite natural to encounter defects due to normal wear and tear and corrosion.

Two number of pressure gauges ( out of 8 ) attached to ACF and 2 gauges (out of 12) of DMFs work found non-operational. 

· All such defects are routinely addressed and taken care of by our team running the plant. 

Two aeration (out of 3) found out of order.

· These were under routine maintenance and were duly made fully operational subsequently.

One vacuum filter found out of order and other also partially operational due to non-operational of vacuum pump.

· Reported out-of-order Vacuum Filter is under break down maintenance requiring major repairs. Effective steps are beings undertaken at our end to make this Filter operational in the shortest possible time. Moreover, the partially operational Vacuum Filter has been made fully operational. As such there is no hitch in the smooth operation of the plant.

TDS

· Neither NEERI has recommended nor DSIIDC has provided any technology / hardware (such as RO, DM plant or evaporation) for reduction of TDS at any stage of operation. CPCB and EPCA have also agreed to keep  the fixing of standard of TDS at abeyance or to raise the standard an achievable value.

· We feel that holding  CETP Society responsible for any lapses talking place outside the plant is neither correct nor justifiable.

· Occurrence of defects in any equipment in a plant like ours is a natural phenomenon which takes place during the course of its normal running. The so-called deficiencies are, therefore, not really deficiencies but issues that may occur during operation of any plant of similar nature. What is important is the fact that appropriate and timely actions have been taken and being taken to ensure proper running of he plant.

Flow intake range - 0.78 to 1.56 MLD.

· This is the responsibility of DJB in terms the Agreement for maintenance and Operation of CETP. However, the management of the Society is taking all measures under its control to ensure compliance of these directions.

· The sewer lines on Badli are badly chocked and require extensive desilting and cleaning. As a result of chocking of the conveyance system, its capacity to carry effluent to the plant is getting severely limited and this also results in its overflowing at several locations in the estate and the effluent gets entry into the open drains of the area.

Bank Guarantee of Rs. Five Lakhs 

· There have been no willful wrong doing / default on our part, there is no justification whatsoever in asking us to submit a bank guarantee. It is therefore, prayed tat this direction may please be withdrawn.

· There is no justification in asking for any affidavit from us on the matter.

· Our request for withdrawing the harsh penalty of imposing a bank guarantee and filing of affidavit shall merit your favorable consideration. 

Inspection status:

Observation during inspection of CETP on 27.11.07 is as follows:

Flow meter at inlet not in operational condition. 

Flow meter at outlet of CETP not installed.

Grit chamber, equalization tank & pre chlorination tanks are fillede with silt/ sludge.

Pre chlorination & post chlorination not done.

Dosing of Alum & bleaching  not carried out since long, pipe lines of dosing defective. 

Pressure gauges of DMF & ACF (4nos) are not functioning.

One vaccume filter is non operational condition.
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Average intake in month of Oct 07 - 0.70 MLD

A shed provided for storage of Hazardous Waste.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Since the unit appears to have corrected some of the deficiencies, a fresh inspection may be done and report be submitted in next CMC (MSW) meeting. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 

Action Taken Report
Letter issued on 25.01.08. 

Inspection status:

Observation during inspection of CETP on 21.01.2008 is as follows:

· Flow meter at inlet found operational. 

· Grit chamber found cleaned. CETP society has installed a sludge pump for removal  of sludge from equalization tank.
· One pre chlorination tank cleaning activity going on during inspection.
· Pre chlorination & post chlorination dosing found functioned.
· Pressure gauges of ACF & DMF found replaced. During inspection 4 ACF & DMF found operational. As reported, ACF & DMF are operated on rotational basis being low intake effluent.
· One vacuum filter found out of order & other found operational.
· Total intake during Dec 07-19.42 ML
DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	TSS- 520                          Cr-2.92
	_
	Non operational
	Non operational
	Cr- 3.6
	_
	Cr-2.41
	_


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

No action. 

Action Taken Report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-480
	_
	Cr- 4.21
	_


Decision of Consent Management Committee in its meeting dated 12.05.2008:

In view of the parameter BOD is not meeting the prescribed standard at the outlet of CETP, as per monitoring conducted by DPCC laboratory in month of April, 2008, Bank Guarantee is reduced from Rs. 5 Lakh to Rs. One Lakh and confirmed to be submitted by 30.06.2008 by CETP Society.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008
Wazirpur Indl Area CETP ( 24 MLD)
Consent status of CETP

Consent to operate issued on 23.02.07 to CETP society for period of three years and valid up 27.12.09.

Decision of Committee taken on 19.10.2007

The unit has not complied with the directions given after inspection on 13.4.07. A SCN notice for closure / revocation of consent be issued.

The unit has further not bothered to correct deficiencies found during the inspection on 19.7.07. It was also found that against the installed capacity of 24 MLD, the CETP Society is operating it at only 3.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

 The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The society will submit a Bank Guarantee of Rs. Ten Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections not done by 31.12.07. The unit is given a last chance to correct its deficiencies by 31.12.07 failing which the consent will be revoked and heavy penalty will be imposed on CETP society. CETP society must operate the CETP plant professionally, efficiently, effectively. Copy should be sent to MD (DSIDC) and Comm. of Industries.
Deficiencies mentioned in SCN issued & brief of its reply by CETP Society :

Flow meter installed at inlet was still out of order. The same has gone to the manufacturer for repair.

· We are taking up the matter with DSIDC who has selected this Hardware for change over to physical/mechanical weir, so that there are no break downs.

No flow meter installed at outlet of CETP.

· In the EPCA meeting (Aug. 2005), the Chairperson, DPCC had promised to provide outlet flow meter, if this is done we shall e grateful.

Flow observed to be in range of 3-4 MLD against instak\lled capacity of 24 MLD.

· All the Small and tiny units operating in the area generated only 3.4 MLD (Trade & Domestic) effluent as per average water consumption calculations. However, effluent what so ever is coming to CETP is being taken care of.

· Matter regarding creation of abnormally higher capacity is subjudice as the industries has been the big losers by way of enhance capital cost as well as recurring operation & maintenance cost.

Receiving chamber & grit chamber filled with silt/ sludge.

· In spite of regular cleaning receiving chamber / grit chamber gets filled with slit due to heavy surge of solid waste due to demolitions by MCD / DDA, and storm water / kacha muddy drain (carrying mud) into the effluent coming to CETP.
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· There is no provision for mechanical cleaning. You are requested to kindly guide / advise us to further streamline the system.

Conveyance system was yet to be commissioned.
· Conveyance system has already been commissioned by any specific short fall may reported to DJB through DSIDC for a corrective action as the responsibility for operation and maintenance of Conveyance system is of DJB/DSIDC.

Pressure gauges attached to DMF & ACF were found not in operational condition. 

· PGs are functional and are being checked fortnightly, problem if any is being rectified and re-calibrated.  PG have no impact on the operation of tertiary plant, it is merely an indication for backwash requirement.

No pretreatment for pH was being done at unit level. However, pH of in-effluent observed as 2.7. 

· pH after treatment at the outlet of CETP is well within limits as per DPCC analysis reports of lasts one and half years, however , the individual industries monitoring at present is being done by DPCC, for which we have repeated written  to the Appropriate Authority to transfer power to CETP Societies as decided in the EPCA meeting and written in the O&M agreement as promised by the Government of Delhi.  It would be in the interest of the CETP Societies and also make things functional better, necessary authority be vested with the management of CETP Societies so as to such situation does not arise. Hope DPCC will use its good office to facilitate this.

Vacuum filter (both), flush mixture (2 nos) were not in operation since last few days.

· As  the influent is only 3 MLD , we operate only vacuum filter at a time, other standby is in working condition. We operate only two units (flesh mixer) at a time, other are kept as standby.

As per DPCC analysis report, dt 09-04-07, TDS (4087) was not meeting the prescribed standards. 
· There is no provision of reducing TDS. It was pointed out in the meeting by NEERI as well CPCB that the Total Dissolved Solids in treated effluent from most of CETPs are high and not able to meet the TDS standard.

· CPCB and EPCA have also agreed to keep the fixing of standard of TDS at abeyance or to raise the standard to achievable value.

· Regarding value of BOD as 36 mg/I at the outlet on 13.9.2007 monitoring, it may be due to shock load from Domestic Waste Water entering CETP along with trade effluent.

Bank Guarantee
· The correction of deficiencies are being very seriously looked into for 100% service, whereas deficiencies due to design fault, lack of appropriate hardware / technology or lack of authority as vested with CETP Societies under direction with the Appropriate Authority, we would therefore very strongly recommend your intervention for setting write the thing instead of passing balance to the CETP Societies and irrelevantly imposing Bank Guarantee of Rs 10 lacs, for which we request to withdraw the condition for submission of Bank Guarantee as we are committed to operated  maintain CETP.

Inspection status:

Observation during inspection of CETP on 05.12.07 along with CPCB during training program is as follows:

Flow meter at inlet out of order & sent for repair as per documents shown.

Equalization tank found filled with significant quantity of silt/ sludge.

Conveyance system for WIA is yet to be completed.

No flow meter installed at outlet of CETP.

Vacuum filter & flash mixer found in operation.
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One tube settler is under cleaning.

Pressure gauges attached to ACFs & DMFs are found functional.

Average intake during month of Nov. 07 – 1.93 MLD.
Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Since the unit appears to have corrected some of the deficiencies, a fresh inspection may be done and report be submitted in next CMC (MSW) meeting. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 
Decision of Consent Management Committee in its 35th meeting of CMC (orange) dated 14.01.2008 :

On closed inspection of the file, in view of the representation made by the Wazirpur Industrial Association to Hon’ble CM 10.01.08 reveal that two out of the three deficiencies have been corrected. Since the CETP society is amending its ways, the committee felt that the Bank Guarantee of Rs. 3 Lakhs for a period of six moths may be taken from the society within one month in order to ensure that it corrects these three deficiencies consistently. 

Action Taken Report
As decided by CMC on 14.01.2008, Letter  issued on 12.02.2008 for seeking Bank Guarantee & affidavit. No reply received. 
Inspection status:

Observation during inspection of CETP on 22.01.2008 is as follows:

· New flow meter installs but found non operational.

· Equalization tank found filled with significant silt/sludge.

· No flow meter installed at out let of CETP.

· Pressure gauges attached to ACF & DMF found operational.

· pH at inlet (raw effluent sump) at CETP was 1- 1.5. 

· Vacuum pump, filter & flash mixer found operational 

· Total intake during month of Dec 07 was 57.65 ML at average of 1.85 MLD.

· CETP society is adding dosing of NaOH in the raw effluent sump to make pH about 3 before sanding effluent to grit chamber of CETP.
· Hazardous Waste/ sludge found stored in two sheds and in sludge holding tank. One new shed is under construction.
DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	pH- 1.8           Cr-24.64
	TDS-4940
	pH- 1.2         TSS- 468       Ni-4.1           Cu-6.6          Cr-24.0
	TDS-2790
	pH- 2.6         Ni-3.6           Cr-28.0   Cr+6- 2.8
	_
	pH- 2.6         Ni-3.2           Cr-12.44
	TDS-2501


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

4. Letter be issued to CETP to submit an affidavit, as to why TDS is exceeding at the outlet of CETP and parameters at inlet are fluctuating as per water analysis report. 

5. All deficiencies of 22 Jan 08 may be corrected by CETP within 1 month.

6. Individual connections to conveyance system must be ensured for all individual polluting units.
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Action Taken Report
Letter issued on   24.03.2008.  Reply to the notice dated 24.03.2008 not received so far.

A letter has been received from DSIIDC on 03.04.2008 regarding non functioning of pumps at Wazirpur Industrial Area due to low pH. As approved, Directions u/s 33 (A) of Water Act was issued to Wazirpur CETP Society on 15.04.2008 to ensure that all the members of CETP Society shall treat their trade effluent so as to meet the prescribed norms of parameter pH of 5.5 before discharging into the conveyance system to enable the operation of CETP, Wazirpur.

The society has submitted the reply to the directions u/s33(A) of Water Act on 15-04-2008 wherein it is mentioned that notice has been circulated to all the water polluting units/pickling units in the area and send another reminder to them on 28-4-2008, but there is no response from the units and there is no improvement in the pH at the inlet of CETP and requested to suggest as to how to get the needful done. The society has also submitted the list of the 201 water polluting units(150{pickling}, 12{Dyeing},14{Electroplating},9{Service Station} and 16{other category})

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	pH- 1.7       TSS- 260    Ni-3.6           Cr-30   Cr+6- 2.5
	TDS-4150
	Non operational
	Non operational


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
Dr.S. K. Gupta, Prof IIT has agreed to send one Associate Professor who will be provided transport and other facilities by DPCC to check the CETP plant and he will suggest  how TDS can be reduced substantially. 
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Jhilmil & Friends Colony Indl Area CETP ( 16.8 MLD)
Consent status of CETP

Consent to operate issued on 28.02.07 to CETP society for period of three years and valid up 07.01.2010.

Decision of Committee taken on 19.10.2007

Directions issued after Inspection on 16.4.07 have been responded by the society. However, the inspection of 11.7.07 still found certain deficiencies which should be communicated to the society by the SCN u/s 33 of Water Act. While the July and Aug. monitoring reports showed certain norms not in compliance, the September report finds the CETP functioning with in the norms. 

It was also found that against the installed capacity of 16.8 MLD, the CETP Society is operating it at only 5.0 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The Society may be asked to be cautious and correct all deficiencies by 31.12.07 and submit an affidavit, failing which a BG of Rs. 5 lakh may be imposed on the society.  

The copy should be sent to MD (DSIDC) and Comm. of Industries.  
Deficiencies mentioned in SCN issued & brief of its reply by CETP Society :

Both equalization tanks were found filled with significant quantity of  silt/sludge.

· Cleaning of the equalization tanks, two equalization tanks, each will take at least one month one month or so, as was done in 2006 after monsoon’s.

No settling was observed in grid chamber.

· Grit chamber is in operation as per design/ construction, done by DSIIDC and is regularly cleaned.

Large quantity of oil and grease was observed in both equalization tanks.

· Door to door notices were sent to individuals factories to operate their ETPs. In fitness of things DPCC can help us by ding surprise checks, rather than penalizing the society, who have their own limitations.

1 vacuum filter found was found non operational.

· Both vacuum pumps are in operation on alternate basis.

3 no receiving pumps (out of 6) were found under repair.

· Presently all the six receiving pumps are in operation.

Flow observed to be in the range of 1.5- 3.5 MLD against installed capacity of 16.8 MLD.

Individual connections with conveyance system

Notices for individual connections to conveyance system have already been sent & most of members have connected to conveyance system. For defaulters action to be taken by DJB/ DPCC. However we have again sent the reminders. Requested to help for enhancing the inflow by directing the nearby Patparganj Indl. Area & other area (Dilshad Garden/ Shahdara North Area) to bring effluent to Jhilmil CETP.        
As per DPCC analysis report some parameters  are not meeting the norms laid down.
· Regarding some of the parameters viz. TDS, Cl, CU, Cr, it was decided by EPCA to maintained only four parameters by CETP’s . Only on this ground the handing/ taken over of CETPs were done by the society and the society agreed to maintained parameters as maintained by DSIDC at that time. 
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· To Submit list of employees working at CETP.

· Some of the deficiencies which are practically possible for the society to remove have been started immediately.

Inspection status:

Observation during inspection of CETP on 19.12.07 is as follows:

Equalization tank are found filled with significant quantity of  silt/sludge.

Silt removed from grit chamber found lying near grit chamber on katcha floor in open for drying and as informed, after drying it will sore in shed.

Both vacuum filters found in operational condition.

No flow meter at outlet of CETP

Sludge thickner pump repairing work going on during inspection.

Average intake effluent during month of Nov. 07 –  4.54 MLD.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Since the unit appears to have corrected some of the deficiencies, a fresh inspection may be done and report be submitted in next CMC (MSW) meeting. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 

Action Taken Report
Letter issued on 25.01.08. CETP society has submitted letter on 12.02.08 informing that cleaning of silt in tanks is in progress, gird chambers are regularly cleaned, vacuum pumps and filters are in working condition.
Inspection status:

Observation during inspection of CETP on 18.01.2008 is as follows:

· One equalization tank is not in use, as kept for desilting of tank by using sludge pump.

· One vacuum filter & one vacuum pump were out of order. 

· Sludge thickener pumps (both) found out of order.

· effluent during month of Dec 07 was 108.35 ML (average-3.5 MCD)

· Flow meter of inlet found operational.
DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	_
	BOD-34       Cl-1880       TDS-3290
	TSS-684
	TDS-2250
	TSS-472      Cu-5.2              Cr-2.3
	_
	TSS-468        Cr-3.6
	BOD- 34          TDS-2867


Letter received from CETP society on 26-2-08 stating that in EPCA meeting it was decided that the TDS and Cl. Parameters will not be taken into account as these are the origin  of the groundwater.
· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Letter to be issued to CETP to submit an affidavit as to why the parameters are fluctuating as per water analysis report. Apart from this they will also submit the minutes of EPCA wherein it is decided that the parameters of TDS and Chloride will not be taken into account. Deficiencies of the inspection report of 18 Jan 08 should be corrected by the CETP within 1 month.

Action Taken Report
Letter issued on 24.03.2008.

CETP society has submitted reply on 17.04.08 and brief is under:

11. The DPCC analysis report indicate that some inlet parameters are not within the prescribed standards. In this connection it is highlighted that the individual ETP’s in the industrial area which discharge effluents into the sewer are being monitored by DPCC 
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12. The CETP society has a limited role and no teeth to control the individual ETP’s which are under the direct control of DPCC.

13. As regard the removal of CL and TDS at the outlet it is directed that the ground water being used in the industrial process is very heavily loaded with Cl- and TDS. DPCC while accepting the feasibility report of NEERI in the preliminary design technology has taken care of this fact and the CETP’s were designed under the direct/ indirect supervision of DPCC.

14. The CETP society are using the technology that was approved by DPCC and constructed by DSIIDC. The Society is controlling and maintaining the parameters as were done by DSIDC, before handing over.The society submitted the copy of agreement made for operation and maintenance of CETP.

15. The vacuum filter and vacuum pump were under maintenance and have been repaired.

16. Sludge thickener pump were out of order, but augmented with separate submersible pump. The necessary steps have been taken in this regard and the deficiencies have been removed. 

17. If DPCC has any objection on shutdown of equipment for maintenance, the society will  not carry out maintenance work and further consequence will be on DPCC.

18. The Minutes of meeting of EPCA can be obtained from the EPCA secretariat at CPCB.

19. The condition of submitting an affidavit in regard that parameters are fluctuating, is rejected with strong force on solid grounds that the requirement of an affidavit is not warranted in any of the environment, water or air act. DPCC is not a court for which an evidence is be recorded by an affidavit and technically a huge plant like CETP is going to have fluctuations in the inlet and out let parameters and a future fiction cannot be translated in present confirmation.

20. In the light of above mentioned facts and all surrounding factors, DPCC has to provide the guidance for removal of Cl and TDS within the economic means of the society and in case DPCC feels that the society has failed to carry out the responsibility it can take over the plant and run on its own to maintain Cl and TDS parameters.

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-340
	TDS-2810
	Cu-4.5
	BOD-32       Cl-1220       TDS-3060


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
DPCC is the regulatory body and under the Water Act. DPCC has full power to ask for any information to be authenticated through an affidavit. Society must therefore file an affidavit by 30.06.2008, without fail. 
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai
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    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

DSIDC Nangloi Indl Area CETP ( 12 MLD)
Consent status of CETP

Consent application for consent to operate was submitted by the CETP Society on 27.06.2007. 

Decision of Committee taken on 19.10.2007

The deficiencies noted in the inspection of 18.7.07 may be communicated to the unit and time given up to 31.12.07 to correct the deficiencies. The latest inspection of sept. indicates that TDS parameters not meeting the  norms.

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 1.0 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the   connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

 The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The society will submit a Bank Guarantee of Rs. Two Lakhs Fifty Thousands (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done by 31.12.2007. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.  
Deficiencies mentioned in SCN issued & brief of its reply by CETP Society :

Flow at the inlet observed is very low (in the range of 2.75 MLD) against the installed capacity of 12 MLD.
· The DPCC very well knows that the CETP Nangloi has been designed over capacity by NEERI.

Pressure gauges attached to DMF & ACF were found in non operational condition.
· It hardly matters whether pressure gauges are operational or not till the designed standards are beings met. Still however as the plant is under 3 year warranty, the DPCC should have caught hold of DSIIDC/L&T to get the same replaced . 

Flow meter at outlet of CETP found non operational.
· It is well understood that the same quantity of effluent comes to the plant which would be treated before discharging and as such there should not be any objection in this matter.

As per DPCC analysis report dt 13.04.2007, BOD (42), Cl (2050) & TDS (4697) are exceeding the norms laid down.
· BOD level was marginally increased from the permissible range in that period but the same has been brought under control.

· We were handed over the plant in Oct, 05, wherein before the Bhure Lal Committee also, we were told that TDS can not be maintained as it depends on the quality of incoming water in the plant. TDS was never within the permissible range.

Bank Guarantee
· As such you would please appreciate that issuing Show Cause Notice and asking for a Bank Guarantee when the Society is already meeting its obligation is uncalled for and require immediate withdrawal. Request you to kindly issues the Consent to Operate at the earliest.
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Inspection status:

Observation during inspection of CETP on 19.12.07 is as follows:

Flow meter at inlet found in operation.

Pressure gauges attached to DMF & ACFs found out of order.

Flow meter at outlet found non functional.

Average intake during month of Nov. 07- 1.8 MLD

One oil & grease screamer at grit chamber found under maintenance.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Since the unit appears to have corrected some of the deficiencies, a fresh inspection may be done and report be submitted in next CMC (MSW) meeting. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 

Action Taken Report
 Letter issued on 28.01.2008.

Inspection status:

Observation during inspection of CETP on 21.01.2008 is as follows:

· CETP found in operation

· Pressure gauges of DMF & ACF found replaced/ repaired & found operational (4 DMF & 3 ACF are in operational).
· Oil & grease screamer of grit chamber repaired & found operational.
· Flow meter at inlet found operational 
· Total intake of effluent during Dec. 07 was 48.2 ML.
· Filter pump & filter found operational.
DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	TSS-460
	BOD-33          TDS-2070
	TSS-460
	TDS-2510
	TSS - 460
	BOD-25      Cl-1700   TDS-3210
	TSS-364
	BOD- 33          TDS-3172


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Letter to be issued to CETP to submit an affidavit as to why the parameters are not meeting the prescribed limit. 

Action Taken Report
Letter issued on 19.03.2008. society has submitted reply & stated as under:

8. The above plant was constructed under your guidance and expert opinion. The construction was carried out by L&T through DSIDC.

9. Every now and then it is observed that the BOD level of the effluents discharge goes up and we are not able to find out any equipment installed in the aforesaid plant to control the BOD at the desired limit. You are therefore requested to kindly guide us as to how the BOD level should be controlled within the permissible limits.
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10. If for any reason, any plant or machinery or part thereof  has not been installed in the plant please let us know the detail specifications for further action in the matter.

11. Our Operating Agency M/s Om Bio Chem System Pvt. Ltd., had submitted an affidavit duly Notarized, that there are no equipment/ any mechanism in the plant to control the BOD at the desired limit.

12. Some parameters were eliminated from pollution control Law Series: PCLS/4/2000-2001. TDS (Total Dissolved Solids) and Cl-No limit defined. [Limit defined in EPA for CETP Inlet and outlet]

13. The TDS & CL are increased in ground water i.e. because of non availability of sufficient surface water. The BOD level is increased some of our sample i.e. because of non availability of sufficient power supply.

14. We here by under take on behalf of DSIDC & UN CETP Society, we are operating & maintaining the above said plant as per designed efficiency of plant.
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-340
	TDS-2840
	TSS-484
	BOD-35  


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
In view of the parameter TDS & Cl are not meeting the prescribed standard at the outlet of CETP, as per monitoring conducted by DPCC laboratory in month of April, 2008, Bank Guarantee is reduced from Rs. 2.5 Lakh to Rs. One Lakh and confirmed to be submitted by 30.06.2008 by CETP Society.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
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   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

SMA Indl Area CETP ( 12 MLD)
Consent status of CETP

Consent to operate issued on 15.09.04 to DSIDC for period of three year and valid up 27.07.07. CETP society submitted application for consent to operate on 11.04.07.

Decision of Committee taken on 19.10.2007

The unit was inspected on 19.7.07 and gross deficiencies were found. Also the sept. report show TDS in excess of the norms . 

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 1.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The society will submit a Bank Guarantee of Rs. Five Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done by 31.12.2007. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.  
Deficiencies mentioned in SCN issued & brief of its reply by CETP Society :

Equalization tank was found filled with significant quantity of silt/sludge.

· DSIIDC At the time of handing over the plant at submitting undertaking to desilting the plant. 

Sludge kept in open. The existing storage facility was completely full. 

The sludge which is generated from the process is not being stored as per the guide lines of storage of Hazardous Waste Rules. At present it is being dumped in open raw land. 

· DSIIDC at the time of handing over the plant at submitting undertaking to create a new sludge house which is still pending. However initiative of the society for new sludge house is being created.

The existing conveyance system to CETP still choked. Due to that total quantity of Waste Water is not being coming / being received in CETP. 

· The conveyance system of CETP is maintained by DJB and it is working properly.

No flow meter installed at outlet of CETP. 

· This was decided in a meeting with EPCA that the flow meter will be installed by DPCC.

As per DPCC analysis report dt 10-04-07, BOD (38), Chlorides (2120) and TDS (3904) are not within the prescribed norms. 
· In this regard (TDS,CI) the CETP members are being perused not to use ground water for processing. Efforts have been made to control BOD.

During the inspection CETP was not in operation since last few days. 

During inspection it was observed that waste water is being thrown out side of the premises on public land along with silt / sludge. Due to that a pond has become in existence near railway line. 

CETP was under maintenance during the inspection and maintenance was being done by DSIIDC. Therefore it is the responsibility of DSIIDC.
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Individual connections with conveyance system

· We have made all sewer connections to the main conveyance system and letter from the DJB to this effect is being obtained very shortly.

Bank Guarantee
· In the background of clarifications & facts at site, we fail to understand that instead of empowering CETP Society and cooperating/ helping in removing deficiencies in the CETP hardware/ technology provided, DPCC is imposing a bank guarantee. We pray that if the Committee is not satisfied with our reply, a personal hearing may be given. Consent to operate to our CETP Society must be given, otherwise we presume that running of CETP is an offence.

Inspection status:

Observation during inspection of CETP on 27.11.2007 is as follows:

Equalization tank was found filled with significant quantity of silt/sludge.

Sludge kept in open. Work of construction of shed is going on & as reported work will be completed in 15 days.

No flow meter installed at outlet of CETP. 

Sludge dewatering system not in operational condition.

Pressure gauges for DMFs & ACFs are not in working condition (except 2 nos)

Display board wrt HW rules is not updated.

Average intake quantity of effluent during month of Oct. 07 – 1.26 MLD.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Since the unit appears to have corrected some of the deficiencies, a fresh inspection may be done and report be submitted in next CMC (MSW) meeting. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 

Action Taken Report
Letter issued on  28.01.08.

Inspection status:

Observation during inspection of CETP on 21.01.2008 is as follows:

- Equalization tank (both) found filled with significant quantity of silt/sludge. Agitators (both) are non operational due to silt. 

     - One equalization tank inlet stopped/ closed. As reported, society now starts work of                

        cleaning of tank for which it will be dried/closed & then sludge will remove. This work will take approx two months.

     - Pressure gauges of 2 DMF & 1 ACF not in working condition.

     - Sludge kept in sheds, however construction of 2nd shed is also going on.

     - Flow meter at inlet found operational. 

     - One sludge vacuum pump & filter found operational & 2nd in non operational condition.
     - No flow meter installed at outlet of CETP.

     - Total intake during Dec 07 was 48.6 MLD

     DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	TSS- 668                         Cr-4.24
	TDS-3290
	pH- 2.9         TSS- 620       Ni-4.0                     Cr-3.1
	TSS-112       BOD-34      Cl-1100   TDS-2990
	Ni- 3.1        C - 2.4
	BOD- 34          TDS-3666
	NIL
	TDS-2501
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· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Letter be issued to CETP to submit an affidavit, as to why TDS is exceeding at the outlet of CETP and parameters at inlet are fluctuating as per water analysis report. Deficiencies of inspection Report of 21 Jan 08 may be corrected by CETP within 1 month.

Action Taken Report
Letter issued on 24.03.2008.

The society submitted the reply on 23-4-2008 wherein it is stated that the individual ETPs are bring monitored by DPCC inspectors regularly and the inlet parameters fluctuates due to the effluent discharge through ETPs. The CETP society has a limited role and no teeth to control the individual ETPs which are under the direct control of DPCC.

Regarding TDS-ground water of industrial areas is heavily loaded with TDS, DPCC while accepting the feasibility report of NEERI has taken care of this fact and CETPs were designed under/indirect supervision of DPCC.Society is using the technology that was approved by DPCC and constructed by DSIDC.

Regarding deficiencies, the withdrawal of silt from equalization tank was one of the condition of taking over the plant by the society from DSIDC, DSIDC has not fulfilled the condition till date.Silt exclusion will be taken of by the society in the dry season by drying the silt. Agitators are not operational due to silt to safeguard the machinery and to prevent choking of the tube settler.Now the pressure gauges are fully functional. Vacuum pump and filter is under repair and is ready for use now.

The condition of submitting an affidavit in regard that parameters are fluctuating is not agreeable because the requirement of affidavit is not warranted on any of the Environment, Water or Air Act, Affidavit is a mean of recordings of evidence which can not be done for any future unpredictable event which is beyond any body’s control. 

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-380       Ni-3.2                     Cu-5.3     Cr-2.1
	TDS-2100
	TSS- 660       Ni-4.45                     Cu-6.9     Cr-3.2
	TDS-2872


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
In view of the parameter BOD & TDS are not meeting the prescribed standard at the outlet of CETP, as per monitoring conducted by DPCC laboratory in month of April, 2008, Bank Guarantee is reduced from Rs. 5 Lakh to Rs. One Lakh and confirmed to be submitted by 30.06.2008 by CETP Society.

The Society shall remove the silt from equalization tanks (one by one) & other deficiencies within a period of one month and confirm. 
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
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    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

GTK Road Indl Area CETP ( 6 MLD)
Consent status of CETP

 CETP Society has not applied for Consent to operate so far. 

A DO letter was issued on 17.07.07 to MD, DSIDC with a copy to Commissioner of Industries & President, CETP Society asking to apply for consent to operate within a month and remove the deficiencies observed. No reply received from CETP society and Commissioner of Industries regarding rectification of deficiencies. However, DSIDC has submitted a letter dated 03.08.2007 stating that the CETP has already been transferred under the CETP Act to CETP Society.
Decision of Committee taken on 19.10.2007

The unit was inspected on 19.7.07 and gross deficiencies were found. Also the Sept. report show TDS in excess of the norms . 

CETP society is also directed to submit application for Consent to Operate immediately.

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 2.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

 The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The society will submit a Bank Guarantee of Rs. Five Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done by 31.12.2007. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.  
Deficiencies mentioned in SCN issued & brief of its reply by CETP Society :

Flow at the inlet observed is very low (in the range of 2- 2.5 MLD) against the installed capacity of 6 MLD.

· We are surprised why you are writing to us as neither we are a party to construct nor to design. This is only a performance of DSIDC. How DPCC is concerned to such, this in neither to the purpose nor to the jurisdiction of DPCC.

Pressure gauges attached to DMF & ACF were found in non operational condition.
· From the day one, DSIDC provide the same as such & never support us. Further this is the question beyond the jurisdiction of DPCC as DPCC is suppose to check the quality of treated water and not the system.

The flow meter installed in the inlet of CETP was found out of order.

· From the day one , the meter is out of order. DSIDC always operated the system without any flow meter, which was never objected by you to DSIDC.

One floating aerator of equalization tank found out of order.

· DPCC team is very efficient only for inspections but is never concerned to support the society for joint inspections. However the floating aerators was repaired promptly as it is a routine wear & tear of the equipments and is maintained on regular basis.
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Sludge kept in open.

· This is unusual and un-imaginable that DPCC is concerned to such thing. Could you be kind to inform us where the sludge to be kept in & disposed off. We have no words to write on this issue as DPCC failed to provide ant site or support to us till date in spite our repeated submissions.

Poly tech as treatment chemical, is being used in place of Alum.

· DSIDC has permitted the use of polytech in place of Alum. DPCC should explain why such use of polytech is objectionable.

No flow meter installed at the outlet of CETP.

· In EPCA meeting, DPCC was announced that flow meter at outlet shall be supplied free of charge by DPCC to DSIDC as DSIDC was short of funds on this projects.

As per DPCC analysis report dt 10-04-07 TDS (2501) is not as per  prescribed norms. 
· Since the design of the plant are bad and can not perform to produce treated water as per EPA norms, it was decided during EPCA meeting and before DPCC officials that CPCB permits and exempted any limits of TDS otherwise we request DPCC to support us with their valued guidance how to deal with situation on the existing system.

Not applied for consent to operate under Air & Water Act
· Last consent obtained by DSIDC was conditional and no condition were ever fulfilled by DSIDC and plant was operated by DSIDC in complete connivance of DPCC. DSIDC should complete such conditions and apply for the same.

Individual connections with conveyance system

· This is the job of DJB. However society is ready to do the same, if inspectors are provided to us and also we should be authorized to issue consent to establish & operate to our members units jointly with your office.

Bank Guarantee 

· We will appreciate if you guide us how a society could be responsible to work for the jobs fixed for others agencies and you are initiating penalty proceedings under Delhi CETP Acts. Therefore, your demand for Bank Guarantee of Rs. Five Lacks is not only ultra virus but is no basis or with any jurisdiction. However we request you to support the society by joining us to issue permission to establish and to operate to our members units for a better coordination of members and control of quality  of water at inlet of CETP.  

Inspection status:

Observation during inspection of CETP on 18.12.07 is as follows:

The flow meter installed in the inlet of CETP was found out of order.

Pressure gauges attached to DMF & ACF are out of order & non functional condition.
Both aeration tanks are in use & motors of two aerators found removed. As reported, one motor was sent for repairing about 3-4 months back.

Sludge firstly kept in open & after drying (7-10 days) it will store in shed.

One vacuum filter is non functional condition.

Average intake in Nov. 07 – 2.1 MLD.
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Decision of Consent Management Committee in its meeting dated 09.01.2008 :

A fresh inspection may be conduced and put up in next CMC. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected after inspection is to be done in the month of January, 2008. A letter may be issued to CETP Society regarding final view of Bank Guarantee.

Action Taken Report
Letter issued on 28.01.08.

Inspection status:

Observation during inspection of CETP on 07.02.2008 is as follows:

· Flow meter installed at inlet found out of order.

· Pressure gauges attached with ACFs & DMFs were found out of order & non functional condition.

· Two floating aerators (out of four) found non operational, motors of both orators (one in each tank) found removed.

· One vacuum filter found in non operational condition as filter cloth & cabinet found torned.

· Both waste water pumps installed (for lifting of waste water from thickener to equalization tank) found out of order. A sludge pump found installed as temporarily arrangement with loose pipes. 

· Total quantity effluent intake in month of Jan 08-48.41ML (Av-1.62MLD). Month of Dec08-63.65ML (Av-2.05MLD). 

DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	pH- 3.2         TSS- 482             Cu-3.6          
	BOD- 36          TDS-2990
	TSS-740
	NIL
	TSS-820              Cr-2.5
	_
	TSS-484        Cr-2.42
	_


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Letter to be issued to submit an affidavit as to why parameters are not meeting the prescribed limit. Deficiencies of inspection Report of 7 Feb 08 may be corrected by CETP within 1 month.

Action Taken Report
Letter issued on 25.03.2008. The society has submitted the reply on 16-4-2008 and stated as under :

The installed plant has no such mechanism to control the TDS and moreover the TDS of the ground water is very high so to maintain. TDS standard there is need to introduce new technology to the present system. Hence, to control the TDS standard it is beyond the control of the society due to non-effective system.

The flow meter is non- functional since its installation and have some manufacturing defect and no details of its warranty, guarantee or service centre has been provided by DSIDC till date.
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The Pressure gauges  attached to the ACF’s and DMF’s are non-functional since the trial run and have technically defective and cannot be made functional all the time. Moreover, it does not play an important role on treatment of the effluent.

The floating aerators- The plant is mechanically and electrically driven and at any point of time the fault may cause and the same is rectified without unreasonable delay.

One Vacuum Filter- There are two vacuum filters and at a time one remains functional and other is standby. Moreover, one of the vacuum filter was non-functional at the time of handing over and was repaired by the team of the society but it is only non-functioning only due to non-availability of the PVC cabinets fitted over the drum.

Waste Water Pumps- The waste water pumps got choked and stopped working due to the high depth & thick sludge in the waste water sump, so the pumps installed in the sump could not be repaired. The efforts and the steps taken by the society by installing an extra new pump should be appreciated and can not be listed under deficiency. 
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-640
	_
	TSS-412              Cr-2.7
	BOD-32  


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action.
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Lawrence Road CETP (12 MLD)

Consent status of CETP

· Consent to operate expired on 27-07-07. Applied for renewal of consent on 14.12.2007. 

Decision of Committee taken on 19.10.2007

Inspection of 12.7.07 gross deficiencies which have not been rectified the lab reports indicate several norms be flouted. 

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 2.0 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The society will submit a Bank Guarantee of Rs. Five Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done by 31.12.2007. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.  
Deficiencies mentioned in SCN issued & brief of its reply by CETP Society :

Flow observed to be in the range of 1- 1.75 MLD against installed capacity of 12 MLD.

· DSIIDC is not responsible for making individual connection by the industries to the main conveyance system leading to the CETP and has no statutory powers to issue any notice in this regard to individual industry for making the required connection. CETP Society has been advised by us for the same.

No flow meter is installed at outlet of CETP. 

· As per NEERI scheme vetted by DPCC & approved by Hon’ble Supreme Court, only one flow meter was required to be installed which has been installed by DSIIDC. In EPCA, DPCC was agreed to install the flow meter at the outlet of CETP on its own.. It is further stated that technically one flow meter is sufficient to measure the treated flow. 
One vacuum filter (out of 2) found in non operational condition.

· Since, the plant is receiving less quantity of effluent, only one vacuum filter is operated on rotational basis.

2 ACFs out of 6 nos. and 3 DMFs out of 9 nos. were found operational during the inspection.

· All the DMF & ACF are in operational condition and these are being used on rotational basis.

Small quantity of effluent going out of the premises, which is emanating from Grit Chamber, with out any treatment.

· Regarding the leak of effluent from grit chamber necessary action is being taken & the same shall be stopped soon. 
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Dosing of Bleaching powder not being carried out. Pre chlorination as well as post chlorination were found non operational.

· Pre chlorination shall be started soon. However, Post-chlorination is not done as the treated effluent is being put into drain.
· CETP doesn’t have any facility to treat the excessive BOD as it is Physico-Chemical Treatment Plant. Necessary consultation with the experts is being taken together with other treatment options by DSIIDC.

Bank Guarantee

· Submission of Bank Guarantee of Rs. 5 Lacs may please be waived off as DSIIDC is a responsible Govt. Undertaking and not a CETP Society.

Inspection status:

Observation during inspection of CETP on 18.12.07 is as follows:

The flow meter installed in the inlet of CETP was found out of order.

Vacuum filters both found operational condition.

Dosing of bleaching started from 11.12.07 for pre-chlorination

Presently 3 DMF & 2 ACFs are in use. As reported DEMF & ACFs are use on rotational basis as per the intake quantity. 

Pressure gauges attached to DMF & ACF are out of order.
As reported work of grit chamber leakage will be started within a week.

Average intake in Nov. 07 – 1.34 MLD.

High BOD Level at CETP, Lawrence Road

A meeting was taken by Chief Secretary on 29.08.2007 regarding the operation of Lawrence Road CETP. Follow up action taken was discussed in the meeting taken by Secretary (Env.) on 07.09.2007 and accordingly DO letters were issued to MD, DSIIDC on 26.09.2007. A detailed survey of the area was also conducted by SEE. A letter is received from Chief Engineer, DJB stating that the sewage of domestic area is not connected with sewage system for Lawrence Road Indl. Area. Cases of 30 unit of LRIA were discussed in the CMC (Orange) in its meeting held on 12.10.2007. As an immediate measure, at least septic tank may be installed for two Sulabh Shochalas establishments for reducing of BOD level by MCD, a letter was issued to the Commissioner of Industries on 26.12.2007 for taking up this matter with Slum Deptt., MCD under the CETP Act, 2000.

DSIIDC has submitted a letter on 05.12.07 regarding augmentation of CETP at LRIA for treatment of excessive BOD and submitted that DPCC conducted a detailed stud of the process and after which it was conveyed that the existing aeration system may be upgraded or diffuser system may be installed in the Equalization tank for treatment of BOD. The matter was referred to some consultants. DSIIDC have received the reaction from NEERI who have expressed their apprehension with the above suggestion which may not be a workable solution for this problem and instead has suggested BOD treatment though sequentional batch reactors. Matter is be examined for estimation & execution from other experts and waiting for reaction of other consultants.  

A letter has also been received from CETP Society of the area on 24.12.2007 stating that DSIIDC is considering  to modify some physical changes in the design of the plant and requesting to take the Society into confidence & provide full details of the change in process or modifications of the plant. 
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Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Certain deficiencies in the noted in the earlier inspection was communicated to DSIDC. DSIDC in its reply has stated that they have corrected the deficiencies mentioned. An another inspection of CETP was done on 03.01.2008 and following deficiencies were noted:-

The flow meter installed in the inlet of CETP was found out of order.

Pressure gauges attached to DMF & ACF are out of order.
As reported work of grit chamber leakage will be started within a week.

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during last two months are as under:
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet

	Non operational
	Non operational
	_
	BOD- 36,          TDS-2257


A letter from Member Secretary, DPCC may be issued to GM, DSIIDC for correction of deficiencies. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected. 

Action Taken Report
Letter issued on 25.01.08. However, no reply has been received.
DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	_
	BOD-33        Cl-1280          TDS-4150
	TSS-384
	TSS-108      BOD-54    TDS-3250       Sulphide-3.6
	Non operational
	Non operational
	NIL
	BOD- 36          TDS-2257


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Letter to be issued to submit an affidavit as to why parameters are not meeting the prescribed limit with a copy to the  Chairman & MD, DSIIDC. Deficiencies noted in inspection of 03 Jan 08 to be corrected by the CETP within 1 month.

Action Taken Report
Letter issued on 27.03.2008. DSIDC has submitted the reply on 29-4-2008 and stated as under 

Now the reading of the flow meter has been reset and the flow meter is working.

The defective pressure gauges have been got rectified and now all the pressure gauges of AOF & DMF are working. The pump has been installed below the Grit Chamber to take care of leakage of effluent of Grit Chamber.

DPCC awarded the work of designing CETPs in the N. C. T. of Delhi to NEERI and it was DPCC which approved the designed  parameter of the influent reaching to CETP recommended by NEERI including the influent parameter of CETP Lawrence Road DSIIDC took up the construction work of CETPs on the basis of design of NEERI which was duly approved by DPCC.

This issue of BOD has been discussed in various meetings of EPCA, Secretary  (Env.) & Chief Secretary but could not be resolved in spite of efforts put by DSIIDC. DPCC is requested to look into the options came out during these meetings made by various officials time-to-time.
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As the issue of high BOD pertains to DPCC there is no need of filing and affidavit by DSIIDC. Moreover, DSIIDC has no statutory powers as per law for issuing any direction to industries for controlling  BOD.DSIDC also requested that DPCC shall take necessary action to resolve the problem of high BOD so that the plant will be handed over to respective CETP society.

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-380
	BOD-52        Cl-1180          TDS-2310
	Non operational
	Non operational


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
In view of the parameter BOD, Cl & TDS are not meeting the prescribed standard at the outlet of CETP, as per monitoring conducted by DPCC laboratory in month of March & parameter i.e. BOD & TDS not meeting in April, 2008, Bank Guarantee is reduced from Rs. 5 Lakh to Rs. One Lakh and confirmed to be submitted by 30.06.2008 by CETP Society.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

OKHLA CETP  (24 MLD)

Consent status of CETP

· CETP Society submitted the consent application for renewal of  consent on 13-02-07.

Decision of Committee taken on 19.10.2007

The deficiencies found on inspection on 11.4.07 have not been rectified in full. The deficiencies noted on 23.7.07 may be communicated to the society. The lab report show BOD, TDS above the norms 

It was also found that against the installed capacity of 24 MLD, the CETP Society is operating it at only 3.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The society will submit a Bank Guarantee of Rs. Ten Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done by 31.12.2007. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.

Action Taken Report
As decided by the CMC , SCN was issued on 05.11.2007 and CETP Society has submitted its reply on 30.11.2007. Case of the CETP was taken up by the CMC in its meeting held on 13.12.2007.

Decision of Committee taken on 13.12.2007

CMC in its meeting on 09.10.2007 had noted certain deficiencies in the functioning of the CETP and had ordered correction of those deficiencies along with the Bank Guarantee of Rs. 10 lakh. After that, a meeting was sought by all the CETPs Societies with Chairman & Member Secretary, DPCC to air their grievances and to seek redressal. After hearing patiently and acquainting them with the need for running the CETPs efficiently and effectively, Chairman, and Member Secretary, DPCC had agreed that the case of Bank Guarantee may be reviewed if they substantially comply with the correction of deficiencies noted by CMC. In their letter received on 30.11.2007 they have informed in writing but not through an affidavit, that they have corrected the following deficiencies:-

(iv) The defective aerator has been repaired.

(v) Recorder of inlet flow meter has been repaired and now functional.

(vi) Equalization tank was under cleaning process when inspection team visited the CETP.

However, the following deficiencies are yet to be corrected for which they have given the following justification:-

Pressure gauge  

The suppliers of pressure gauge were contacted by the Society and they are of the view that pressure created in the pipe is too weak to operate the pressure gauge. Pressure gauges in ACF have not been fitted even by DSIDC. 

However, the view of the concerned CMC (MSW) is that the quantity of effluent received at CETP i.e. 2.0 to 2.5 MLD of waste water against the installed capacity of 24 MLD does not make any effect on the pressure.
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Flow meter at outlet

Regarding flow meter at outlet, in EPCA meeting it was decided that DPCC  will get it installed and cost will be borne by them. 

TDS

This plant has not been designed to treat TDS, so Society can hardly do anything on the subject. However, Prof. Gutpa, IIT feels that the plant has been designed by the NEERI for reduction of TDS which is evident from the flow chart given at figure 3.29 & 3.30 in the Phase-II report, volume –II of design of common effluent treatment plants for industrial estates in the NCT of Delhi, which shows that TDS of 234 mg/l has been reduced to 128 mg/l. 

Individual connection with conveyance system

CETP has issued public notice in English & Hindi newspapers on 17.11.07. Society has requested all units to produce documentary evidence & list of units who fail to produce this information shall be submitted to appropriate authority.

The CETP society has not submitted the Bank Guarantee of Rs. Ten lacs as sought vide SCN dated 05.11.2007. CETP has informed that they have tried to get it done and the list of defaulters may be submitted to DPCC. 

CMC feels that it is the job of CETP to influence its members and ensure individual connection with the conveyance system. It must, therefore, be done accordingly. 

In view of the fact that the partial deficiencies which are of the serious nature have been corrected, and one deficiency needs to be corrected by DPCC as ruled by EPCA, there is still some work to be done by the CETP Society for pressure gauges and individual connection to the conveyance system and containing the TDS.  The committee is of the view that the intention is to control pollution and if CETP is sincere in its efforts the Bank Guarantee may be reduced to Rs. 5 Lakh along with an affidavit indicating correction of all the deficiencies. Time may be extended up to 31st January, 2008. 

Action Taken Report
 As decided by CMC, letter was issued and reply is yet to be received.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Since time allowed to 31st January, 2008, unit may be inspected in the 1st week of February, 2008 and case may be put up next CMC. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected. A letter may be issued to CETP Society regarding final view of Bank Guarantee. 

Action Taken Report
Letter issued on 28.01.08. CETP society has submitted a letter on 29.01.08 informing that pressure gauges have been replaced and now functional, advised all members to ensure that they are connected to conveyance system leading to CETP, plant is well maintained but yet DPCC has not issued consent and imposed a penalty for the deficiencies / defective instruments installed by DSIDC and society is contemplated to hand over the CETP back to DSIDC/COI.
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Inspection status:

Observation during inspection of CETP on 08.02.2008 is as follows:

· All the four agitators /aerators of both equalization tanks found in operation

· Inlet flow meter found non operational condition, as informed display card of it has been send for repair about one month back. 

· DMFs (6Nos) & ACFs (7Nos) found in operation & pressure gauges found functional. As informed, DMF & ACF operate on rotational basis as per intake effluent quantity. 

· Total quantity of intake effluent during month of Jan 08 was106.87 ML & in month of Dec 07 was 88.52ML.

DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	TSS-260
	_
	TSS-424
	TDS-2390
	TSS-748
	BOD- 42          TDS-2294
	NIL
	TDS-2501


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

To be put up in next CMC (MSW) meeting.
Action Taken Report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-675
	BOD- 40          TDS-2810
	TSS-930
	BOD- 38          TDS-2152


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
In view of the parameter BOD & TDS are not meeting the prescribed standard at the outlet of CETP, as per monitoring conducted by DPCC laboratory in month of Feb., March & April 2008, Bank Guarantee is reduced from Rs. 5 Lakh to Rs. One Lakh and confirmed to be submitted by 30.06.2008 by CETP Society.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

NARELA CETP (22.5  MLD)
Consent status of CETP

Consent to establish granted on 20.01.04 for a period one year. DSIDC applied for consent to operate on 03.03.06. 

Decision of Committee taken on 19.10.2007

While the unit showed compliance of the norms in the Sept. In the inspection 13.7.07 some deficiencies were found. The unit may correct all its deficiencies by 31.12.2007, failing which a BG of Rs. 5 lakh will be impose on the unit. 

It was also found that against the installed capacity of 22.5 MLD, the CETP is operating it at only 1.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the DSIDC to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The DSIDC discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.

The copy should be sent to MD (DSIDC) and Comm. of Industries. 

Deficiencies mentioned in SCN issued & brief of its reply by CETP Society:

Individual connections with conveyance system

· DSIDC has already advised all industrial units to connect to the conveyance system. Since action against individual units in this regard is to be taken under Water, EP Act etc and DPCC is the competent authority for the same.

· There is no CETP Society to run the plant & in our view the provisions of CETP Act can not be implemented in this CETP. Deficiencies as described in SCN have been rectified.

Flow meter installed at inlet of CETP found out of order. 
· A new flow meter has been procured and shall be installed within 15 days at the inlet.

No chemical dosing being done due to non-availability of chemical.
· Chemical dosing has been started and being done regularly.

Significant quantity of silt/sludge found in grit chamber, equalization tanks, tube settler & aeration tank.
· Silt/ sludge accumulated in various tanks i.e. grit chamber, equalization tank, tube settler & aeration tank etc has been removed. 

Only two aerators (out of 6 nos.) found in operational condition.
· All aerators have been made functional.

All ACF (14 nos.) found not in operational during the inspection.
· Now all the ACFs are put to use as asked.

No flow meter installed at outlet of CETP. 
· Technically the flow meter at the outlet is not required.

The deficiencies mentioned are the part of routine maintenance and rectified as and when required on need basis. 

The effluent analysis report reveals that some parameters are not meeting the prescribed standard. 

· No comment given on this issue. 

Regular testing of the effluent is not being done in the laboratory situated in the CETP.
· No comment given on this issue. 
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Inspection status:

Observation during inspection of CETP on 03.01.08 is as follows:

One air blower of aeration found out of order.

Pipes for chemical dosing are chocked & manual dosing is being carried out.

Sludge pipe between tube settler & thickner found chocked.

Flow meter at inlet found out of order. A new flow meter shown during inspection & reported to be installed within 10 days.

Two aerators (out of 6) found out of order.

Pressure gauges of ACFs & DMFs found non working condition.

No flow meter installed at outlet of CETP. 
Most of sludge drying beds are completely filled with sludge.

All ACF found not in operation during the inspection and effluent is being discharged after DMF..
Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Certain deficiencies in the noted in the July inspection was communicated to DSIDC. DSIDC in its reply has stated that they have corrected the deficiencies mentioned. An another inspection of CETP was done on 03.01.2008 and following deficiencies were noted:-

One air blower of aeration tank was found out of order.

Pipes for chemical dosing are chocked & manual dosing is being carried out.

Sludge pipe between tube settler & thickner found chocked.

Flow meter at inlet found out of order. A new flow meter shown during inspection & reported to be installed within 10 days.

Two aerators (out of 6) found out of order.

Pressure gauges of ACFs & DMFs found non working condition.

No flow meter installed at outlet of CETP. 
Most of sludge drying beds is completely filled with sludge.

All ACF found not in operation during the inspection and effluent is being discharged after DMF..
As per DPCC analysis report of the sample collected in the month of Nov. 07, BOD (40mg/l) at the outlet of CETP was found exceeding the prescribed norms .

A letter from Chairman, DPCC may be issued to MD, DSIIDC for correction of deficiencies. The final decision on the bank guarantee will be taken on the basis of extent of deficiencies corrected. 

Action Taken Report
Letter issued on 25.02.2008.

DPCC analysis report
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last four months are as under:
	Jan.08
	Dec. 07
	Nov
	Oct

	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet
	Inlet
	Outlet

	_
	_
	TSS-252
	NIL
	TSS - 288
	BOD-40
	TSS-292
	_


· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Reminder letter to be issued with all deficiencies found during new inspection. 

Action Taken Report
Letter issued on 27.03.2008. DSIDC submitted the reply on 04-04-2008 and stated as under :

· There are two air blowers and being used on alternate basis. Air blower has been got  rectified. It is added that it is a routine maintenance work. Pipe for chemicals dosing are cleaned and now the chemical dosing is being done through these pipes.

Contd..3..

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008
NARELA CETP (22.5  MLD)
..3..
· Choking of pipes is taking place because a lot of plastic pieces are being put by the industries into the conveyance system leading to CETP. It is also added that these plastic pieces are not only choking these pipes but also creating problem in various unit operations i.e. ACF & DMF. 

· Keeping in view the quantum of effluent four nos. of aerators are sufficient enough to take care of biological treatment. 

· Regarding pressure guage of ACF’s and DMF’s found non-working condition, it is a routine maintenance problem and getting rectified day to day basis.

· Technically there is a requirement of only one flow meter which is installed. It is also mentioned that the plant doesn’t have any system for bypassing the effluent and one flow meter is sufficient enough to measure the quantum of effluent.

· The sludge shall be transferred to the sludge disposal facility whenever it will be available. Activated carbon columns are not operated in order to avoid the choking of these columns because of high receipt of plastic pieces sometimes. However these activate4d carbon columns are being operated as and when required.

· For the improvement of  BOD of the treated water efforts are being made  and hopefully the desired made and hopefully the desired BOD as per law shall be maintained continuously. Above deficiencies are the routine deficiencies which are like to happen in such a huge plant. Moreover, these deficiencies are not affecting the operation of the process as the plant is being operated at its 25%-35%.
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during the last two months are as under:
	March.08
	Feb. 08

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-320
	_
	_
	_


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action. 
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Najafgarh Road Industrial area, CETP ( 9.6 MLD)
Consent status of CETP

· DSIDC has submitted a letter dated 03.08.2007 in respect of DO letter 17.07.2007, that the EPCA has already directed not to go for further construction in view of spare capacity in other functional CETPs. As regards settling the dispute with the contractor, DSIDC looking into it as per the terms of the contract separately.

· DSIDC applied for Consent to Establish on 03-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

Report was examined by Dr. B.K Guha Committee and recommended that this area should have separate CETP, since there is no surplus capacity in the CETP in the nearby vicinity.

Decision of Committee taken on 19.10.2007

Member Secretary, DPCC to study Dr. BK Guha Committee report and discuss with Prof. S.K. Gupta. Committee will be taken up this matter in next meeting.

Action Taken Report
Report of Dr. BK Guha Committee dated 03.08.2007 examined.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Member Secretary, DPCC to write a letter to GM, DSIDC to expedite the work of CETP of the area along with B.K. Guha’s Committee report. 

Action Taken Report
Letter issued on 12.02.08. No reply.
· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Reminder letter be issued.
Action Taken Report
 Letter issued on 24.03.2008. DSIDC has submitted the reply on 29-4-2008 and stated that  EPCA has directed that the necessity of Najafgarh Road CETP should be examined with respect to the available capacity of the CETP in the neighborhood area. It is presumed that the DPCC has accepted the report of Guha Committee regarding essentiality of the CETP at Najafgarh Road. In the Minutes, which have been forwarded, the quantity and quality of the effluent to be available at the Najafgarh Road CETP for treatment has not been identified. Since it is an essential requirement , the information on this account may kindly be forwarded for taking further action. It is also pertinent to mention that the quantity and quality mentioned by NEERI in their report have been at variance with the actual site conditions and therefore, before moving further, this information is essential.  
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action.
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Naraina Industrial Area, CETP ( 21.6 MLD)

Consent status of CETP

· DSIDC applied for Consent to Establish on 02-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

·  EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and it was appraised by the representative of DSIDC that CETP is under installation and it is at final stage of construction and after commissioning of the same may be handed over to CETP Society of the area. 

Inspection of CETP was carried out by DPCC officials on 23.07.2007 and following were  observed:

· CETP was under construction.

· Most of the units of CETP mentioned in layout plan have been completed.

· With regards to civil work most of the work have been completed except road and drainage work.

· With regard to electrical work cabling & lighting work are yet to be done. Same is under progress.

· Pipe fitting under progress in chemical dosing system, sludge thickener & DMF/ACFs.

· Electrical panel was also found under installation.

· There are so many machinery are yet to be installed and also lots of works are pending as observed at site.

· The representative of the construction agency i.e. M/s. SPML told that due to non availability of funds the work is not being done fastly.

Decision of Committee taken on 19.10.2007

The CETP is reported under construction for a long time. MS may write to MD (DSIDC) to complete this work by 31.12.07 and handover to CETP society by 31.12.07.

Action Taken Report
Letter issues to DSIIDC. A letter dated 08.11.2007 has been recd from COI w.r.t. status of CETPs in Delhi wherein it was stated that   the CETP at Naraina is at final stage of construction, the same will be handed over to the CETP Society after commissioning & trial run.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

A reminder letter from Member Secretary, DPCC may be issued to GM, DSIIDC

Action Taken Report
Reminder letter issued on 07.02.08. No reply.
· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Reminder letter be issued.
Action Taken Report
 Reminder letter issued on 24.03.2008 wherein they were directed to complete the work and hand over the CETP to CETP society. . No reply is received.

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action.
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Okhla Industrial Estate CETP ( 1.2 MLD)
Consent status of CETP

· DSIDC applied for Consent to Establish on 06-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and recommended that an independent CETP may be installed for this industrial area.

Decision of Committee taken on 19.10.2007

Member Secretary, DPCC to study Dr. BK Guha Committee report and discuss with Prof. S.K. Gupta. Committee will be taken up this matter in next meeting.

Action Taken Report
Report of Dr. BK Guha Committee dated 03.08.2007 examined.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Based on B.K. Guha’s Committee report, Member Secretary, DPCC may write to EPCA for reconsideration of its decision so that necessary action can be taken w.r.t the Okhla Industrial Estate CETP. Copy of the letter may be sent to MD, DSIDC. 

Action Taken Report
Letter issued on 12.02.08.
· Decision of Consent Management Committee in its meeting dated 28.02.2008:

No action.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action.
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Anand Parvat  CETP ( 24 MLD)

Consent status of CETP

· DSIDC applied for Consent to Establish on 05.08.02.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP. 

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and recommended that an independent CETP may be installed for this industrial area.

Decision of Committee taken on 19.10.2007

Member Secretary, DPCC to study Dr. BK Guha Committee report and discuss with Prof. S.K. Gupta. Committee will be taken up this matter in next meeting.

Action Taken Report

Report of Dr. BK Guha Committee dated 03.08.2007 examined.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Based on B.K. Guha’s Committee report, Member Secretary, DPCC may write to EPCA for reconsideration of its decision so that necessary action can be taken on the Anand Parbat CETP. Copy of the letter may be sent to MD, DSIDC. 

Action Taken Report

Letter issued on 12.02.08.

Decision of Consent Management Committee in its meeting dated 28.02.2008:

Letter approved for EPCA in a different file, be issued.

Action Taken Report

 Letter issued on 13.03.2008 from the file of EPCA report & copy placed in file. 

· Decision of Consent Management Committee in its meeting dated 17.04.2008:

“There appears to be no reason to form a Society when there is no CETP in APIA. Taking this stand, we must return all the petition and applications received from CETP Society in APIA to Commissioner of Industries to windup all such Societies. The logic of such Society without CETP is totally unclear and only leads to unnecessary confusion and alleged misuse of funds of members of the Society.”
Action Taken Report

 Letter issued to the commissioner of Industries on 06.05.2008.

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action.
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Mohan Co-operative Industrial Estate CETP (1.8 MLD)
Consent status of CETP

· DSIDC applied for Consent to Establish on 06-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and recommended that the effluent from the Mohan Co-op. Industrial Estate may be treated in the CETP at Okhla Industrial Area.

Decision of Committee taken on 19.10.2007

Member Secretary, DPCC to study Dr. BK Guha Committee report and discuss with Prof. S.K. Gupta. Committee will be taken up this matter in next meeting.

Action Taken Report
Report of Dr. BK Guha Committee dated 03.08.2007 examined.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Member Secretary, DPCC to write to EPCA highlighting the recommendations of B.K. Guha’s Committee report for linking the area to the existing CETP system at OKhla. Copy of the letter may be sent to MD, DSIDC. 

Action Taken Report
Letter issued on 12.02.08.
· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Follow up. 

Action Taken Report
 Letter issued on 15.04.2008 to EPCA highlighting the recommendations of B.K. Guha’s Committee report for linking the area to the existing CETP system at OKhla. Copy of the letter sent to MD, DSIDC. No response received so far.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action.
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Udyog Vihar (Bawana) Industrial Area CETP ( 35 MLD)

Consent status of CETP

· DSIDC applied for Consent to Establish on 05.08.02.

· Consent to Establish was granted on 20.01.2004 for a period of one year.

DSIIDC has not applied for extension of consent to establish or consent to operate. 

Present status of CETP not available.   

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Member Secretary, DPCC to write a letter to GM, DSIDC to expedite the work of CETP of the area and for compliance of provisions of the Air & Water Acts.

Action Taken Report
Letter issued on 28.01.08. No reply.
· Decision of Consent Management Committee in its meeting dated 28.02.2008:

Reminder letter to be issued.

Action Taken Report
 Reminder letter issued on 25.03.2008  to the GM, DSIDC to expedite the work of CETP of the area and for compliance of provisions of the Air & Water Acts. No reply received so far.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:
No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008
Dr. Sen Nursing home Nallah STP  (10 MLD)

Consent Status 

Consent valid up to 25-02-08. Not applied for renewal.
Decision taken  

Issue SCN for deficiencies observed during the inspection.
Action taken report

Plant was inspected on 04.12.06.

SCN issued on 02.01.2007 for the deficiencies observed during the inspection.

No reply has been received. 
As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.
Decision of CMC taken on 19.10.2007

Member Secretary, DPCC to inspect.

Action taken report

STP was inspected on  05.01.2007 and some deficiencies were observed during inspection.
Decision of CMC taken on 09.01.2008

Inspection done on 05.01.2007. Issue notice for rectification of deficiencies within 30 days time, failing which Bank Guarantee of Rs. 2 lakh will be imposed. 

Action taken report

SCN issued on 12.2.2008. Reply awaited.
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 17.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 22.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Case to be taken up in April CMC along with the reply of the unit. 

Action Taken Report

No reply received from the unit in response to SCN issued on 12.02.2008 in pursuance of decision taken on 09.01.2008.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.20008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 11.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Ask him to apply for renewal of consent under Air & Water Act and authorization under HWM Rules. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008
Delhi Gate Nallah STP, (2.2 MGD)

Consent Status 

Consent to operate issued on 15.2.2007 & valid upto 11.10.09.

Decision taken  

Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days and also to maintain the log book properly

Action taken report

Consent Issued. As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

No action. 

Action taken report

-
Decision of CMC taken on 09.01.2008

No action.
Action taken report

No action.
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 17.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 22.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

No action. 
Action Taken Report

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.20008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 11.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

KONDLI STP , Ph-I (10MGD)
Consent Status 

Applied for consent to operate on 19.04.06.

Decision taken on 16.01.2007  

Issue SCN giving last opportunity to remove the deficiencies observed during inspection
Action taken report

SCN issued on 15-02-07. Reply received on 23-02-07. The following submissions have been made:-

· Power back up system, with flow meters, is being provided in due course of time.

· All aerators and PST are in working condition now. 

· Presently, treated effluent is being used for horticulture purpose within the premises of plant. Further reuse of treated effluent is under consideration with DDA.

· Work order has already been placed for renovation of digester and gas holders. 

· Plant has submitted required information as per consent application along with an affidavit.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Consent to operate will be granted once the deficiencies noted in SCN are finally implemented and confirmed to DPCC.
Action taken report

Letter issued on 06.11.2007. Reply recd on 07.12.07. The following submissions have been made:-

The flow meter installed at inlet & outlet are working properly. Case of providing power backup to the flow meter is under process.

All aerators &PST are in working order.

Treated effluent is being used for horticulture within premises, DDA laid pipes to take 2.6 lac Gallon per day, proposed to supply 8 MLD to IL&FS for proposed Gazipur MSW complex. Requested for grant of consent.
Decision of CMC taken on 09.01.2008

The unit has complied with the deficiencies but not filed an affidavit. STP may be inspected and case may be put up in next CMC.
Action taken report

Inspected on 20-2-2008. The observation are as follows : 

· Flow meter at inlet and outlet of STP found installed and operational, work of providing of UPS as power backup going on.

· all aerators found functional however one aerator was found closed as standby.

· All the digesters (three) and gas holder(one) of phase-1 are under refurbishment and work to be awarded shortly as informed. 

· As reported DDA has laid their network for reuse of approximate 2.6 Gallon per Day for horticultures purposes, pump house has been installed by DDA. 

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 31.12.2007), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), except BOD (35 mg/l) other parameters are within the prescribed standard.
Contd..2..

..2..

KONDLI STP , Ph-I (10MGD)
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Ask the unit to file an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

Letter issued on 24.03.2008. Unit has submitted reply on 29.04.08 (without affidavit) and stated that flow meters with power & back up installed at inlet and outlet are working properly, all aerators & PST are in working order, for renovation of digester & gas holders tender is under process for award the work to the lowest tenderer, DDA has laid their network for horticulture and 8 MLD will be supplied to M/s IL&FS for proposed MSW complex at Gazipur. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008),  parameters BOD (32 mg/l) is exceeding the prescribed standard (30 mg/l).
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 19.03.2008), STP found non operational during monitoring.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

The unit may be asked to explain why the STP was non operational and how is the waste water getting disposed off  as observed during inspection by DPCC Laboratory on 19.03.2008, for conducting monitoring. STP to file reply by 30.06.2008. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

KONDLI STP, Ph-II  (25 MGD)

Consent Status 

Applied for consent to operate on 19.04.06.

Decision taken on 16.01.2007  

Issue SCN giving last opportunity to remove the deficiencies observed during inspection.
Action taken report

SCN issued on 15-02-07. Reply received on 23-02-07. The following submissions have been made:-

· Power back up system, with flow meters, is being provided in due course of time.

· All aerators are in working condition now. 

· Work order has been placed for renovation of five sludge digesters and 2 gas holders.

· Presently, treated effluent is being used for horticulture purpose within the premises of plant. Further reuse of treated effluent is under consideration with DDA.

· Work order has already been placed for renovation of digester and gas holders. 

· Plant has submitted required information as per consent application along with an affidavit.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Consent to operate will be granted once the deficiencies noted in SCN are finally implemented and confirm to DPCC.
Action taken report

Letter issued on 06.11.2007. Reply recd on 07.12.07. The following submissions have been made:-

The flow meter installed at inlet & outlet are working properly. Case of providing power backup to the flow meter is under process. All aerators &PST are in working order. Treated effluent is being used for horticulture within premises, DDA laid pipes to take 2.6 lac Gallon per day, proposed to supply 8 MLD to IL&FS for proposed Gazipur MSW complex. Requested for grant of consent.
Decision of CMC taken on 09.01.2008

The unit has complied with the deficiencies but not filed an affidavit. STP may be inspected and case may be put up in next CMC.
Action taken report

Inspected on 20-2-2008. The observation are as follows :

Flow meter at inlet and outlet of STP found installed and operational, work of providing of UPS as power backup going on.

All aerators found functional however one aerator was under maintenance.

All the digesters (five) and gas holder(two) of phase-II are under refurbishment and work to be awarded shortly as informed

As reported DDA has laid their network for reuse of approximate 2.6 Gallon/day for horticultures purposes, pump house has been installed by DDA. 

Work of renovation of sludge drying beds was going on and will be completed within 2 months.
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 31.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Ask the unit to file an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Contd..2..

..2.. 
KONDLI STP , Ph-II (10MGD)
Action Taken Report

Letter issued on 24.03.2008. Unit has submitted reply on 29.04.08 (without affidavit) and stated that flow meters with power & back up installed at inlet and outlet are working properly, all aerators & PST are in working order, for renovation of digester & gas holders tender is awarded and likely to be completed by September, 2008, DDA has laid their network for horticulture and 8 MLD will be supplied to M/s IL&FS for proposed MSW complex at Gazipur. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 19.03.2008), STP found non operational during monitoring.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

The unit may be asked to explain why the STP was non operational and how is the waste water getting disposed off  as observed during inspection by DPCC Laboratory on 19.03.2008, for conducting monitoring. STP to file reply by 30.06.2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

KONDLI STP, Ph-III , (10 MGD)
Consent Status 

Consent issued on22.09.05 and valid up to 02-12-07.Applied for renewal of Consent on 16.11.2007.
Decision taken  

Issue SCN to the plant with a copy to CE, DJB
Action taken report

SCN issued on 13-03-07.

Reply received on 03-04-07. The following submissions have been made:-

Power back up system, with flow meters, is being provided. 

All aerators are in working condition now. Report is being submitted month wise. 

Sludge analysis is being carried out in the lab of DJB at STP Kondli and same is being forwarded to Director (T & QC) DJB. However, a copy of report from July 06 to Feb 07 is enclosed herewith. 

Record is being maintained at Laboratory under the supervision of ACWQA Kondli plant.  

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Consent to operate will be granted once the deficiencies noted in SCN are finally implemented and confirm to DPCC.
Action taken report

Letter issued on 06.11.2007. Reply recd on 07.12.07. The following submissions have been made:-

The flow meter installed at inlet & outlet are working properly. Case of providing power backup to the flow meter is under process.

All aerators &PST are in working order.

Treated effluent is being used for horticulture within premises, 

DDA laid pipes to take 2.6 lac Gallon per day, proposed to supply 8 MLD to IL&FS for proposed Gazipur MSW complex. Requested for grant of consent.
Decision of CMC taken on 09.01.2008

The unit has complied with the deficiencies but not filed an affidavit. STP may be inspected and case may be put up in next CMC.

Action taken report

Flow meter at inlet and outlet of STP found installed and operational, work of providing of UPS as power backup going on.

All aerators found functional, Digesters (three) and gas holder(2) of phase III found functional. 

Bio-gas generated is burnt at site. As informed, a generator is purposed to install in near future at Phase-IV STP (45 MGD) to generate electricity by bio-gas for operation of said phase-IV STP.

As informed the work of phase-IV STP will be awarded shortly and schedule time for construction is 2 years. 

DDA has laid their network for reuse of approximate 2.6 Gallon per Day for horticultures purposes and pump house has been installed by DDA. 

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 31.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), except TSS (54 mg/l) other parameters are within the prescribed standard.
Contd..2..

..2..

KONDLI STP , Ph-III (10MGD)
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be issued to the unit for submitting an affidavit as to why the parameters are not meeting the prescribed limit and also to file an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

Letter issued on 24.03.2008. Unit has submitted reply on 29.04.08 (without affidavit) and stated that flow meters with power & back up installed at inlet and outlet are working properly, all aerators & PST are in working order, the digesters and gas holders are working properly, DDA has laid their network for horticulture and 8 MLD will be supplied to M/s IL&FS for proposed MSW complex at Gazipur. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 19.03.2008), STP found non operational during monitoring.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

The unit may be asked to explain why the STP was non operational and how is the waste water getting disposed off  as observed during inspection by DPCC Laboratory on 19.03.2008, for conducting monitoring. STP to file reply by 30.06.2008. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Nehru Vihar, Oxidation Pond STP (13.5 MLD)

Consent Status 
Consent issued on21.09.05 and  valid up to 28.11.07. Applied for renewal of consent on 25.10.2007.

Decision taken  

-
Action taken report

· Plant was inspected on 15.11.06.

· SCN issued on 26.12.2007 as number of deficiencies were observed during the above said inspection.

· Plant has not submitted any reply. 

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.
Decision of CMC taken on 19.10.2007

SEE  to inspect.
Action taken report

Inspected on 03.01.2008.  Applied for renewal of consent on 25.10.2007.
Decision of CMC taken on 09.01.2008

The unit was inspected on 03.01.2008 by SEE & deficiencies were noted. Issue letter to DJB that if the STP will correct the deficiencies within 30 days, application for consent for renewal will be considered accordingly.
Action taken report

Letter issued on 12-2-2008. No Reply received.
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 17.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Reminder letter to be issued to the unit for submitting an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

 Letter issued on 25.03.2008.

Unit has submitted reply on 03.04.08 (without affidavit) and submitted that approach road to the outlet point has been cleared and are being maintained properly, photographs of the site enclosed, after the de-silting of oxidation pond no. 9 the DJB has provided the bio-remediation treatment of the sewage water at the inlet channel of the oxidation pond and de-silting of the oxidation ponds is not felt necessary at this stage. However, the result of the final effluent of the outlet of the oxidation pond are within the prescribed limit and requested to grant the consent.  

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard.
Contd..2..
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Nehru Vihar, Oxidation Pond STP (13.5 MLD)

As per DPCC Analysis report, dated 09.04.2008 (sampling done on 17.03.2008), all parameters are within the prescribed standard.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

The de-silting of oxidation pond should be done in a phased manner for better treatment. A time bound program is to be submitted in this regard within period of one month. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Keshopur STP (72MGD (40+20+12)

Consent Status 

Consent issued on 21.09.05 & expired on 24-09-07 for 60 MGD. 
Applied for renewal of consent on 7-1-2008.
Decision taken  

-
Action taken report

· Plant inspected by DPCC officials on 5.12.2006.

· SCN issued on 02.1.2007 as number of deficiencies     were observed.

· Plant has not submitted any reply.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

· However, no consent application for the STP of 12 MGD capacity. DPCC lab reported that said STP was found abundant during sampling in Sept 2007. 

Decision of CMC taken on 19.10.2007

Ask for renewal of consent. Unit may also be asked to rectify the deficiencies as communicated vide SCN dated 2.1.07. STP may give time of one month to do so.
Action taken report

Letter issued on 07.11.2007.  Submitted application for renewal of consent by post, (ID No. 24675 dated 07.01.2007) & as decided, letter for deficiencies issued on 08.01.08. No comments about the deficiencies mentioned in the letter.

Decision of CMC taken on 09.01.2008

Letter was issued on 07.11.07 for correction of deficiencies. No reply received. If the unit does not file an affidavit within 30 days, Bank Guarantee of Rs. One Lakh under Water Act will be imposed & further action will be taken.
Action taken report
Letter issued on 7-2-2008. Reply awaited.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 01.01.2008), all parameters are within the prescribed standard for phase-I & Phase-II. Phase-III STP (12 MGD) found non operational during operational.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 23.01.2008), all parameters are within the prescribed standard for phase-I. For Phase-II, TSS964mg/l) & BOD ( 40 mg/l) are exceeding the prescribed norms. Phase-III STP (12 MGD) found non operational during operational.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be issued to the unit for submitting an affidavit as to why the parameters are not meeting the prescribed limit and also to file an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

 Letter issued on 24.03.2008. No reply has been received from the unit. 

A letter received from National River Conservation Directorate, MOEF, Govt of India dated 25.04.2008 regarding construction and augmentation of treatment capacity (72 MGD) of STP at Keshopur under YAP-II in Delhi. DJB has submitted a DPR for treatment of sewage in order to meet standards of 20 mg/l and 30 mg/l for BOD and SS respectively.  However, there is inadequate provision for disinfection of Faecal Coliform. NRCD has requested that details of standards and specific guideline issued by DPCC to DJB with regard to improve the water quality of Yamuna may be intiamated to the NRCD so that they can consider their proposal. 
Contd..2..
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Keshopur STP (72MGD (40+20+12)

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard for phase-I & Phase-II. Phase-III STP (12 MGD) found non operational during operational.
As per DPCC Analysis report, dated 09.04.2008  (sampling done on 18.03.2008), all parameters are within the prescribed standard for phase-I & Phase-II. Phase-III STP (12 MGD) found non operational during operational.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

The unit may be asked to explain why the STP Phase-III (12 MGD) was non operational and how is the waste water getting disposed off  as observed during inspection by DPCC Laboratory on 18.03.2008 for conducting monitoring. STP to file reply by 30.06.2008. 

An appropriate reply for MOEF will be drafted by SEE for this STP and put up on file for approval before issue. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Mehrauli  STP (5 MGD)
Consent Status 

Consent issued on 20.03.2007 & valid upto 15.12.09.

Decision taken  

Issue consent to operate subject to the following consent conditions as well as comments:

1. Install mechanical sludge dewatering system.

2. Ensure proper storage of dry sludge.                

3. Examination of the issue related to low capacity utilization and quick resolution of the problem in consultation with related agencies.                                  

Comments:-

 a. DPCC would appreciate if DJB takes steps to generate gas form the STP.                                                                                                   
b. DJB would make all efforts to reuse the treated effluents in the nearby parks and farm houses.                                              

Action taken report

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Mehrauli STP has not replied to the consent conditions imposed on 20.3.07. STP may be asked to reply within one month positively. 

Action taken report

Letter issued on 06.11.2007. Reply received on 28.12.2007 and submitted the action taken report w.r.t. compliance of consent conditions.  
Decision of CMC taken on 09.01.2008

The matter of low intake quantity of sewage at STPs will be taken up in next CMC (MSWM) Meeting with the DJB & MCD.
Action taken report

Meeting notice issued to invites DJB and MCD Officials.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 24.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be Member (Drainage) with a copy to Sh. V. K. Jain, SE (E&M), DJB who have  attend the meeting) by Member Secretary, DPCC for seeking reasons of low intake quantity of sewage & under utilization of STP capacity.   

Action Taken Report

 Letter issued on 31.03.2008. No reply received so far.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 24.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

MS to issue reminder to Member (Drainage), DJB on last decision of CMC dated 29.02.2008 for seeking reasons of low intake quantity of sewage & under utilization of STP capacity.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Yamuna Vihar Phase –I STP (10 MGD)

Consent Status 

Consent issued on 28.2.2007 & valid upto 16.11.07. Applied for renewal of consent on 25.10.2007.  
Decision taken  

Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days.
Action taken report

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

STP has not replied to consent conditions imposed on 28.02.07. STP may be asked to reply within one month positively. 

Action taken report

Letter issued on 06.11.2007. Reply received on 28.12.2007 and submitted the action taken report w.r.t. compliance of consent conditions. Applied for renewal of consent on 25.10.2007.  
Decision of CMC taken on 09.01.2008

SEE to inspect and to submit report in the next CMC (MSW) Meeting.
Action taken report

Inspected on 19-2-2008. The observation are as follows: 

All aerators found in operation. 
Ultrasonic flow meters installed at inlet and outlet of STP. As informed magnetic flow meter van not be provided being open channel discharge.
Bio-gas generated in plant is burnt at site, however as informed DJB has plant to install generators(3 nos. x 1000 KVA) for generation of electricity from bio-gas of phase-I&II and same will be installed in next two months. 
All 12 SDBs were found filled with Sludge as reported STP is facing problem w.r.t lifting of sludge/manure. 
Regarding reuse of treated effluent, an effluent pump house is under installation near the STP.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 31.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be issued to the unit for submitting an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

 Letter issued on 25.03.2008. No reply received.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 27.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 19.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Yamuna Vihar Phase –II STP  (10 MGD)

Consent Status 

Consent issued on 28.2.2007 & valid upto 28.12.09.

Decision taken  

Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days.
Action taken report

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), plant is not meeting the prescribed standard.

Decision of CMC taken on 19.10.2007

The unit has not replied to consent conditions imposed on 28.2.07. The unit is also not meeting with the prescribed standards. SCN may be issued u/s 33 A of Water Act for remedial action within one month. 

Action taken report

Letter issued on 07.11.2007. Reply received on 28.12.2007 and submitted the action taken report w.r.t. compliance of consent conditions.  
Decision of CMC taken on 09.01.2008

SEE to inspect and to submit report in the next CMC (MSW) Meeting.
Action taken report

Inspected on 19-2-2008. The observation are as follows : 

Ultrasonic flow meters installed at inlet and outlet of STP, commissioning is expected within a week. 

All aerators found operational. 

A new fine screen installed after primary screen section. 

Bio-gas generated in plant is burnt at site, however as informed DJB has plant to install generators(3 nos. x 1000 KVA) for generation of electricity from bio-gas of phase-I&II and same will be installed in next two months. 
SDBs were found filled with Sludge as reported STP is facing problem w.r.t lifting of sludge/manure. 
Regarding reuse of treated effluent, an effluent pump house is under installation near the STP.
Acoustic enclosures installed with the DG sets of 7.5 KVA and 160 KVA.
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 31.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be issued to the unit for submitting an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

Letter issued on 24.03.2008. No reply received so far. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 27.02.2008), parameters BOD (34 mg/l) is exceeding the prescribed standard (30 mg/l).
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 19.03.2008), parameters BOD (33 mg/l) is exceeding the prescribed standard (30 mg/l).
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Ask the unit to file explanation why BOD is exceeding the standard in the month of March & April, 2008 by 30.06.2008. Call on July, 2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Rithala STP– Ph-I, (40 MGD)

Consent Status 

Previous Consent valid upto 04.05.06. Applied on 29.06.2006 for renewal of consent.
Decision taken  

Issue SCN giving last opportunity to remove deficiencies observed during inspection.

Action taken report

SCN issued on 15.02.07.Reply received on 09.03.2007 & following submissions have been made:-
Necessary action initiated for rectification of flow meter. Repair of 3 aerators is underway.
Secondary settling tanks have been operational after rectification. Gas holders are under repair. 5 MGD of treated effluent is being given to DDA for horticulture purpose. In addition to some quantity being lifted by DDA through tankers. Gas collection improved. 1200 m3 gas is being generated per day and sent to Phase – II for power generation.
As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Unit was given last opportunity to correct deficiencies. A reply received on 9.3.07 indicates that some remedial action has been taken. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 

Action taken report

Letter issued on 07.11.2007. Reply received on 26.12.2007 and submitted affidavit to confirm correction of deficiencies. Further requested for exemption of Bank Guarantee as all defects/ deficiencies attended.  
Decision of CMC taken on 09.01.2008

MS, DPCC  to inspect  and submit the report in next CMC (MSW) Meeting.
Action taken report
Inspected on 21-2-2008. The observation are as follows :

Ultrasonic flow meters found operational. 

18 Aerators (out of 24) found operational, as informed aerators are operated on rotational basis as per requirement. 

Gas generated in phase-I is transferred to phase-II for operation of generators. 

One sludge digester found under maintenance. 

Approximate 1200 cubic meter gas is generated per day. 

Average intake effluent intake in jan,’2008 was 17.1 MGD.

One gas holder found not in use and as informed it is to be reconstructed /refurnished. Treated effluent (5MGD) is used by DDA for horticulture. It is purposed that 25 MGD treated effluents will be supplied to Proposed Pragati Power Projects, Bawana and 2 MGD to NDPL.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007) except TSS (62 mg/l), other parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 29.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to the Member (Drainage) for seeking reasons of low intake quantity of sewage & under utilization of STP capacity. Letter to be issued to the unit for submitting an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Contd..2..
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Rithala STP– Ph-I, (40 MGD)

Action Taken Report

 Letters issued on 26.03.2008. 
Reply received on 31.03.2008 stating that DJB has rectified all its deficiencies. DJB has requested that exemption may be granted to submit Bank Guarantee as DJB is running the STP for public service purpose and have no profit motive unlike other private installation where these norms are generally applicable.  DJB has already submitted an affidavit regarding rectification of deficiencies. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 28.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 17.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Rithala  STP– Ph-II, ( 40 MGD)

Consent Status 

Previous Consent valid upto 21.01.06. Applied for renewal of consent on 20.01.2006. 

Decision taken  

Issue SCN giving last opportunity to remove the deficiencies observed during inspection

Action taken report

SCN issued on dated 15-02-07. Reply received on 22-03-07. The following submissions have been made:-

The defective flow meter at treated effluent channel made operational. Both sludge thickeners are in working condition now. Sludge de-watering unit is operated only during monsoon season. Matter wrt reuse of treated effluent is under planning stage. Electricity is being generated as per    raw sewage availability. As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Unit was given last opportunity to correct deficiencies. A reply received on 22.03.07 indicates that some remedial action has been taken. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 

Action taken report

Letter issued on 07.11.2007. Reply received on 26.12.2007 and submitted affidavit to confirm correction of deficiencies. Further requested for exemption of Bank Guarantee as all defects/ deficiencies attended.  
Decision of CMC taken on 09.01.2008

MS, DPCC  to inspect  and submit the report in next CMC (MSW) Meeting.
Action taken report

Inspected on 21-2-2008. The observation are as follows :

Ultrasonic flow meters operational. 

Primary Settling Tanks and Final Settling tanks found operational. 

One aeration tank out of four found not in use and as informed tank is under cleaning and not in use from last six months. 

Three generators (each 890KWH) installed for generation of electricity from bio-gas and found operational.

Total power requirement per day for phase-II is approx. 34000 KWH/ day (for 40 MGD effluents) and average power generation from bio-gas was 14000 KWH/ day. As informed actual requirement for power is 20,000 to 25,000 KWH/ day as per the average intake.  

Approximate 8000 cubic meter gas is generated per day. 

Average intake effluent intake in Jan, 2008 was 23.64 MGD. 

Treated effluent (5MGD) is used by DDA for horticulture. It is purposed that 25 MGD treated effluents will be supplied to Proposed Pragati Power Projects, Bawana and 2 MGD to NDPL.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 29.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be Member (Drainage) for seeking reasons of low intake quantity of sewage & under utilization of STP capacity. Letter to be issued to the unit for submitting an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Contd..2..
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Rithala STP– Ph-I, (40 MGD)

Action Taken Report

Letters issued on 26.03.2008. 

Reply received on 31.03.2008 stating that DJB has rectified all its deficiencies. DJB has requested that exemption may be granted to submit Bank Guarantee as DJB is running the STP for public service purpose and have no profit motive unlike other private installation where these norms are generally applicable.  DJB has already submitted an affidavit regarding rectification of deficiencies. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 28.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 17.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Pappankalan STP ( 20 MGD)

Consent Status 

Previous Consent valid upto 09.12.04. Applied for renewal of consent on 10.12.2004. 

Decision taken  

Issue SCN to SE, a copy to Chief Engineer giving last opportunity to rectify the deficiencies

Action taken report

SCN issued on 15.02.07. No reply received. 

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

While the unit is applied for consent he has not corrected deficiencies. Unit was given last opportunity to correct deficiencies. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 

Action taken report

Letter issued on 07.11.2007. Reply received on 26.12.2007 and submitted affidavit to confirm correction of deficiencies. Further requested for exemption of Bank Guarantee being a Govt. deptt. Under GNCTD. Submitted application for renewal of consent by post, (ID No. 24674 dated 07.01.2007) & as decided, letter for deficiencies issued on 08.01.08.
Decision of CMC taken on 09.01.2008

EE to inspect and report submit in next CMC (MSW) Meeting.
Action taken report

Aerators 22 nos  found in operation and 2 are under maintenance. 

Ultrasonic flow meter found operational. 
Sewage intake is low (14-15MGD) compared to installed capacity, as reported by Sh. Katakwal, EE DJB, this is due to the no population in the catchment area i.e. Dwarka. Presently they are taking sewage from Najafgarh drain also. 
All the digester found under use, however biogas generated is burned in the plant through burners as the provision of supply of  biogas is not provided so far due to less occupancy in the nearby vicinity of  STP. 
Acoustic enclosure provided with the DG set of 125KVA. 
As reported, DDA has constructed for reservoirs for reuse of treated effluent.     

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 23.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

To ensure the maximum capacity utilization of the installed STP near Najafgarh nallah, STPs may be identified and accordingly letter may be written to CEO, Delhi Jal Board for taking the required quantity of water from Najafgarh Drain. 

Letter to Member (Drainage) for seeking affidavit for the reasons of low intake quantity of sewage & under utilization of STP capacity after inspection of the STP personally. Case to be taken up in April CMC.

Action Taken Report

Letters issued on 26.03.2008. 

Unit has submitted its reply along with an affidavit on 15.04.2008 stating that the reason for low intake quantity of sewage and under utilization of 20 MGD STP after inspection along with Member (Draining) are as under :-

Contd..2..
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Pappankalan STP ( 20 MGD)

(iii) The encatchment area of this 20 MGD STP is not fully developed, as and when area is fully developed, the capacity of STP would full be utilized.

(iv) Presently, they are lifting approx. 10 MGD sewage water from Palam Drain / Nalah for this STP and treating about 16 MGD sewage at this STP.
As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 26.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Najafgarh STP, ( 5 MGD
Consent Status 

Applied for consent to operate on 29.11.2004. 

Decision taken  

Issue SCN to SE, a copy to Chief Engineer giving last opportunity to rectify the deficiencies.

Action taken report

SCN issued on 15.02.07. No reply received.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

While the unit is applied for consent he has not corrected deficiencies. Unit was given last opportunity to correct deficiencies. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 

Action taken report

Letter issued on 07.11.2007. Submitted affidavit on 09.01.2008 to confirm correction of deficiencies. Deposited fee on 08.01.08 for conducting effluent analysis by DPCC lab.

Submitted application for renewal of consent by post, (ID No. 24673 dated 07.01.2007) & as decided, letter for deficiencies issued on 08.01.08.
Decision of CMC taken on 09.01.2008

EE to inspect and report submit in next CMC (MSW) Meeting.
Action taken report

All 16 aerators found operational. 
Average sewage in take is 1.5MGD to 2.0MGD. 
As reported Sewer lines are yet to be installed in catchment area of STP and presently they are taking sewage from Najafgarh and Dhrampura Drain. 
One DG Set found installed in dismantled conditions and of no use. 
Only single power supply line provided and power failure is approx. 100-125hr/ month, as per logbook. 

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 23.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

To ensure the maximum capacity utilization of the installed STP near Najafgarh nallah, STPs may be identified and accordingly letter may be written to CEO, Delhi Jal Board for taking the required quantity of water from Najafgarh Drain. 

Letter to Member (Drainage) for seeking affidavit for the reasons of low intake quantity of sewage & under utilization of STP capacity after inspection of the STP personally. Case to be taken up in April CMC.

Action Taken Report

Letters issued on 26.03.2008. No reply received so far.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 26.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Ask the unit to file reply sought by CMC on 29.02.2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Nilothi STP (40 MGD)

Consent Status 

Consent expired in 02-12-06. Applied for renewal of consent on 26-11-2007.
Decision taken  

-
Action taken report

Plant was inspected on 17.11.2006.

SCN was issued on 26.12.06, as numbers of deficiencies were observed.

Plant has not submitted consent application for renewal of consent.

As per inspection by DPCC laboratory dated 19.09.2007 it reveals that the plant was non operational during the monitoring. 

Decision of CMC taken on 19.10.2007

The unit was issued SCN on 17.11.2006 and the reply received indicates that some deficiencies have been corrected. SEE to inspect and submit a report on file for necessary action.  The unit may ask to apply for renewal of consent immediately.
Action taken report

Letter issued on 07.11.2007. no reply received. Inspected on 04.01.2007 and some deficiencies were observed during inspection. Not applied for renewal of consent.
Decision of CMC taken on 09.01.2008

Inspection was done by SEE on 04.01.2007 and the points were noted which may be communicated to the STP to follow up the points.  
Action taken report

Letter issued on 7-2-2008. No reply received.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 21.11.2007), Except TSS (64 mg/l) & BOD (34 mg/l) others parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 24.01.2007), Except BOD (33 mg/l) others parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

To ensure the maximum capacity utilization of the installed STP near Najafgarh nallah, STPs may be identified and accordingly letter may be written to CEO, Delhi Jal Board for taking the required quantity of water from Najafgarh Drain. 

Reminder letter to be issued to the unit to apply for consent, for submitting an affidavit as to why the parameters are not meeting the prescribed limit and also to file an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

Letters issued on 26.03.2008. No reply received so far.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 28.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 18.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Ask the unit to file reply sought by CMC on 29.02.2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Rohini STP (15 MGD)

Consent Status 

Plant has submitted application on 01-05-07 for consent to operate. 

Decision taken  

CE, DJB was asked to apply for consent, who agreed to do the needful.
Action taken report

As per DPCC laboratory report, during the last several occasions, plant found non operational. Hence, no monitoring report available with DPCC. However plant has submitted analysis report of its own. Treated effluent quality is as per norms laid down.
As per inspection by DPCC laboratory dated 21.09.2007 it reveals that the plant was non operational during the monitoring. 

Decision of CMC taken on 19.10.2007

SEE to inspect and report on file.
Action taken report

Inspected on 04.01.2007.

Decision of CMC taken on 09.01.2008

Inspection was done by SEE on 04.01.2007 and the points were noted which may be communicated to the STP to follow up the points.  
Action taken report

Letter was issued on 12-2-2008. No reply received.

As per DPCC Analysis report, dated 11.01.2008 STP was found non operational during inspection on 21.09.2007.
As per DPCC Analysis report, dated 25.02.2008 STP was found non operational during inspection on 29.01.2007.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Sh. Aditya Narayan Singh, Scientist, Deptt of Env., will inspect the STP & submit report on file. Based on that, decision will be taken to write letter to Member (Drainage), DJB. Case to be taken up in April CMC.

Action taken report

Inspected by Sh. A. N. Singh.

As per DPCC Analysis report, dated 18.03.2008 (visited on 28.02.2008), STP was found non operational during inspection on 21.09.2007.
As per DPCC Analysis report, dated 09.04.2008 (visited on 17.03.2008), STP was found non operational during inspection on 21.09.2007.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

The STP is not getting adequate water as per the installed capacity. As per the inspection report it was found that there is lack of coordination between DJB and DDA for getting adequate water at STP. Issue letter to both DJB and DDA that they make best possible efforts to ensure that the capacity of the STP plant is better utilized in pubic interest. Call Ex. Engineer of Rohini Zone from DJB & DDA in next CMC (MSW) meeting. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Coronation Pillar STP (40 MGD)

Consent Status 

Consent to operate issued on 28.2.2007 valid upto 12.03.2009.

Decision taken  

Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days and also to maintain the log book properly.

Action taken report

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

No action. 

Action taken report

-
Decision of CMC taken on 09.01.2008

No action. 

Action taken report

No action

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 17.12.2007), all parameters are within the prescribed standard. Phase-III (10 MGD) found non operational during sampling.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be Member (Drainage) for seeking affidavit for the reasons of low intake quantity of sewage & under utilization of STP capacity (only 10 MGD). 
Action Taken Report

 Letter issued on 25.03.2008. 
Unit has submitted its reply along with an affidavit on 11.04.08 & informed that the commo0n area SPS of NSTP are Jahangirpuri, Nehru Vihar, Adarsh Nagar, Model Town, R.U. Nagar. Out of these trunk sewers i.e. UTS & NTS and Jahangirpuri Trunk Sewers are settled resulting into less flow of sewage. The rehabilitation of UTS/WTS is in progress which may increase sewer flow. Also the tenders on rehabilitation of Jahangirpuri Trunk Sewer have been called for which work will be awarded in near future. However, all the sewage coming to the STP is fully treated without by-passing any sewage. 
As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard for Phase-I, II,III and old clarifier.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 18.03.2008), all parameters are within the prescribed standard for Phase-I, II,III. BOD (32 mg/l) is exceeding the prescribed norms for old clarifier.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Let the unit file reply by 30.06.2008, why the BOD is exceeding the prescribed norms in the monitoring conducted by DPCC Laboratory on 18.03.2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Vasant Kunj STP (5.2 MGD)

Consent Status 

Consent issued on 22.09.05 & valid up to 11-12-07.Applied for renewal on 29-1-2008.

Decision taken  

-

Action taken report

Plant was inspected on 14.11.06.

SCN issued on 26.12.2007 as number of deficiencies were observed during the above said inspection.

Plant has not submitted any reply. 

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Unit was given last opportunity to correct deficiencies. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 

Action taken report

Letter issued on 06.11.2007. No reply received.
Decision of CMC taken on 09.01.2008

EE to inspect and put up in next CMC (MSW) meeting.
Action taken report

Inspected on 22-1-2008 and observations are as under: 

Flow meter installed for 2.2. MGD plant found operational, however flow meter of 3 MGD found non-operational condition. 

4 aerators (out of 8) for 2.2 MGD and 4 aerators (out of 10) found out of order.

Logbook maintained for operation of pumps etc.

Treated effluent discharge in drain leading to Sanjay Ban as reported.

Representative of DJB not shown the records wrt removal of sludge/ manure from the plant.

Applied for renewal of consent on 29.01.2008.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007), all parameters are within the prescribed standard for phase-I (2.2 MGD) plant. However for phase-II (3.0 MGD) plant TSS (65 mg/l) & BOD (34 mg/l) are exceeding the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 24.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue notice for non operation of flow meter & aerators, to file an affidavit w.r.t. correction of deficiencies within one month & reason for non submission of Bank Guarantee. Case to be taken up in April CMC.
Action Taken Report

 Letter issued on 25.03.2008. Reply received on 24.04.2008 without affidavit. 
As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (visited on 18.03.2008), STP was found non operational.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

The unit may be asked to explain why the STP was non operational and how is the waste water getting disposed off  as observed during inspection by DPCC Laboratory on 18.03.2008, for conducting monitoring. STP to file reply by 30.06.2008. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Narela STP (10 MGD)

Consent Status 

Previous Consent valid upto 14.01.2005. Applied for renewal of consent on 14.01.2005 and issued on 7-11-2007 and valid up to 13-1-2008.Applied for renewal of consent on 3-1-2008.
Decision taken  

Issue SCN giving last opportunity to remove the deficiencies observed during inspection.
Action taken report

SCN issued on 20-03-2007. Reply received on 18-05-07 The following submissions have been made:-

Flow meter at inlet & outlet of STP are in working condition.                            

Treated effluent is being used for irrigation at the plant and possibility is being explored for its use by DDA or other Civil Agency.

Possibility is being explored for installing mechanical sludge dewatering system at the plant.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Renewal of the consent granted with clear condition that the plant shall operate properly and efficiently.
Action taken report

Consent issued on 07.11.2007.
Decision of CMC taken on 09.01.2008

No action.
Action taken report

No action. Applied for renewal of consent on 3-1-2008.
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 17.12.2007) except BOD (33 mg/l), other parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 24.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to be Member (Drainage) for seeking affidavit for the reasons of low intake quantity of sewage & under utilization of STP capacity (only 10 MGD). 
Action Taken Report

Letter issued on 26.03.2008. 

Unit has submitted its reply along with an affidavit on 11.04.08 & informed that the supply of clear water in the area is less due to non commissioning of Bawana Water Treatment Plant. Moreover, there is less habitat in the area further decreasing sewage in the catchment area. Nearby villages sewer is also un-trapped due to non availability of sewage systems. However, all the sewage coming to STP is full treated without by-passing any sewage. It is not proposed to lay sewer system in nearby villages. Also laying of sewerage system in nearby colonies is in progress. All about efforts may increase intake flow  to the STP  and will improve utilization capacity of STP.

Contd..2..

..2..

Narela STP (10 MGD)

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 25.03.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

OKHLA STP , [Phase- I, II, III & IV, (12+30+37+45), Total 124 MGD) ]

Consent Status 

Consent to operate was granted by CPCB on 23.01.1987 (valid upto 31.12.88), 

Applied on 03.04.1998 issued by DPCC on 14.06.99 (valid upto 31.05.2000), 

Applied on 10.05.2000 issued by DPCC on 18.04.2001 (valid upto 17.04.2002).

Applied on 08.10.2002 issued by DPCC on 20.01.2004 (valid upto 17.04.2005).

Applied for renewal on 10.03.2005 for Phase I, II, III & IV Plant (124 MGD) and yet to be decided. 

Applied for renewal on 10.03.2008 for phase-I (12 MGD) plant (ID No. 25118).

Applied for renewal on 10.03.2008 for phase-II (30 MGD) plant (ID No. 25120).
Applied for renewal on 10.03.2008 for phase-III (37 MGD) plant (ID No. 25117).
Applied for renewal on 10.03.2008 for phase-IV (45 MGD) plant (ID No. 25119).
Decision taken  

Issue SCN giving last opportunity to remove the deficiencies observed during inspection
Action taken report

SCN issued on 15.2.2007. Reply received on 26-03-07. The following submissions have been made:-

· Magnetic flow meter is not feasible. Ultrasonic flow meter also did not work due to deposition of sludge /plastic floating material on probes of the meter.

· Wrt renovation of sludge drying beds, necessary action is being taken by construction division.

· The issue, of trapping of effluents flowing in the two drains passing through the plant, has not been addressed in the reply.

· The supply of effluents for irrigation after primary treatment suspended. The matter is under examination.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC taken on 19.10.2007

Unit has applied for renewal of consent but has not corrected all the deficiencies pointed out vide SCN issued on 15.2.07. Unit may be reminded to correct all deficiencies and only then consent will be granted.
Action taken report

Letter issued on 07.11.2007. No reply received.
Decision of CMC taken on 09.01.2008

SEE to inspect and put up in next CMC (MSW) meeting.
Action taken report
Inspected on 19-2-2008. 

No flow meters were installed with any of the four STPs. Aerators found operational. 

Bio-gas generated in STPs supplied to south Delhi area i.e. Lajpat Nagat, New friends colony, sukhdev Vihar etc. 

Effluents from different pump houses which is to STPs, no open drain carrying raw effluents seen in the premises. 

As enquired storm water drain(Harkesh Nagar Drain) is passing through STP, the said drain being storm water drain is not connected with STP. The drain leading to Madanpur Khadar is closed, being area is acquired by DDA. 

No bypass observed.  All the four STPs are connected to a common channels within the premises before discharge. 

As Informed about 10-15 MGD treated effluents is used for horticultures by CPWD. About 5MGD treated effluent to the also used by Jaitpur village for agriculture purposes. 
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 18.12.2007) all  parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 22.01.2007), all parameters are within the prescribed standard.
Contd..2..

..2..

OKHLA STP , [Phase- I, II, III & IV, (12+30+37+45), Total 124 MGD) ]

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter for installation of flow meter and TOC analyzer.

Sh. Aditya Narayan Singh will study the file & decision will be taken accordingly.  

Action Taken Report

 Letter issued on 03.04.2008. As decided on file, note of Sh. A. N. Singh is to be putup in next CMC. 
Now DJB has submitted separate application (4 applications) for renewal of consent for each phase of STP. 

Applied for renewal on 10.03.2008 for phase-I (12 MGD) plant (ID No. 25118).

Applied for renewal on 10.03.2008 for phase-II (30 MGD) plant (ID No. 25120).
Applied for renewal on 10.03.2008 for phase-III (37 MGD) plant (ID No. 25117).
Applied for renewal on 10.03.2008 for phase-IV (45 MGD) plant (ID No. 25119).
As per DPCC Analysis report, dated 18.03.2008 (sampling done on 03.03.2008), all parameters are within the prescribed standard. for Phase I, II, II & IV STPs.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 20.03.2008), all parameters are within the prescribed standard for Phase I, II, II & IV STPs.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Consent is renewed for all the four applications. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Okhla STP, (16 MGD)

Consent Status 

Consent issued on 21.09.05 & valid up to 02-12-07. Applied for renewal of consent on 17.012.07.
Decision taken  

_
Action taken report

Plant was inspected on 06.12.06. SCN dated 02.1.2007 was issued as number of deficiencies were observed. Plant  submitted reply with the following submissions:-

· Magnetic flow meter is not feasible in such type of STP’s. Ultrasonic flow meter also did not work due to deposition of sludge /plastic floating material on probes of the meter.

· Fourteen to sixteen aerators at a time are sufficient for generating effluent of desired quantity .However, all digesters and aerators have been made operational.

·  Presently, part of treated effluent is being used for horticulture purpose from this unit. 

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.
Decision of CMC taken on 19.10.2007

Unit has applied for renewal of consent but has not correct all the deficiencies pointed out vide SCN issued on 02.01.2007 

Unit may be reminded to correct all deficiencies and only then consent will be granted.

Action taken report

Letter issued on 06.11.2007. No reply received.
Decision of CMC taken on 09.01.2008

SEE to inspect and put up in next CMC (MSW) meeting.
Action taken report

Inspected on 19-2-2008. 

Ultrasonic flow meters installed at inlet and outlet of STP found of functional. 

Aerators found operational and sludge digesters are in use.

TOC analyzer installed at outlet of STP however found non-operational condition as informed TOC analyzer is not in use for last few moths due to non-availability of its chemicals and non-maintenance by supplier of TOC analyzer. 

Bio-gas generated in STPs supplied to south Delhi area i.e. Lajpat Nagat, New friends colony, sukhdev Vihar etc. 

This STP is connected with other four STPs to a common channels within the premises before discharge. 

As Informed about 10-15 MGD treated effluents is used for horticultures by CPWD. About 5MGD treated effluent to the also used by Jaitpur village for agriculture purposes. 

Applied for renewal of consent on 17.12.07
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 18.12.2007) all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 22.01.2007), all parameters are within the prescribed standard.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter for non functioning of TOC analyzer.
Sh. Aditya Narayan Singh will study the file & decision will be taken accordingly.  

Action Taken Report

 Letter issued on 01.04.2008. Submitted reply on 21.04.08 in response to our letter dated 01.04.08, informing that TOC Analyzer is in working order and copies of reports are enclosed.  

Contd..2..

..2..

Okhla STP, (16 MGD)

As decided on file, note of Sh. A. N. Singh is to be putup in next CMC. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 03.03.2008), all parameters are within the prescribed standard for Phase V STPs.

As per DPCC Analysis report, dated 09.04.2008 (sampling done on 20.03.2008), all parameters are within the prescribed standard for Phase V STPs.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Consent is renewed. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

STP at C-DOT Campus, Chattarpur, Mehrauli, New Delhi-30. ((125 KLD)

Consent Status 

Consent to operate expired on 12.4.2007.

 Applied for renewal of consent on 11.03.2008 vide ID No. 25144. 

Decision taken  

-
Action taken report

A letter was issued on 26.06.2007, to  submit the consent application, but no reply/consent application received.

Decision of CMC taken on 19.10.2007

Unit may be asked to apply for renewal of consent. 

SEE to inspect. 

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Inspected on 04.01.2007. Sewage of office complex is being treated in STP. Most of the treated effluent is being used for horticulture purposes in complex. Flow meter at inlet not installed. Chlorination not done as feeding pump is out of order. Requested for one month time for submission of desired details.(i.e. consent application)
Decision of CMC taken on 09.01.2008

A letter for deficiencies be sent to unit and put up in next CMC (MSW) meeting.
Action taken report

Letter issued on 12.02.08. Reply received on 28.02.08.

Analysis report not received from DPCC laboratory so far.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue letter to apply for renewal of consent & to submit affidavit w.r.t. correction of deficiencies with in one month.

SSO(Water) to ensure that she will do the monthly monitoring of all CETPs & STPs and submit the test report before the CMC(MSW) meeting.

Action Taken Report

 Letter issued on 26.03.2008. Unit has submitted reply on 24.04.208. Applied for renewal of consent on 11.03.2008 vide ID No. 25144. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.2008), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 09.04.2008 (sampling done on 28.03.2008), all parameters are within the prescribed standard.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

Consent is renewed. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Holambi Kalan STP, (2 MLD)
Consent Status 

Consent issued on 14.05.04 & valid upto 08.10.06.Not applied for renewal of consent.
Decision taken  

Copy o f the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-07 to instruct the officials concerned to apply for the renewal of consent.
Action taken report

Copies of the letters/SCN issued on 01-11-2006 & 29-11-2006 handed over during CMC meeting held on 21-02-07. Consent issued on 14.05.04 & valid upto 08.10.06.

Decision of CMC taken on 19.10.2007

Unit may be asked to apply for renewal of consent. 

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Letter issued on 07.11.2007. No reply received . 

Not applied for renewal of consent.
Decision of CMC taken on 09.01.2008

Issue reminder letter.
Action taken report

Letter issued on 12.02.08. No reply received.

Analysis report not received from DPCC laboratory so far.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue final reminder letter to concerned EE with the copy to Addl. Commissioner (MCD) to applying for renewal of consent. 

SSO(Water) to ensure that she will do the monthly monitoring of all CETPs & STPs and submit the test report before the CMC(MSW) meeting.

Action Taken Report

 Letter issued on 25.03.2008. Ex. Engineer (S) DDI, MCD has submitted reply on 04.04.08, informing that the STPs at Tikri Khurd and Holambi are non-operational due to some administrative reasons and he is  making all his efforts to make it operational and to hand over these STPs to DJB. Further, requested for three months time for this process.

As per DPCC Analysis report dated 18.03.2008, STP was non operational.
As per DPCC Analysis report, dated 09.04.2008 STP was non operational.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

To take up with DJB in July, 2008 and ask the unit to apply for renewal of consent. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Bakkarwala STP, (3 MLD)
Consent Status 

Consent issued on 12.02.08 and valid up to 20.05.2010.
Decision taken  

Copy of the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-07 to instruct the officials concerned to apply for the renewal of consent.

Action taken report

Copies of the letters/SCN issued on 01-11-06, 29-11-06 handed over during CMC meeting held on 21-02-07.  Previous Consent valid upto 12.06.06. 

Plant has submitted consent application for renewal of consent on 21-05-07 with self analysis report.

Decision of CMC taken on 19.10.2007

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Inspected on 04.01.2008.
Decision of CMC taken on 09.01.2008

Consent granted.
Action taken report

Consent issued on 12.02.08.

Analysis report not received from DPCC laboratory so far.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

SSO(Water) to ensure that she will do the monthly monitoring of all CETPs & STPs and submit the test report before the CMC(MSW) meeting.

Action Taken Report

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 28.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 31.03.2008), all parameters are within the prescribed standard.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Molar Band STP (3 MLD)
Consent Status 

Consent issued on 12.02.08 and valid up to 20.05.2010.
Decision taken  

Copy of the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-2007 to instruct the officials concerned to apply for the renewal of consent.
Action taken report

Copies of the letters / SCN issued on 01-11-2006 & 29-11-06 handed over during CMC meeting held on 21-02-2007.  Previous Consent valid upto 12.06.06. 

Plant has submitted consent application for renewal of consent on 21-05-2007 with self analysis report.

Decision of CMC taken on 19.10.2007

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Inspected on 04.01.2008.
Decision of CMC taken on 09.01.2008

Consent granted.
Action taken report

Consent issued on 12.02.08.

Analysis report not received from DPCC laboratory so far.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

SSO(Water) to ensure that she will do the monthly monitoring of all CETPs & STPs and submit the test report before the CMC(MSW) meeting.

Action Taken Report

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 19.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 28.03.2008), all parameters are within the prescribed standard.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

 Tikri Khurd STP (2 MLD)
Consent Status 

Consent expired on 12.06.06. Not applied for renewal.

Decision taken  

Copy o f the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-07 to instruct the officials concerned to apply for the renewal of consent.

Action taken report

Copies of the letters/SCN issued on 01-11-2006 & 29-11-06 handed over during CMC meeting held on 21-02-07. Previous Consent valid upto 12.06.06. Letter issued on 29.11.06 for seeking consent application for renewal. No application for renewal of consent received.

Decision of CMC taken on 19.10.2007

Unit may be ask for apply to renewal of consent. 

SEE to inspect. MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Visited on 03.01.2008. Premises of STP found locked. As per information gathered from nearby residents, STP is non operational & locked from last 8-10 months.
Decision of CMC taken on 09.01.2008

MS may write to Dy. Commissioner, MCD Narela Zone asking for reasons of closing and details about when STP will restart. Copy to Slum & JJ Deptt, MCD
Action taken report

Letter issued on 12.02.08. No reply received.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to Sh. Naresh Kumar, Addl. Commissioner (MCD) through Chairman, DPCC giving details of previous letters.

Action taken report

Letter issued on 25.03.2008. Ex. Engineer (S) DDI, MCD has submitted reply on 04.04.08, informing that the STPs at Tikri Khurd and Holambi are non-operational due to some administrative reasons and he is  making all his efforts to make it operational and to hand over these STPs to DJB. Further, requested for three months time for this process.

As per DPCC Analysis report dated 18.03.2008, STP was non operational.
As per DPCC Analysis report, dated 09.04.2008 STP was non operational.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

To take up with DJB in July, 2008 and ask the unit to apply for renewal of consent. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Ghitorni STP,  (5 MGD)
Consent Status 

Not applied for consent.

Decision taken  

CE, DJB was asked to apply for consent, who agreed to do the needful.
Action taken report

No application for consent received.

As per DJB, plant will be commissioned by Dec. 2007. 

Decision of CMC taken on 19.10.2007

Unit may be ask for apply to renewal of consent. 

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs..
Action taken report

Visited on 08.01.2008. Premises of STP found completely dry & non operational. As per information gathered from nearby residents & security person of STP, it  is non operational from last many years. A letter recd from DJB informing that Gitorni STP is yet to be commissioned by DJB after the raw sewage is made available by DDA at the plant. Consent will be submitted to DPCC after operation of plant.

Decision of CMC taken on 09.01.2008

MS to write Member (drainage), DJB to give reason for not operating the STP for a long time even the sewage is generated from the surrounding area.
Action taken report

Letter issued on 12.02.08. No reply received.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue reminder letter to Member (Drainage) by Member Secretary, DPCC.  
Action Taken Report

 Letter issued on 26.03.2008. A letter received oj 26.03.08 from S.E., DJB informing that this STP is not working due to non availability of raw sewage for which the network is to be laid by DDA and requested that matter may be taken up with DDA for laying of network, so that this STP is made functional.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

The STP is not getting adequate water as per the installed capacity. As per the inspection report it was found that there is lack of coordination between DJB and DDA for getting adequate water at STP. Issue letter to both DJB and DDA that they make best possible efforts to ensure that the capacity of the STP plant is better utilized in pubic interest. 
Call the Ex. Engineer of South Zone from DJB & DDA in next CMC (MSW) meeting. 

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

STP at National Bureau of Plant Genetic Resources ICAR, Pusa Campus, (80 KLD)
Consent Status 

Consent expired on 07.06.07. Not applied for renewal of consent.

Decision taken  

-
Action taken report

Consent to operate expired on 07.06.2007, and not applied for renewal of consent.

A letter was issued on 26.06.2007 to submit the consent application, but no reply/consent application received.

Decision of CMC taken on 19.10.2007

Unit may be ask for apply to renewal of consent.

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Inspected on 03.01.2008. During inspection it was found that sewage of institute received at STP is directly goes to the final sump though screen. Sewage was not passed through other units of STP. From the final sump, sewage is pumped out in the near by outlet drain for discharge. No dry/wet sludge observed at site.

Neither applied for renewal of consent nor submitted reply of letter.

Decision of CMC taken on 09.01.2008

MS to write Director General,  PUSA regarding non operation of STP and that the effluent be discharge only after proper treatment.
Action taken report

Letter issued on 12.02.08. Reply awaited.

Analysis report not received from DPCC laboratory so far.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to Joint Secretary, ICAR with copy to Director General, PUSA through Chairman, DPCC.

SSO(Water) to ensure that she will do the monthly monitoring of all CETPs & STPs and submit the test report before the CMC(MSW) meeting.

Action taken report

Letter issued on 04.04.2008. As desired by Chairman, matter was discussed with Dir. General of PUSA by Member Secretary, DPCC and asked to apply for renewal of CTO and Compliance report before 12.5.08 .  He told that STP is looked after by CPWD but he will instruct them  for compliance.    
As per DPCC Analysis report dated 18.03.2008, STP was non operational.
As per DPCC Analysis report, dated 09.04.2008 STP was non operational.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Ask the unit to give reasons for non operation of STP by 30.06.2008 positively. 
Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

STP at BSNL, CTO Project, Mathura Lane, Janpath, New Delhi.
Consent Status 

Not applied for consent.

Decision taken  

-
Action taken report

Plant has submitted a letter dt 30-05-2007 & requested to provide acceptable standard.

A letter was issued on 03.07.2007 to submit application for consent to establish/operate. But no reply received in this regard
Decision of CMC taken on 19.10.2007

Unit may be ask for apply to renewal of consent.

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

STP found non operational condition. Filter press found dry. No dry or wet sludge found. STP is installed only for office complex. As reported, office has no canteen & STP is yet to be commissioned. However all pipe fittings etc found installed. No flow meter installed at inlet/ outlet of STP. Sewage collected in STP is being pumped outside without any treatment.

A reply has been received on 07.01.08 informing that the process for submitting the consent application of STP is in process & it is likely to be submitted within one month time.

Decision of CMC taken on 09.01.2008

MS to write a letter MD, BSNL for rectification of deficiencies and to ensure the operation of STP.
Action taken report

Letter issued on 12.02.08. No reply received.

Analysis report not received from DPCC laboratory so far.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

MS to speak with MD, BSNL & sort out the matter. 

Action Taken Report

MS has talked to Sh. Goel, MD, BSNL on 02.04.2008 and . 

Unit has submitted reply, however, Consent application not received so far.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

EE, MSWM to inspect and report by 30.06.2008.

Chairman
     M. S.       Prof. S.K Gupta

SEE
Dr. Chetna Harjai

EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Wazirabad Water Treatment Plant, Wazirabad

Consent status:

Not applied for consent under Air & Water Acts. 

Decision of Committee taken on 19.10.2007

Committee has also decided that other two units i.e Wazirabad Water Works & Chandrawal Water Works be also asked to apply for consent to operate under Air & Water Acts.

Action Taken Report

Letter for seeking consent to operate under Air & water Acts issued on 07.11.2007. No reply received so far.

DPCC analysis report
As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water.
Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Reminder letter may be issued.

Action taken report

Letter issued on 12.02.2008. No reply received.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue final reminder letter. 

Action Taken Report

Final reminder letter issued on 27.03.2008. Reply received on 11-4-2008 wherein it is mentioned that the matter is under process for submitting the application under Air& Water Act.

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:

Ask the unit to apply for consent to Establish under Air & Water Act. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
     Member (Env. Deptt.)
MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Chandrawal  Water Treatment Plant, Chandrawal

Consent status:

Not applied for consent under Air & Water Acts. 

Decision of Committee taken on 19.10.2007

Committee has also decided that other two units i.e Wazirabad Water Works & Chandrawal Water Works be also asked to apply for consent to operate under Air & Water Acts.

Action Taken Report

Letter for seeking consent to operate under Air & water Acts issued on 07.11.2007. No reply received so far.

DPCC analysis report
As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Reminder letter may be issued.

Action taken report

Letter issued on 12.02.2008. No reply received.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue final reminder letter. 

Action Taken Report

Letter issued on 27.03.2008. Reply not received.

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:

Ask the unit to apply for consent to Establish under Air & Water Act. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Haiderpur  Water Treatment Plant, Haiderpur

Consent status:

Applied for consent to operate on 13.02.2008.

Decision of Committee taken on 19.10.2007

Unit may be ask for apply for consent to operate.  MS to direct lab officials of DPCC to do regular monthly lab testing for drinking water standards.
Action Taken Report

Letter for seeking consent to operate under Air & water Acts issued on 07.11.2007. No reply received so far.

DPCC analysis report
As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Reminder letter may be issued.

Action taken report

Letter issued on 12.02.2008. Applied for consent to operate on 13.02.2008.
As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.
· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Member Secretary, DPCC to inspect & report in April CMC(MSW). 

Action taken report

Plant was inspected on 08-05-2008 by Member Secretary.

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:

Ask the unit to apply for consent to Establish under Air & Water Act for both its old & new units. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Nangloi Water Treatment Plant, Nangloi

Consent status:

Not applied for consent under Air & Water Acts. 

Decision of Committee taken on 19.10.2007

Unit may be ask for apply for consent to operate.  MS to direct lab officials of DPCC to do regular monthly lab testing for drinking water standards.
Action Taken Report

Letter for seeking consent to operate under Air & water Acts issued on 07.11.2007. No reply received so far.

DPCC analysis report
As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Reminder letter may be issued.

Action taken report

Letter issued on 12.02.2008. No reply received.

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue  reminder letter for reply. 

Action Taken Report

Letter issued on 27.03.2008. Received application for consent to operate through Post on 29-4-2008 which is not complete(less consent fee, trade effluent generated but no treatment method mentioned), Demand Draft is yet to be detatched.

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:

Ask the unit to apply for consent to Establish under Air & Water Act at Enquiry Counter of DPCC and application for Consent to operate to be returned back to the unit in original with fee draft. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Sonia Vihar Water Treatment Plant, Sonia Vihar

Consent status:

Consent to operate granted on 13.03.2007. 

Decision of Committee taken on 19.10.2007

Ask the unit to compliance report of consent condition. MS to direct lab officials of DPCC to do regular monthly lab testing for drinking water standards.  

Committee has also decided that  other two units i.e Wazirabad Water Works & Chandrawal Water Works be also asked to apply for consent to operate under Air & Water Acts.

Action Taken Report

Letter for seeking compliance report of consent to operate under Air & water Acts issued on 06.11.2007. 

Reply received on 02.01.2008.

DPCC analysis report
As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water except Hardness ( as CaCo3-360mg/l ).

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

No action.

Action taken report

No action. 

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

No action. 

Action Taken Report

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Bhagirathi Water Treatment Plant, Near Waziradad, Delhi   

Consent status:

Not applied for consent under Air & Water Acts. 

DPCC analysis report
As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water).

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Issue letter for asking to apply for consent under Air & water Acts.

Action taken report

Letter issued on 13.02.2008. No reply received. 

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Issue  reminder letter. 

Action Taken Report

Reminder letter issued on 27.03.2008 to apply for consent to operate. Submitted reply on 22.04.2008, that this office shall formally apply for consent shortly and also raise the query that the fee for Air Act is required to be paid or not. 

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2008:

Ask the unit to apply for consent to Establish under Air & Water Act at Enquiry Counter of DPCC and clarify his point for fee. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
Member (Env. Deptt.)

MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Remarks:
A letter has been received from Central Pollution Control Board (Copy enclosed) regarding installation of Continuous online TOC analyzer for bulk monitoring of CETP /STP. 

Letters have also been sent to the Member Secretaries of Andhra  and Tamil Nadu  Pollution Control Pollution Board wherein they were requested to mention the cost of the TOC analyzer being installed at STPs and to clarify the standards prescribed for TOC of STP treated waste water. However no reply has been received from the concerned officials.

Decision of Consent Management Committee in its meeting dated 09.01.2008 :

Member Secretary, DPCC may write to Member Secretary, CPCB for the financial assistance of TOC analyzer which shall be installed at the CETP/STP as the TOC analyzer will be installed first time in the case of CETP. 

Action Taken Report

Letter issued on 20.02.2008. 

· Decision of Consent Management Committee in its meeting dated 29.02.2008:

Letter to Chairman, CPCB through Chairman, DPCC.

Action Taken Report

 Letter issued on 15.04.2008. In response of letter dated 20.02.08, Additional Director, CPCB vide his letter dated 02.04.08, has informed that there is no provision in CPCB funds for providing such a support.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

A letter may be made by MS to Member (Drainage) to TOC analyzer costing about Rs. 14 Lakh.

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
     Member (Env. Deptt.)
MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Representation received from M/s Sanjay Enterprises regarding re-generation and reuse of activated carbon in CETPs.

M/s Sanjay Enterprises has submitted the representation on behalf of M/s Industrial Carbon (P) Ltd. regarding technology available for re-generation and reuse of activated carbon for the CETPs installed in Delhi. The brief of the proposal is as under:

8. Normal life of activated carbon in ACF of CETP is approximate 21 days. The re-generation facility is not established in Delhi so far.

9. All over the world, activated carbon is re-generated and reuse and fresh carbon is used only for topping up.

10. Why need of re-generation:

Cost of fresh activated carbon is very high i.e.

60 MT (in 1 CETP) x Rs. 55000 (Per MT) + Taxes = approx 40 Lacs for every 21 days for each CETP

660 MT carbon is not made in India in every 21 days and we have to import and spend our foreign currency

Space is required for storing all the exausted carbon in dry cool place for 20 years or spend money for its incineration.

11. A facility of re-generation should be established as joint venture with Delhi state or we shall set up the total unit but land is to be provided by you in any of the CETPs or any other suitable place, land and building with electrification and water connection shall be your scope

12. Only after such facility is established successful use of ACF becomes economical a perfectly treated water which meets pollution control norms is as pure as ground water and can be used for all practical purposes except human drinking application 

13. By selling treated water and income of approximate 3 crore can be generated from which only 10% may go for cost and saving of Rs. 2.7 crore/ day is  visualized. 

14. They have already submitted their proposal for re-generation plant to Chief Engineer DSIIDC, Commissioner (Plg.), DDA etc.  

Sh. J. M. Chaturvedi & Sh. Rohit Kumar Madhavji visited this office on 16.04.08 and explain the proposal before the SEEs and other officials.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

Ask the unit to go to concerned CETP for marketing. 
Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
     Member (Env. Deptt.)
MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

The cases pending before Hon’ble Supreme Court commonly known as Maily Yamuna,  

This file contains some copies of the orders passed by HSC as well as affidavits filled by some govt. authorities. Chairman, DPCC vide note dated 11.04.08 directed to put up the matter in CMC (MSW) this month.

Hon’ble Supreme Court on the basis of one newspaper clipping published in HT times on 18.07.94 Ceased of the matter wrt water quality of river Yamuna. 

Hon’ble Supreme Court time and again directed to all the govt. authorities to make the water quality of at least ‘C’ level. i.e. useful for bathing. 

During pursuance of the various orders, the order dated 13.09.99 and 27.08.99 the Hon’ble court has ordered that “with effect from 1st Nov. 1999, no industrial effluent would be allowed to discharge directly or indirectly into the river Yamuna” may be referred and needs to be examine. 

As per the note of ALO dated 09.04.08 as such there is no directions for implementation is pending on part of DPCC, however Hon’ble court was not satisfied with implementation of various orders despite promises and assurances given to the court for improving the quality of water of river Yamuna.

Subsequent, to the filing of the affidavit by the Principal Secretary (UD) in pursuance of order dated 12.04.05 Hon’ble court has directed to set up the STP at the mouth of he drains meeting the river Yamuna so as to clean it like river Thames. 

The next date of hearing is 08.07.08. 

Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
     Member (Env. Deptt.)
MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

Inviting proposal for establishment of Common Effluent Treatment Plants
A letter dated 15.04.2008 has been received from the Joint Secretary, Ministry of Env. & Forest, Govt. of India inviting proposal for establishment of Common Effluent Treatment Plants along with necessary documents after coordinating with State Environment Department, so that proposal  may be considered for senction of Central subsidy during the financial year 2008-09, for which funds have been provided. 

A letter dated 16.08.2007 on the same matter has also been received from MoEF (copy enclosed). As decided, reply was sent to the Jt. Secretary, MoEF on 11.10.07  (copy enclosed) informing that out of 15 proposed CETPs, at present 10 CETPs are in operation in different industrial areas of Delhi. DSIIDC was the agency for construction of all the 10 CETPS installed so far. Industries Department, Govt of Delhi is the nodel agency for the implementation of CETP Act. Hence DSIIDC may be asked to submit the proposal of setting up of CETP as per the scheme of the MoEF, Govt. of India. 

Decision of Consent Management Committee in its meeting dated 12.05.2008:

There are 10 industrial areas which are still do not have CETP. The letter can also be forwarded to the DSIDC for writing to MOEF. Accordingly draft to JS, MOEF may be put up. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
     Member (Env. Deptt.)
MSWM Cell

Decision of Committee (MSWM) taken in its meeting dated 12.05.2008

6th quarterly review meeting convened by the Chief Secretary, Delhi in compliance of the order of the hon’ble Supreme Court in case No. CWP/725/1994Captioned “AND QUIET FLOWS THE MAILY YAMUNA Vs. CPCB & ORS was held on 10.03.2008. The discussion held with various stakeholders is as under:-
(B) Delhi Jal Board

Action Taken/ Target:-

· In so far as rehabilitation of trunk sewers is concerned, presently the main trunk sewers carrying sewage to the Sewage Treatment Plants are choked due to siltation and settlement at some locations. Due to this, the entire sewage is not reaching the Sewage Treatment Plants. Due to mal functioning of these trunk sewers, there is back flow of sewage in the area. To give relief to the residents, dewatering pumps (trolleys) have been installed temporarily at required locations which pump out the sewage into the drains. Hence, some quantity of sewage is flowing into the drains which should have been flowing into the sewerage network Hence, no sewage will be flowing into the drains after rehabilitation of these sewers. This exercise will be done by Consultant within 6-9 months. Hence for design purpose the scenario of 2009 when the entire reach of trunk sewers will be desilted and set right, will be considered while designing the size of the sewer i.e. part of para 38 (a), (b) & (c) of the Expert Committee report. This analysis does not have to wait till the completion of the actual rehabilitation work of trunk sewers. 
· The interceptor sewer concept comprises the following components:-

a. Laying of interceptor sewers along three major drains of Irrigation & Food Control Department (i.e. Najafgarh, Supplementary and Shahdara).

b. Augmentation of the existing capacity of Sewage Treatment Plants at the mouth of Delhi Gate drain and Dr. Sen Nursing Home Drain.

c. Intercepting 13 small drains into Bela Road and Ring Road Trunk sewer after rehabilitation. 

d. Construction of additional Sewerage Treatment Plants after utilization of full capacity of existing plants.

Out of above 4 components, EIL has been entrusted the first component only whereas remaining 3 components shall be done by DJB and completed by 2009.

· EIL will prepare the schemes in various phases. There are 3 major drains; Najafgarh, Supplementary and Shahdara which carry part of untreated sewage and discharges into river Yamuna. Supplementary and Najafgarh drain meet with river Yamuna just on the down stream of Wazirabad barrage and thus, river Yamuna carries water mixed with sewage through entire reach of Delhi of 22 Kms. The Shahdara drain meets river Yamuna down stream of Delhi.

· It is proposed to target these 2 drains in phase-I so that entire reach within Delhi is improved in terms of quality of river water before the Commonwealth Games. Delhi Jal Boards’s works in respect of component No. 2, 3 & 4 above are also to be completed before 2010. Thus the maximum improvement in river quality will be achieved by 2010. However, the work of Shahdara drain will be concurrently done and efforts will be made to complete the work of Shahdara drain latest by 2012. M/s EIL has assured of necessary feedback by 15th June, 2008 so that revised affidavit could be filed in the Hon’ble Supreme Court. M/s EIL has submitted the timeline which are enclosed with the minutes of the meeting dated 10.03.2008.

Contd..2..

..2..

2. Work related to Abatement of Pollution in River Yamuna:
(a) Laying of Interceptor sewers comprising following components :

The Project Management Consultancy work has been awarded to M/s Engineers India Ltd., The work is scheduled to be completed by December 2012 which includes planning work to be completed within 12 months. The work has been divided into two phases :-

Phase-I :  Laying Interceptor sewer along Najafgarh & Supplementary drain, shall be completed by 2010.

Phase-II :  Laying of Interceptor sewer along Shahdra drain, shall be completed by 2012.

The tenders on Design Build, Operate basis shall be invited after getting assessment of quantum of flow into Delhi Gate & Dr. Sen Nursing Home drains and quality parameters of the sewage flowing into the drains. The work shall be completed by Dec. 2009

Balance 13 drains shall be intercepted into Bela Road and Ring Road Trunk sewers which are being rehabilitated and completed by December 2009. The sewage shall be conveyed to Okhla Sewage Treatment Plant.


The capacity of the existing plants shall be augmented after their full utilization.
(b) Refurbishment of Sewage Treatment Plants, Pumping Stations and Trunk sewers.

Delhi Jal Board has already awarded the works of Rehabilitation of 50 kms Trunk Sewers which will be completed by December 2009. Simultaneously, existing identified Sewage Pumping Stations and Sewage Treatment Plants are also being rehabilitated.

(c) Augmentation of Capacity of existing Sewage Treatment Plants to meet the demand of the growing population.

Capacity of Kondli, Yamuna Vihar & Okhla Sewage Treatment Plants is being augmented by 45, 25 & 30 MGD respectively by December 2009.

(d) Sewering of unsewered area:
v. All the 44 resettlement colonies have been sewered. 

vi. Out of 567 U/A-regularized colonies, sewers laid in 523 colonies. In the remaining colonies, work is in progress in a phased manner.

vii. Out of 135 urban villages, sewers laid in 107 villages. Work in progress in the remaining urban villages in phased manner. 
viii. Administrative approval for laying sewerage system in 27 villages has already been accorded. Allotment of land for construction of STP/WSP/SPS is being processed by Revenue & Land & Building department. Lands at 15 locations of Gram Sabha have been finalized. The work has been awarded for laying sewerage system in sixteen villages and in future villages tenders are under process of award for work.. 
Contd..3..

..3..

Irrigation & Floor Control Department :
Action taken/ Target

1. The work of construction of around 34 Kms boundary wall on both sides of Najafgarh drain within the habitation area is in its full swing. The boundary wall on upstream side of Kakrola is not being constructed as there is hardly habitation area. The work shall be completed by August 2008.

Similarly, 30 Kms stretch of boundary wall along Supplementary drain shall be completed by August 2009.

Boundary wall along Shahdra drain is already constructed. 

2. The joint inspection of MCD & Irrigation & Floor Control was carried out at all outfall structures ….

It was decided that all the outfall structures shall be revamped / maintain by Irrigation & Flood Control department as a deposit work on behalf of MCD.

3. The list of 85 bridges and action plan for providing M.S. nets shall be provided by them.

4. The work of Forestation along major drains shall be got done with the help of Ministry of Environment & Forest, Govt. of NCT of Delhi. 

5. It was further emphasized upon to do regular desilting and channelizing the drains to maintain the flow. The cunnette must also be provided in all the drains to take care the dry weather flow. The plantation / a forestation on the banks of major drains must be encouraged to prevent the scouring during rains. 
 MCD

6. Joint Inspection of MCD drains and their out fall structures. 

The joint inspection had already carried out with Irrigation & Flood Control Department and report submitted with Urban Development department. MCD requested to get revamped and channelize all the out fall structures by the department of Irrigation & Flood Control department.

7. Construction of Boundary walls along 16 drains under their jurisdiction. 
MCD has identified the vulnerable locations for construction of boundary wall within habitation area where chances of garbage dumping is more. However, after constructing boundary wall, the difficulty in desilting of drains will arise.

8. Plantation along drains 

It was emphasized to take similar action by MCD as that of Irrigation & Flood Control department.

9. Legal Action against defaulters
Challans have been done against the defaulters who were caught littering or dumping garbage into drains.

10. Awareness Program
MCD intimated that they are launching awareness program to educate the people not to through garbage into drains and Yamuna River.
The Chief Secretary directed to submit the photographs of such points where MCD is doing the work in respect of cleaning River Yamuna. 

Contd..4..

..4..

Slum & J.J. Department of MCD
Action taken/ Target

4. It was intimated that Slum and J.J. department is implementing plan scheme of Relocation of J.J. Clusters on the request of various departments like DDA, PWD, GAIL etc.

5. They intimated that no fresh formal request has been received from any of the department to remove jhuggis from the bank of drains.

6. They are requesting Govt. to  allot more land for shifting of Jhuggis.

DDA
Action taken/ Target

The representative of DDA informed that they have already removed the clusters from the bank of River Yamuna except for Batla house, Bodh Vihar and Majnu Ka Tilla where the matter is pending in the Court. However, the Chief Secretary directed to submit the latest status in this respect.

 DSIIDC

Action taken/ Target

· 10 CETPs constructed and 9 handed over to respective societies for operation.

· 1 CETP at Naraina Industrial Area is under construction and completed by July 2008.

· Balance four CETPs at Anand Parbat, Mohan Cooperative, Okhla Industrial Estate and Najafgarh Road are kept in abeyance as per the directions given in EPCA report submitted to the Hon’ble Supreme Court. The decision of the Hon’ble Supreme Court is still awaited.

· Treated water from these CETPs is meeting with the EPA standards and being discharge into drain. But Secretary (Env.) intimated that some Plants are not meeting the standard. 
Decision of Consent Management Committee in its meeting dated 12.05.2008:

No action. 
Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
     Member (Env. Deptt.)
MSWM Cell

Table Agenda: 

General Decision on the study of CETPs in Delhi

Dr. A. K. Neema, IIT may kindly be requested to file his report on CETPs by 30.06.2008 positively. Dr. Neema may be asked to inspect those CETPs also which were stopped by EPCA orders so that latest update is received on each of these CETPs. For this additional work one month additional time is granted to file supplementary report. 

Chairman
     M. S.       Prof. S.K Gupta

SEE

Dr. Chetna Harzai
EE
AEE 

   DPCC
    DPCC    Member (Acd. Inst)      (MSW) 
     Member (Env. Deptt.)
MSWM Cell

	 
	 
	 
	Consent under Air & Water Act
	Authorisation under MSWM Rules

	S. No.
	Name of  Project
	Operating Agency
	Date of Application 
	Consent issued on
	Consent validity
	Present status
	Date of Application 
	Auth. issued on
	Auth.  validity
	Present status

	1
	Revival of the Compost Plant of Municipal Corporation of Delhi at Okhla, Delhi.
	Municipal Corporation of Delhi and IL & FS 
	 
	29.01.08
	25.01.09
	Valid
	20.11.07
	 
	 
	Pending

	2
	Upgradation of the A.P.M.C. Compost Plant at Tikri Khurd/ Khampur, G.T. Karnal Road, Delhi-40.
	Spiral Services, New Sabzi Mandi, Azad Pur, Delhi-33.
	 
	29.01.08
	25.01.09
	CTE Valid. Applied for CTO on 04.03.08
	20.11.07
	 
	 
	Pending

	3
	Modern Poultry & Egg Market at Ghazipur, New Delhi.
	Delhi Agriculture Marketing Board, 9, Institutional Area, Pankha Road, Janakpuri, New Delhi-110058.
	24.01.08
	 
	 
	Pending
	_
	 
	 
	_

	4
	Municipal Waste Complex at Gazipur Bio-gas Plant Site
	M/s New Delhi Waste Processing Company Ltd.
	 
	03.07.07
	21.06.08
	Valid
	29.03.07
	 
	 
	Pending

	5
	 Delhi Food  Processing Complex (Meat), Slaughter House at Ghazipur, Delhi 
	Municipal Corporation of Delhi
	02.06.05
	 
	 
	Pending
	_
	 
	 
	_

	6
	Intigirated Municipal Solid Waste Complex, Timarpur, Delhi
	M/s Timarpur-Okhla Waste Management Co Pvt. Ltd.
	 
	25.09.07
	06.07.09
	Valid
	 
	09.03.07
	08.03.09
	Valid

	7
	NDMC Compost Plant Site, Near Okhla STP, Okhla, New delhi
	M/s Timarpur-Okhla Waste Management Co Pvt. Ltd.
	 
	03.07.07
	09.05.08
	Not applied for renewal.
	 
	09.03.07
	08.03.09
	Valid


	S. No.
	Name of CETP
	Date of Application 
	Consent issued on
	Consent validity
	Present status

	1
	Mayapuri Industrial Area
	07.05.07
	 
	 
	Pending

	2
	Mangolpuri Industrial Area
	 
	27.07.07
	 
	Valid

	3
	Badli Industrial Area
	 
	28.02.07
	28.12.09
	Valid

	4
	Wazirpur Industrial Area
	 
	23.02.07
	27.12.09
	Valid

	5
	Jhilmil Industrial Area
	 
	28.02.07
	07.01.10
	Valid

	6
	Nangloi Industrial Area
	27.06.07
	 
	 
	Pending

	7
	SMA Industrial Area
	11.04.07
	 
	 
	Pending

	8
	GTK Road Industrial Area
	 
	15.09.04
	27.07.07
	Not Applied for renewal.

	9
	Lawrence Road Industrial Area
	14.12.07
	 
	 
	Pending

	10
	Okhla Industrial Area
	13.02.07
	 
	 
	Pending

	11
	Narela Industrial Area
	03.03.06
	 
	 
	Pending

	12
	Najafgarh Road Industrial Area
	03.07.02
	 
	 
	Construction suspended

	13
	Naraina Industrial Area
	02.07.02
	 
	 
	Under construction by DSIDC

	14
	Okhla Industrial Estate
	06.07.02
	 
	 
	Kept in abeyance by EPCA

	15
	Anand Parbat Industrial Area
	05.08.02
	20.01.04
	19.01.05
	Kept in abeyance by EPCA

	16
	Mohan Co-operative Industrial Estate
	06.07.02
	 
	 
	Kept in abeyance by EPCA

	17
	Udyog Vihar (Bawana) Industrial Area
	05.08.02
	20.01.04
	19.01.05
	Not Applied for extention of Establish/  Consent to operate.


	S. No.
	Name of Power Plant
	Date of Application 
	Consent issued on
	Consent validity
	Present status

	1
	NTPC, BTPS, Badarpur
	 
	27.07.07
	21.03.10
	Valid

	2
	I P Thermal Power Station
	17.04.08
	 
	 
	Pending

	3
	Rajghat Power Station
	30.06.04
	 
	 
	Pending

	4
	Pargati Power Station, ITO
	18.12.07
	 
	 
	Pending

	5
	I. P. Gas Turbine Power Plant, ITO
	27.12.07
	 
	 
	Pending

	6
	NTPC, BTPS, Stage-III Expn, Badarpur, 
	05.02.07
	 
	 
	Pending

	7
	Combined Cycle Power Project, Bawana (Pargati Power)
	 
	19.03.07
	18.03.08
	Not applied for extention.

	S. No. 
	Name of WTP
	Date of Application 
	Consent issued on
	Consent validity
	Present status

	1
	Wazirabad Water Treatment Plant
	Not Applied
	 
	 
	Not Applied

	2
	Chandrawal Water Treatment Plant
	Not Applied
	 
	 
	Not Applied

	3
	Haiderpur Water Treatment Plant
	13.02.08
	 
	 
	Asked to apply for consent to Establish.

	4
	Nangloi Water Treatment Plant
	Appliaction for consent to operate returned in original.
	 
	 
	Asked to apply for consent to Establish.

	5
	Sonia Vihar Water Treatment Plant
	07.12.06
	13.03.07
	06.12.09
	Valid

	6
	Bhagirathi Water Treatment Plant
	Not Applied
	 
	 
	Not Applied

	S. No. 
	Name of STP
	Installed capacity
	Date of Application 
	Consent issued on
	Consent validity
	Present status

	1
	Dr. Sen Nursing Home
	2.2 MGD
	13.05.2008
	 
	 
	Pending

	2
	Delhi Gate
	2.2 MGD
	 
	15.02.07
	11.10.09
	Valid

	3
	Kondli Phase-I
	10 MGD
	19.04.06
	 
	 
	Pending

	4
	Kondli Phase-II
	25 MGD
	19.04.06
	 
	 
	Pending

	5
	Kondli Phase-III
	10 MGD
	16.11.07
	 
	 
	Pending

	6
	Oxidation pond (Nehru Vihar)
	6 MGD
	25.10.07
	 
	 
	Pending

	7
	Kesho pur 
	72 MGD
	07.01.08
	 
	 
	Pending

	8
	Mehrauli
	5 MGD
	 
	20.03.07
	15.12.09
	Valid

	9
	Yamuna Vihar Ph-I
	10 MGD
	25.10.07
	 
	 
	Pending

	10
	Yamuna Vihar Ph-II
	10 MGD
	 
	28.02.07
	28.12.09
	Valid

	11
	Rithala Ph-I
	40 MGD
	29.06.06
	 
	 
	Pending

	12
	Rithala Ph-II
	40 MGD
	20.01.06
	 
	 
	Pending

	13
	Pappan kalan
	20 MGD
	10.12.04
	 
	 
	Pending

	14
	Najafgarh
	5 MGD
	29.11.04
	 
	 
	Pending

	15
	Nilothi
	40 MGD
	26.11.07
	 
	 
	Pending

	16
	Rohini
	15 MGD
	01.05.07
	 
	 
	Pending

	17
	Coronation Pillar (Ph-I, II, III and old clarifier)
	40 (4 x 10) MGD
	 
	28.02.07
	12.03.09
	Valid

	18
	Vasant Kunj (Plant 1 & 2)
	5.2 MGD
	29.01.08
	 
	 
	Pending

	19
	Narela
	10 MGD
	03.01.08
	 
	 
	Pending

	20
	Okhla (Plant -I, II, III & IV)
	124  MGD (12+30+37+45)
	10.03.08
	May. 08
	09.03.11
	Valid

	21
	Okhla (Plant -V)
	16 MGD
	17.12.07
	May. 08
	16.12.10
	Valid

	22
	C Dot Campus (Mehrauli)
	125 kLD
	11.03.08
	May. 08
	10.03.11
	Valid

	23
	Holambi
	2 MGD
	 
	14.05.04
	08.10.06
	Not applied for renewal.

	24
	Bakarwala
	3 MGD
	 
	12.02.08
	20.05.10
	Valid

	25
	Molarband
	3 MGD
	 
	12.02.08
	20.05.10
	Valid

	26
	Tikri khurd
	2 MGD
	 
	 
	12.06.06
	Not applied for renewal.

	27
	Gitorni
	5 MGD
	Not applied
	 
	 
	Not applied

	28
	Pusa Campus
	29 MGD
	 
	 
	07.06.07
	Not applied for renewal.

	29
	CTO Project, Mathura lane, Janpath
	 
	Not applied
	 
	 
	Not applied



