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	DELHI POLLUTION CONTROL COMMITTEE

DEPARTMENT OF ENVIRONMENT, (GOVT. OF NCT OF DELHI)

4TH FLOOR, ISBT BUILDING, KASHMERE GATE, DELHI-6

visit us at : http://dpcc.delhigovt.nic.in




F.No.DPCC/MSWM/07/

                                            dated:

MEETING NOTICE

5th meeting of the Committee constituted for deciding consent under the Air and Water Acts, for CETPs, STPs, WTPs & Power Plants cases, will be held on 19.10.2007 at 03.00 PM in the Conference Room of Chairman, DPCC at Level 6, C Wing, Delhi Secretariat, New Delhi. 

You are requested to kindly make it convenient to attend the said meeting at the scheduled date and time.


Sr. Env. Engineer

Municipal Solid Waste Management Cell
1. PS to Chairman for the information of Chairman, DPCC.

2. Member Secretary, DPCC

3. Prof. S. K. Gupta, Head, Chemical Engg. Department, IIT, Hauz Kauz, New Delhi – 16. 

4. Sh. B. Kumar, SEE (MSWM), DPCC.
5. Sh. M. Dwarakanth, SSO, Dept. of Env,. GNCTD.
6. Env. Engineers (MSWM)

7. AEEs (MSWM – I & II)

Copy for information to:

1. Administrative Officer, DPCC – With the request to arrange a vehicle for picking and dropping Prof. SK Gupta from IIT, Delhi.

2. Accounts Officer, DPCC for payment of Rs. 1000/- to Prof. SK Gupta, IIT, Delhi for attending the said meeting.

Sr. Env. Engineer

Municipal Solid Waste Management Cell
Agenda for 5TH  CMC (MSW Cell) meeting to be held on 19.10.07.

A meeting of the Committee constituted for deciding the consent under the Air and Water Acts, for CETPs, STPs, WTPs & Power Plants cases, is scheduled to be held on 19.10.07.
Agenda 1 – Application for Empanelment of Laboratory of Sulabh International Academy of Environmental Sanitation. 

Agenda 2 - Cases of public grievance in respect of MSW. 

Agenda 3 - Cases of power plant w.r.t seven (7) power plants. 
Agenda 4 – Case of Municipal Solid Waste Management Project of one unit. 

Agenda 5 – Cases of CETPs – w.r.t 16 CETPs. 

Agenda 6 – Cases of STPs – w.r.t. 29 STPs. 

Agenda 7 – Cases of Water Treatment Plants –  w.r.t. 2 plants. 

Agenda 8 - Any other item with the permission of Chairman.
Minutes of the 5th meeting of the Committee Constituted for deciding the Consent under the Air and Water Acts, for CETPs, STPs, WTPs, MSW Projects & Power Plants cases, held on 19.10.2007 in the Conference Room of Chairman, DPCC.

   The following officers, attended the meeting on 12.10.2007

1. Sh. J. K Dadoo, Chairman, DPCC

2. Sh. K. Mahesh, Member Secretary, DPCC

3. Sh. S.K.Gupta ,Head Chemical Engineering Deptt.,IIT Delhi 

4. Sh. B. Kumar, SEE, DPCC

5. Sh. M. Dwarakanath, SSO, Deptt of Env., GNCTD 

6. AEEs (MSWM Cell)

Leave of absence was granted to EE (MSWM Cell), DPCC. 

The 5th meeting of the Committee constituted for deciding the Consent under the Air and Water Acts, for CETPs, STPs, WTPs, MSW Projects & Power Plants cases was held on 19.10.2007 and following decisions were taken in the meeting: 
Agenda 1- One Laboratory Case

CMC considered the application for empanelment of Sulabh International Academy of Environmental Sanitation and was rejected. As the laboratory is not reorganized under EP Act (1986) by MOE&F. 


Agenda 2- Cases of public grievance in respect of MSW 
I. A complaint has been received against the functioning of Wazirpur CETP which was considered by the committee. The committee felt that Member Secretary, DPCC to call the members of CETP Societies and direct them that: - 

a. All individual units must be directed to connect their units with the conveyance system with CETP by 31.12.07

b. CETP society must operate the CETP plant professionally, efficiently, effectively. 

II. The letter of Industrial Carbon Pvt. Ltd. was considered by the Committee and it was decided to forward it to all the11 CETPs and 29 STPs. 
Agenda 3 - Cases of seven power plants. 

All the 7 cases were discussed and decisions taken are annexed as Annexure – I.
Agenda 4 – 1 Case of Municipal Solid Waste Management Project and decisions taken are annexed as Annexure – II
Agenda 5 – 16 Cases of CETPs . 

All the 16 cases were discussed and decisions taken are annexed as Annexure – III.

.
Agenda 6 – Cases of  29 STPs.
All the 29 cases were discussed and decisions taken are annexed as Annexure – IV

Agenda 7 – Cases of  3 Water Treatment Plants. 

All the 3 cases were discussed and decisions taken are annexed as Annexure – V .
The next meeting is scheduled for second week of January 2008.
Meeting ended with thanks to the Chair.

*****
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	DELHI POLLUTION CONTROL COMMITTEE

DEPARTMENT OF ENVIRONMENT, (GOVT. OF NCT OF DELHI)

4TH FLOOR, ISBT BUILDING, KASHMERE GATE, DELHI-6

visit us at : http://dpcc.delhigovt.nic.in





F.No.DPCC/MSWM/2007   



      Dated: 
Subject:- Minutes of the 5th meeting of the committee constituted for deciding the Consent under the Air and Water Acts, for CETPs, STPs, WTPs, MSW Projects & Power Plants cases, held on 19.10.2007 in the Conference Room of Chairman, DPCC.


Please find enclosed herewith the minutes of 5th meeting of the committee constituted for deciding the Consent under the Air and Water Acts, for CETPs, STPs, WTPs, MSW Projects & Power Plants cases, held on 19.10.2007  in the conference room of Chairman, DPCC.

(B Kumar)

Sr. Env. Engineer

1. Chairman, DPCC
2. Member  Secretary, DPCC

3. Prof. S.K.Gupta , Head Chemical  Engineering  Deptt. ,IIT Delhi

4. Sh. Dwarakanath, SSO, Environment Department, GNCTD

5. EE and AEEs of MSWM Cell, DPCC.
Copy to:-

1. Incharge, Computer Cell, DPCC-for placing the aforementioned minutes of the committee on the Website of DPCC.
(B Kumar)

Sr. Env. Engineer
Agenda 2

I. WIA CETP – a complaint has been received against the functioning of CETP which was considered by the committee. The committee felt that Ms may called the member of CETP society and direct them that: - 

c. All individual unit must be persuaded to connect their connection with conveyance system with CETP by 31.12.07

d. CETP society must operate the CETP plant professionally, efficiently, effectively failing which a BG of amt. will be raised from 10 lakhs to 20 lakhs. 

MS may also warn all DPCC officials connecting to WIA to desist from any activity which prevents control of pollution effectively and comprehensively, after this warning the concerned officials will have to face penal action. 

MS may also may instruct DPCC lab officials not to do grab sampling but sampling should be done composite in case of CETP. In case of composite manner for all CETP and STPs. 

II. The letter of Industrial Carbon Pvt. Ltd. was examined by the committee and it was decided to forward it to all 11 CETPs and 29 STPs. 

Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Sl. No.
	Name
	Decision Taken on 26.06.2007
	Action Taken

	Decision


	1.
	Pragati Power Station , Bawana

	Issue consent to the unit for 1600 MW considering Environmental Clearance granted by MoEF for 1600 MW.


	Consent to establish issued for one year, for 1600 MW on 27/7/2007.


	No action.




Chairman   Member Secretary     Dr. S.K Gupta      SEE (MSWM)      Sh. M. Dwarkanath     EE (MSWM)     AEE (MSWM) 





Prof.  of I.I.T. Delhi



SSO (Env.)
Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Sl. No.
	Name
	Decision Taken on 26.06.2007


	Action Taken

	Decision


	2.


	Rajghat Power Station


	A reminder letter  to be issued to the  Pr. Secretary (Power) under the signature of  Chairman, DPCC 


	Letter issued to Pr. Secretary (Power) on 17.07.2007.

The unit has replied that Ministry of Power, GNCTD has taken a decision for closing the coal based power plants in near future. A request has been made that as huge funds are required for installation of ETP, permission may be given that water is used for transporting fly ash to ash ponds. 

This power station was also inspected by Zonal office Lucknow of CPCB on 21.08.07 & observed that untreated effluent (TSS- 198 mg/l) is being discharge into to river. They recommended:

· Adequate waste water treatment plant should be provided.

· An interrupted access to ash pond area should be provided.

· CPCB has desired that RTPS take measures to implement the above recommendations within a time frame agreed mutually and be asked to submit time targeted Action Plan & ATR.

Applied for “Consent to Operate” on 30.06.2004.         
	A letter may be issued to General Manager to comply with CPCB directions given during inspection by CPCB on 21.8.07. This compliance must be done by 31.12.07. 




Chairman   Member Secretary     Dr. S.K Gupta      SEE (MSWM)      Sh. M. Dwarkanath     EE (MSWM)     AEE (MSWM) 





Prof.  of I.I.T. Delhi



SSO (Env.)
Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Sl. No.
	Name
	Decision Taken on 26.06.2007
	Action Taken / Status
	Decision


	3.


	Pragati Power Station, ITO

	Power Plant may be asked to carryout continuous monitoring and make efforts for installation of automatic air quality monitoring station 


	Letter issued on 20/8/2007. No reply received so far.

A letter dt 27.08.07 received from Manager (T) Environment, IPGCL-PPCL, informing that-

- MCD is not allowing to dump the Water Treatment Plant (WTP) sludge at Compost Plant /SLF site of MCD.

- The sludge is being dumped at the side of RTPS ash pond to be used by fly ash manufacturer because it contains more than 50% CaO and it is non hazardous.

- Part of this sludge get mixed with wet ash in the ash pond as the less quantity required for bricks manufacturing.

- Requested to instruct MCD to accept the sludge.

- If it is not materialized, the disposal in ash pond / fly ash brick manufacturer stockyard will be continued and requested to moderate suitably the Terms & Conditions of the consent issued. 

Consent to Operate issued on 21.12.05 and valid upto 12.01.08.


	In response to letter received from Manager (T) Environment, IPGCL-PPCL be informed that the sludge may be used for brick manufacturing by using available technology and with the help of NGOs like Development Alternative. 




Chairman   Member Secretary     Dr. S.K Gupta      SEE (MSWM)      Sh. M. Dwarkanath     EE (MSWM)     AEE (MSWM) 





Prof.  of I.I.T. Delhi



SSO (Env.)
Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Sl. No.
	Name
	Decision Taken on 26.06.2007
	Action Taken/ Status


	Decision


	4.
	I. P. Gas Turbine Power Station,

 IP Estate


	_


	A letter dt 27.08.07 received from Manager (T) Environment, IPGCL-PPCL, informing that-

- MCD is not allowing to dump the Water Treatment Plant (WTP) sludge at Compost Plant /SLF site of MCD.

- The sludge is being dumped at the side of RTPS ash pond to be used by fly ash manufacturer because it contains more than 50% CaO and it is non hazardous.

- Part of this sludge get mixed with wet ash in the ash pond as the less quantity required for bricks manufacturing.

- Requested to instruct MCD to accept the sludge.

- If it is not materialized, the disposal in ash pond / fly ash brick manufacturer stockyard will be continued and requested to moderate suitably the Terms & Conditions of the consent issued.

Consent to Operate issued on 23.03.07 and valid upto 04.01.07.


	In response to letter received from Manager (T) Environment, IPGCL-PPCL be informed that the sludge may be used for brick manufacturing by using available technology and with the help of NGOs like Development Alternative.




Chairman   Member Secretary     Dr. S.K Gupta      SEE (MSWM)      Sh. M. Dwarkanath     EE (MSWM)     AEE (MSWM) 





Prof.  of I.I.T. Delhi



SSO (Env.)
Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Sl. No.
	Name
	Decision Taken on 26.06.2007
	Action Taken/ Status


	Decision


	5.
	NTPC, BTPS (Stage-III Expansion),

Badarpur


	Decision taken by Govt. of India and the deficiencies observed in the Detailed Project Report are to be placed before the Committee in the next CMC.


	Letter issued to NTPC on 25/07/2007. 

As observed from the Detailed project report the proposed stack height of the power plant is not meeting the standards as per Environmental Protection Act, 1986.

(Stack height proposed is 148 m while required stack height is 275m)

Applied for consent to establish on 05.02.2007.

Environment Clearance to be obtained from MoEF, Govt. of India.


	Unit may be asked to submit the EIA Clearance. Member Secretary will contact MoEF, Govt. of India regarding EIA clearance accorded to the unit.


Chairman   Member Secretary     Dr. S.K Gupta      SEE (MSWM)      Sh. M. Dwarkanath     EE (MSWM)     AEE (MSWM) 





Prof.  of I.I.T. Delhi



SSO (Env.)
Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Sl. No.
	Name
	Decision Taken on 26.06.2007


	Action Taken/ Status
	Decision

	6.
	M/s Badarpur Thermal Power Station
	Issue consent to the unit with the condition that the unit will meet the noise standards in respect of D.G. Set.
	Consent issued on 27.07.2007 (valid up to 21.03.2010) with the condition that the unit will meet the noise standards in respect of D.G. Set.

This power station was also inspected by Zonal office Lucknow of CPCB on 23.08.07 & observed that particulate matter emission from unit II & V was within the limit. They recommended:

· BTPS should install ash pond effluent recirculation system.

· BTPS should install dedicated fly ash collection system.

· Ash dyke should be designed to withstand the hydraulic load of ash while raising its height, since area downstream of ash pond is densely populated.

· CPCB has desired that BTPS takes majors to implement the above recommendations within a time frame agreed mutually and asked to submit time targeted Action Plan & ATR.
	A letter may be issued to General Manager to comply with CPCB directions given during inspection by CPCB on 23.8.07. This compliance must be done by 31.12.07. 




Chairman   Member Secretary     Dr. S.K Gupta      SEE (MSWM)      Sh. M. Dwarkanath     EE (MSWM)     AEE (MSWM) 





Prof.  of I.I.T. Delhi



SSO (Env.)


Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Sl. No.
	Name
	Decision Taken on 26.06.2007


	Action Taken / Status
	Decision

	7.
	M/s I.P. Thermal Power Station
	
	This power station was also inspected by Zonal office Lucknow of CPCB on 20.08.07 & observed that particulate matter emission from unit 3 & 5 was exceeding the limit. They recommended:

· IPTPS should adopt better ESP maintenance practices and ash evacuation system for controlling the emission of particulate matter.

· IPTPS should also take necessary action for better ash pond management to maintain the concentration of suspended solids within the prescribed limit.

· IPTPS should improve over all housekeeping immediately.

· CPCB has desired that IPTPS takes majors to implement the above recommendations within a time frame agreed mutually and asked to submit time targeted Action Plan & ATR.

Consent issued on 19.03.07 and valid up to 27.04.08.


	A letter may be issued to General Manager to comply with CPCB directions given during inspection by CPCB on 20.8.07.This compliance must be done by 31.12.07. 




Chairman   Member Secretary     Dr. S.K Gupta      SEE (MSWM)      Sh. M. Dwarkanath     EE (MSWM)     AEE (MSWM) 





Prof.  of I.I.T. Delhi



SSO (Env.)
Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Sl. No


	Name of the agency
	Particulars of the project
	Decision taken on 11.09.07
	Action taken 
	Decision of the committee

	1.


	Municipal Corporation of Delhi and Timarpur Okhla Waste Management Co. Pvt. Ltd., MSW Complex,, Timarpur Incineration Plant Site, Timarpur, Delhi
	Setting up of the integrated municipal waste complex at Timarpur, Delhi -110 009. The capacity of the project would be 600 TPD MSW besides 100 MGD liquid Waste. The treatment/processing of the MSW would be based on DST-TIFAC technology of mixed municipal waste to RDF/Fluff preparation and bio-gas generation from the organic waste. The power generation would be 3.75 MW. Cost of the project is Rs. 400 million.
	Consent to Establish under Air and Water Act has been extended up to 6-7-2009 with the condition to submit the EIA clearance and balance fee. The consent to Establish will be issued in the name of  Timarpur- Okhla Waste Management Co. Pvt. Ltd (Earlier Timarpur Waste Management Co).
	Consent to establish issued on 25.09.07 & valid up to 06.07.09.

EIA clearance and balance fee of Rs. 2500 not submitted by the unit.
	No action.


Chairman   Member Secretary     Dr. S.K Gupta      SEE (MSWM)      Sh. M. Dwarkanath     EE (MSWM)     AEE (MSWM) 





Prof.  of I.I.T. Delhi



SSO (Env.)
Decisions taken by CMC (MSW) in its 7th Meeting held on 28.12.2007
	Sl. No


	Name of the agency
	Particulars of the project
	Decision taken on 11.09.07
	Action taken 
	Decision of the committee

	1.


	Municipal Corporation of Delhi and Timarpur Okhla Waste Management Co. Pvt. Ltd., MSW Complex,, Timarpur Incineration Plant Site, Timarpur, Delhi
	Setting up of the integrated municipal waste complex at Timarpur, Delhi -110 009. The capacity of the project would be 600 TPD MSW besides 100 MGD liquid Waste. The treatment/processing of the MSW would be based on DST-TIFAC technology of mixed municipal waste to RDF/Fluff preparation and bio-gas generation from the organic waste. The power generation would be 3.75 MW. Cost of the project is Rs. 400 million.
	Consent to Establish under Air and Water Act has been extended up to 6-7-2009 with the condition to submit the EIA clearance and balance fee. The consent to Establish will be issued in the name of  Timarpur- Okhla Waste Management Co. Pvt. Ltd (Earlier Timarpur Waste Management Co).
	Consent to establish issued on 25.09.07 & valid up to 06.07.09.

EIA clearance and balance fee of Rs. 2500 not submitted by the unit.
	No action.


Chairman   Member Secretary     Dr. S.K Gupta      SEE (MSWM)      Sh. M. Dwarkanath     EE (MSWM)     AEE (MSWM) 





Prof.  of I.I.T. Delhi



SSO (Env.)
Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Sl. No


	Name of the agency
	Particulars of the project
	Decision taken on 11.09.07
	Action taken 
	Decision of the committee

	1.


	Municipal Corporation of Delhi and Timarpur Okhla Waste Management Co. Pvt. Ltd., MSW Complex,, Timarpur Incineration Plant Site, Timarpur, Delhi
	Setting up of the integrated municipal waste complex at Timarpur, Delhi -110 009. The capacity of the project would be 600 TPD MSW besides 100 MGD liquid Waste. The treatment/processing of the MSW would be based on DST-TIFAC technology of mixed municipal waste to RDF/Fluff preparation and bio-gas generation from the organic waste. The power generation would be 3.75 MW. Cost of the project is Rs. 400 million.
	Consent to Establish under Air and Water Act has been extended up to 6-7-2009 with the condition to submit the EIA clearance and balance fee. The consent to Establish will be issued in the name of  Timarpur- Okhla Waste Management Co. Pvt. Ltd (Earlier Timarpur Waste Management Co).
	Consent to establish issued on 25.09.07 & valid up to 06.07.09.

EIA clearance and balance fee of Rs. 2500 not submitted by the unit.
	No action.


Chairman   Member Secretary     Dr. S.K Gupta      SEE (MSWM)      Sh. M. Dwarkanath     EE (MSWM)     AEE (MSWM) 





Prof.  of I.I.T. Delhi



SSO (Env.)
Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken
	Action taken / Status
	Decision

	1
	Dr. Sen Nursing home Nallah STP

(10 MLD) 
	Issue SCN for deficiencies observed during the inspection.
	· Plant was inspected on 04.12.06.

· SCN issued on 02.01.2007 for the deficiencies observed during the inspection.

· No reply has been teceived. 

· Consent valid up to 25-02-08.

· As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.


	Member Secretary, DPCC to inspect.




Chairman
Member Secretary
       SEE
        Dr. S.K Gupta          M. Dwaraknath                    EE 
          AEE 

DPCC

   DPCC

MSWM Cell
    Member (Acd. Inst)   Member (Env. Deptt.)
    MSWM Cell  MSWM Cell

Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity 
	Decision taken on 16.01.2007
	Action taken / Status
	Decision

	2
	Delhi Gate Nallah 

(2.2 MGD)
	Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days and also to maintain the log book properly

	Consent to operate issued on 15.2.2007 & valid upto 11.10.09.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.


	No action. 




Chairman
Member Secretary
       SEE
        Dr. S.K Gupta          M. Dwaraknath                    EE 
          AEE 

DPCC

   DPCC

MSWM Cell
    Member (Acd. Inst)   Member (Env. Deptt.)
    MSWM Cell  MSWM Cell

Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on16.01.07
	Action taken / Status
	Decision

	3.
	KONDLI – Ph-I 


	Issue SCN giving last opportunity to remove the deficiencies observed during inspection
	 SCN issued on 15-02-07

Reply received on 23-02-07. The following submissions have been made:-

· Power back up system, with flow meters, is being provided in due course of time.

· All aerators and PST are in working condition now. 

· Presently, treated effluent is being used for horticulture purpose within the premises of plant. Further reuse of treated effluent is under consideration with DDA.

· Work order has already been placed for renovation of digester and gas holders. 

· Plant has submitted required information as per consent application along with an affidavit.

· As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Applied for consent to operate on 19.04.06.


	.

Consent to operate will be granted once the deficiencies noted in SCN are finally implemented and confirmed to DPCC.


Chairman
Member Secretary
       SEE
        Dr. S.K Gupta          M. Dwaraknath                    EE 
          AEE 

DPCC

   DPCC

MSWM Cell
    Member (Acd. Inst)   Member (Env. Deptt.)
    MSWM Cell  MSWM Cell

Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on16.01.07
	Action taken / Status
	Decision

	4.
	KONDLI, 

Ph-II 

(25 MGD) 
	Issue SCN giving last opportunity to remove the deficiencies observed during inspection.
	SCN issued on 15-02-07
Reply received on 23-02-07. The following submissions have been made:-

· Power back up system, with flow meters, is being provided in due course of time.

· All aerators are in working condition now. 

· Work order has been placed for renovation of five sludge digesters and      2 gas holders.

· Presently, treated effluent is being used for horticulture purpose within the premises of plant. Further reuse of treated effluent is under consideration with DDA.

· Work order has already been placed for renovation of digester and gas holders. 

· Plant has submitted required information as per consent application along with an affidavit.

· As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Applied for consent to operate on 19.04.06.


	Consent to operate will be granted once the deficiencies noted in SCN are finally implemented and confirm to DPCC.


Chairman
Member Secretary
       SEE
        Dr. S.K Gupta          M. Dwaraknath                    EE 
          AEE 

DPCC

   DPCC

MSWM Cell
    Member (Acd. Inst)   Member (Env. Deptt.)
    MSWM Cell  MSWM Cell

Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on 21.02.2007
	Action taken / Status
	Decision

	5.
	KONDLI – Ph-III 

(10 MGD)
	Issue SCN to the plant with a copy to CE, DJB
	SCN issued on 13-03-07.

Reply received on 03-04-07. The following submissions have been made:-

· Power back up system, with flow meters, is being provided..

· All aerators are in working condition now.

· Report is being submitted month wise.

· Sludge analysis is being carried out in the lab of DJB at STP Kondli and same is being forwarded to Director (T & QC) DJB. However, a copy of report from July 06 to Feb 07 is enclosed herewith.

· Record is being maintained at Laboratory under the supervision of ACWQA Kondli plant.  

· As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

· Consent issued on22.09.05 and  valid up to 02-12-07.


	.

Consent to operate will be granted once the deficiencies noted in SCN are finally implemented and confirm to DPCC.


Chairman
Member Secretary
       SEE
        Dr. S.K Gupta          M. Dwaraknath                    EE 
          AEE 

DPCC

   DPCC

MSWM Cell
    Member (Acd. Inst)   Member (Env. Deptt.)
    MSWM Cell  MSWM Cell

Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken
	Action taken / Status
	Decision

	6.
	Nehru Vihar, Oxidation Pond STP (13.5 MLD) 
	_
	· Consent issued on21.09.05 and  valid up to 28.11.07.

· Plant was inspected on 15.11.06.

· SCN issued on 26.12.2007 as number of deficiencies were observed during the above said inspection.

· Plant has not submitted any reply. 

· As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.


	.

SEE  to inspect. 


Chairman
Member Secretary
       SEE
        Dr. S.K Gupta          M. Dwaraknath                    EE 
          AEE 

DPCC

   DPCC

MSWM Cell
    Member (Acd. Inst)   Member (Env. Deptt.)
    MSWM Cell  MSWM Cell

                                                       Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken 
	Action taken / Status
	Decision

	7
	 Keshopur STP

(72 MGD) 

(40+20+12)
	_
	· Consent issued on 21.09.05 & expired on 24-09-07 for 60 MGD. Not applied for renewal

· Plant inspected by DPCC officials on 5.12.2006.

· SCN issued on 02.1.2007 as number of deficiencies     were observed.

· Plant has not submitted any reply.

· As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

· However, no consent application for the STP  of 12 MGD capacity. DPCC lab reported that said STP was found abundant during sampling in Sept 2007. 


	.

Ask for renewal of consent. Unit may also be asked to rectify the deficiencies as communicated vide SCN dated 2.1.07. STP may give time of one month to do so.


Chairman
Member Secretary
       SEE
        Dr. S.K Gupta          M. Dwaraknath                    EE 
          AEE 

DPCC

   DPCC

MSWM Cell
    Member (Acd. Inst)   Member (Env. Deptt.)
    MSWM Cell  MSWM Cell

Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on 21.02.2007


	Action taken / Status
	Decision

	8.
	Mehrauli     STP 
	Issue consent to operate subject to the following consent conditions as well as comments:

1. Install mechanical sludge dewatering system.


2. Ensure proper storage of dry sludge.

                                                                                                                                                                                                                               3. Examination of the issue related to low capacity utilization and quick resolution of the problem in consultation with related agencies.                                  

Comments:-

 a. DPCC would appreciate if DJB takes steps to generate gas form the STP.                                                                                                   
b. DJB would make all efforts to reuse the treated effluents in the nearby parks and farm houses.                                              


	Consent issued on 20.03.2007 & valid upto 15.12.09.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.


	Mehrauli STP has not replied to the consent conditions imposed on 20.3.07. STP may be asked to reply within one month positively. 
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on 16.01.2007
	Action taken / Status
	Decision

	9.
	Yamuna Vihar Phase –I STP (10 MGD) 
	Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days.
	Consent issued on 28.2.2007 & valid upto 16.11.07.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.


	STP has not replied to consent conditions imposed on 28.02.07. STP may be asked to reply within one month positively. 
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on 16.01.2007
	Action taken / Status
	Decision

	10.
	Yamuna Vihar Phase –II STP

 (10 MGD) 
	Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days.
	Consent issued on 28.2.2007 & valid upto 28.12.09.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), plant is not meeting the prescribed standard.


	The unit has not replied to consent conditions imposed on 28.2.07. The unit is also not meeting with the prescribed standards. SCN may be issued u/s 33 A of Water Act for remedial action within one month. 
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on16.01.07
	Action taken / Status
	Decision
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity 
	Decision taken on16.01.07
	Action taken / Status
	Decision

	12.
	Rithala  STP– Ph-II 

( 40 MGD)
	Issue SCN giving last opportunity to remove the deficiencies observed during inspection

	SCN issued on dated 15-02-07.

Reply received on 22-03-07. The following submissions have been made:-

· The defective flow meter at treated effluent channel made operational. 

· Both sludge thickeners are in working condition now.

· Sludge de-watering unit is operated only during monsoon season.

· Matter wrt reuse of treated effluent is under planning stage.

· Electricity is being generated as per    raw sewage availability. 
· As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Previous Consent valid upto 21.01.06. Applied for renewal of consent on 20.01.2006. 


	.

Unit was given last opportunity to correct deficiencies. A reply received on 22.03.07 indicates that some remedial action has been taken. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision Taken on16.01.07
	Action taken / Status
	Decision

	13.
	Pappankalan ( 20 MGD) 


	Issue SCN to SE, a copy to Chief Engineer giving last opportunity to rectify the deficiencies

	SCN issued on 15.02.07. 

No reply received. 
As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Previous Consent valid upto 09.12.04. Applied for renewal of consent on 10.12.2004. 


	While the unit is applied for consent he has not corrected deficiencies. Unit was given last opportunity to correct deficiencies. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision Taken on16.01.07
	Action taken / Status
	Decision

	14.
	Najafgarh STP 

( 5 MGD

	Issue SCN to SE, a copy to Chief Engineer giving last opportunity to rectify the deficiencies.


	SCN issued on 15.02.07. No reply received.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Applied for consent to operate on 29.11.2004. 


	While the unit is applied for consent he has not corrected deficiencies. Unit was given last opportunity to correct deficiencies. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken
	Action taken / Status
	Decision

	15.
	Nilothi STP (40 MGD)
	_
	· Consent expired in 02-12-06. Not applied for renewal of consent.

· Plant was inspected on 17.11.2006.

· SCN was issued on 26.12.06, as numbers of deficiencies were observed.

· Plant has not submitted consent application for renewal of consent.

· As per inspection by DPCC laboratory dated 19.09.2007 it reveals that the plant was non operational during the monitoring. 


	.

The unit was issued SCN on 17.11.2006 and the reply received indicates that some deficiencies have been corrected. 

SEE to inspect and submit a report on file for necessary action.  

The unit may ask to apply for renewal of consent immediately.
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on 21.02.2007
	Action taken / Status 


	Decision

	16.
	Rohini STP (15 MGD) 
	CE, DJB was asked to apply for consent, who agreed to do the needful.
	· Plant has submitted application on 01-05-07 for consent to operate. 

· As per DPCC laboratory report, during the last several occasions, plant found non operational.
· Hence, no monitoring report available with DPCC. However plant has submitted analysis report of its own. Treated effluent quality is as per norms laid down.
· As per inspection by DPCC laboratory dated 21.09.2007 it reveals that the plant was non operational during the monitoring. 


	SEE to inspect and report on file.
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on 16.01.2007
	Action taken / Status
	Decision

	17.
	Coronation Pillar (40 MGD) 
	Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days and also to maintain the log book properly.

	Consent to operate issued on 28.2.2007 valid upto 12.03.2009.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.


	No action. 
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken
	

Action taken / Status
	Decision

	18.
	Vasant Kunj STP (5.2 MGD) 
	_
	· Consent issued on 22.09.05 & valid up to 11-12-07.

· Plant was inspected on 14.11.06.

· SCN issued on 26.12.2007 as number of deficiencies were observed during the above said inspection.

· Plant has not submitted any reply. 

· As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.


	.

Unit was given last opportunity to correct deficiencies. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on16.01.07
	Action taken / Status
	Decision

	19.
	Narela STP (10 MGD)  


	Issue SCN giving last opportunity to remove the deficiencies observed during inspection.
	SCN issued on 20-03-2007

Reply received on 18-05-07 The following submissions have been made:-

· Flow meter at inlet & outlet of STP are in working condition.                            

·  Treated effluent is being used for irrigation at the plant and possibility is being explored for its use by DDA or other Civil Agency.

· Possibility is being explored for installing mechanical sludge dewatering system at the plant.

· As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Previous Consent valid upto 14.01.2005. Applied for renewal of consent on 14.01.2005. 


	Renewal of the consent granted with clear condition that the plant shall operate properly and efficiently.
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on16.01.07
	Action taken / Status 
	Decision

	20.
	OKHLA STP 

[Plant No.- I, II, III & IV, 

(12+30+37+45)

Total 124 MGD) ]


	Issue SCN giving last opportunity to remove the deficiencies observed during inspection
	SCN issued on 15.2.2007

Reply received on 26-03-07. The following submissions have been made:-

· Magnetic flow meter is not feasible. Ultrasonic flow meter also did not work due to deposition of sludge /plastic floating material on probes of the meter.

· Wrt renovation of sludge drying beds, necessary action is being taken by construction division.

· The issue, of trapping of effluents flowing in the two drains passing through the plant, has not been addressed in the reply.

· The supply of effluents for irrigation after primary treatment suspended. The matter is under examination.

· As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

. Previous Consent valid upto 17.04.05. Applied for renewal of consent on 10.03.2005. 


	Unit has applied for renewal of consent but has not corrected all the deficiencies pointed out vide SCN issued on 15.2.07 

Unit may be reminded to correct all deficiencies and only then consent will be granted.
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            Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken
	Action taken / Status
	Decision

	21.
	Okhla STP 

(16 MGD)


	_
	· Consent issued on 21.09.05 & valid up to 02-12-07.

· Plant was inspected on 06.12.06.

· SCN dated 02.1.2007 was issued as number of deficiencies were observed.

· Plant  submitted reply with the following submissions:-

· Magnetic flow meter is not feasible in such type of STP’s. Ultrasonic flow meter also did not work due to deposition of sludge /plastic floating material on probes of the meter.

· Fourteen to sixteen aerators at a time are sufficient for generating effluent of desired quantity .However, all digesters and aerators have been made operational.

·  Presently, part of treated effluent is being used for horticulture purpose from this unit. 

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.


	Unit has applied for renewal of consent but has not correct all the deficiencies pointed out vide SCN issued on 02.01.2007 

Unit may be reminded to correct all deficiencies and only then consent will be granted.
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken
	Action taken / Status
	Decision

	22.
	STP at C-DOT Campus, Chattarpur, 

Mehrauli, New Delhi-30.

((125 KLD)


	_
	· Consent to operate expired on 12.4.2007.

.

· A letter was issued on 26.06.2007, to  submit the consent application, but no reply/consent application received.


	Unit may be asked to apply for renewal of consent. 

SEE to inspect. 

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on 21.02.2007
	Action taken / Status
	Decision

	23.
	Holambi Kalan STP 

(2 MLD) 
	Copy o f the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-07 to instruct the officials concerned to apply for the renewal of consent.
	Copies of the letters/SCN issued on 01-11-2006 & 29-11-2006 handed over during CMC meeting held on 21-02-07.  

Consent issued on 14.05.04 & valid upto 08.10.06.

No application for renewal received.


	.

Unit may be asked to apply for renewal of consent. 

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on 21.02.2007
	Action taken / Status
	Decision

	24.
	Bakkarwala STP 

(3 MLD)
	Copy of the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-07 to instruct the officials concerned to apply for the renewal of consent.


	   Copies of the letters/SCN issued on 01-11-06, 29-11-06 handed over during CMC meeting held on 21-02-07.  

Previous Consent valid upto 12.06.06. 

Plant has submitted consent application for renewal of consent on 21-05-07 with self analysis report.
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SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on 21.02.2007
	Action taken / Status
	Decision

	25.
	Molar Band STP (3 MLD)
	Copy of the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-2007 to instruct the officials concerned to apply for the renewal of consent.
	Copies of the letters / SCN issued on 01-11-2006 & 29-11-06 handed over during CMC meeting held on 21-02-2007.  

Previous Consent valid upto 12.06.06. 

Plant has submitted consent application for renewal of consent on 21-05-2007 with self analysis report.


	.

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
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                                          Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on 21.02.2007
	Action taken / Status
	Decision

	26.
	Tikri Khurd STP (2 MLD) 
	Copy o f the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-07 to instruct the officials concerned to apply for the renewal of consent.


	Copies of the letters/SCN issued on 01-11-2006 & 29-11-06 handed over during CMC meeting held on 21-02-07.  

Previous Consent valid upto 12.06.06. 

Letter issued on 29.11.06 for seeking consent application for renewal.

No application for renewal of consent received.


	.

Unit may be ask for apply to renewal of consent. 

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken  on 21.02.2007


	Action taken / Status
	Decision

	27.
	Ghitorni STP

 (5 MGD) 
	CE, DJB was asked to apply for consent, who agreed to do the needful.
	No application for consent received.

As per DJB, plant will be commissioned by Dec. 2007. 


	Unit may be ask for apply to renewal of consent. 

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs..
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken
	Action taken / Status
	Decision

	28.
	STP at National Bureau of Plant Genetic Resources ICAR, Pusa Campus.

(80 KLD)

	_
	· Consent to operate expired on 07.06.2007, and not applied for renewal of consent.

· A letter was issued on 26.06.2007 to submit the consent application, but no reply/consent application received.


	Unit may be ask for apply to renewal of consent.

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken
	Action taken / Status
	Decision

	29.
	STP at BSNL, CTO Project, Mathura Lane, Janpath, New Delhi.
	_
	· Plant has submitted a letter dt 30-05-2007 & requested to provide acceptable standard.

· A letter was issued on 03.07.2007 to submit application for consent to establish/operate. But no reply received in this regard.

 
	.

Unit may be ask for apply to renewal of consent.

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken
	Action taken / Status
	Decision

	1.
	Water Treatment Plant,  Nangloi

     (40  MGD) 
	_
	Plant has submitted a letter dt 16-05-07 & requested for NOC to operate the WTP.

Letter issued on for asking to apply for consent under Air & Water Act on prescribed application form. 

Not applied for consent so far.  
	.

Unit may be ask for apply for consent to operate.

MS to direct lab officials of DPCC to do regular monthly lab testing for drinking water standards.
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken
	Action taken / Status
	Decision

	2.
	Water Treatment Plant , Haiderpur 

(200 MGD)
	_
	Plant has submitted a letter dt 03-05-07 & requested for NOC to operate the WTP.

Letter issued on for asking to apply for consent under Air & Water Act on prescribed application form. 

Not applied for consent so far.  
	.

Unit may be ask for apply for consent to operate.

MS to direct lab officials of DPCC to do regular monthly lab testing for drinking water standards.
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Sl. No.
	Name of STP & installed capacity
	Decision taken on 21.02.2007
	Action taken / Status


	Decision

	3.
	Water Treatment Plant,

Sonia Vihar, 

( 140 MGD)
	Issue consent to operate for three years subject to the following conditions:

1.  Install mechanical sludge dewatering system.

2. Submit an action plan for proper sludge disposal as per law.
	Consent issued on 13.03.2007
	Ask the unit to compliance report of consent condition. 

MS to direct lab officials of DPCC to do regular monthly lab testing for drinking water standards.

Committee has also decided that  other two units i.e Wazirabad Water Works & Chandrawal Water Works be also asked to apply for consent to operate under Air & Water Acts.
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Name
	Decision taken on 26.06.2007
	Action Taken
	Consent Status
	Status


	Decision of Committee

	1. 

MAYAPURI CETP  (12 MLD)
	A letter under the signature of                 Chairman, DPCC to be issued   to MD, DSIDC with a copy to  Commissioner of Industries & President, CETP Society asking  to apply for  consent to operate and remove the deficiencies observed by the DPCC officials during the inspection on 11-04-07.
	DO letter was issued on  17.07.07              
	DSIDC Applied for consent to establish on 03.07.02. Application consent to operate was received on 03.05.02. Consent to operate granted on 20.01.04 for a period of three year and valid up to 05.05.05. DSIDC has submitted application of renewal of consent on 21.04.05. 

CETP society, Mayapuri submitted application for consent to operate on 07.05.07 
	· Consent application for consent to operate was submitted by the CETP Society. 
· No reply received from CETP Society and Commissioner of Industries regarding rectification of deficiencies. However, DSIDC has submitted a letter dated 03.08.2007 stating that the CETP has already been transferred under the CETP Act to CETP Society. The appropriate authority for initiating action is Jt. Commissioner of Industries. 
· Complaint has been received from Rajouri Apartments RWA against the Nuisance caused by CETP Mayapuri and same has been forwarded to DJB.

· During the inspection on 12.07.07, the following were  observed  
· Flow intake range -   3.5 MLD.

· Significant quantity of silt/sludge found in equalization tanks & pre chlorination tanks. However, one equalization tank was found without effluent/dry for desilting of silt/sludge. 
· Pressure gauges attached to DMFs & ACFs found in non operational condition.
· No flow meter installed at outlet of CETP. 
· As reported, CETP not being received effluent from REPS- II due to blockage/blocking in pipe line/rising main for one month.
· As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during last three months are as under:
Sept

Aug

July

Inlet

Outlet

Inlet

Outlet

Inlet

Outlet

TSS-516

BOD-36        TDS-3520

TSS-416

BOD-33        TDS-2318

TSS-384

BOD-42        TDS-2540


	The case of Mayapuri CETP was examined by the Committee and it was found that TSS (at inlet), BOD &  TDS (at outlet) are well above the norms. 

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 4.2 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.
The CETP society will submit a Bank Guarantee of Rs. 5 lakh (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.


Chairman     Member Secretary
SEE
       Dr. S.K Gupta             M. Dwaraknath                 EE 
          
 AEE 
DPCC
       DPCC

    MSWM Cell    Member (Acd. Inst)   Member (Env. Deptt.)     MSWM Cell   MSWM Cell

Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Name
	Decision taken on 26.06.2007
	Action Taken
	Consent Status
	Status
	Decision

	2.

MANGOL PURI CETP (2.4 MLD) 
	Consent to Operate to be  granted with the condition that : 

1. Increase the effluent quantity.

2. To install mechanical dewatering system.

3. To modify the acoustic enclosure with DG set to achieve the insertion loss.


	 Consent to operate issued with conditions  on 27.07.2007 
	Consent to operate issued to CETP Society on 27.04.07 for a period three years and valid up to 04.02.2010.
	The compliance of consent conditions not  received so far from CETP Society. 

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during last three months are as under:
Sept

Aug

July

Inlet

Outlet

Inlet

Outlet

Inlet

Outlet

TSS-475

Cl-1960          TDS-4780

TSS-512

Cl-1230          TDS-7137

TSS-340

Cl-3200          TDS-7260         Fluride-2.8

· During the inspection on 18.07.07, the following were  observed  
·  Flow intake range -   1.1 to 1.35 MLD.

· Flow meter installed at inlet (near primary clarifier) shows reading 46.5M3/Hr.

· No flow meter installed at outlet of CETP.

· Pressure gauges, attached to DMF & ACFs found non-operational condition.


	A letter issued to CETP 
society to correct the 
deficiencies noted during 
the inspection on 18.07.07
and to comply with the earlier conditions which were imposed when 
the consent to operate was 
granted. It was also found 
that against the installed
 capacity of 2.4 MLD, the
 CETP Society is operating 
it at only 1.5 MLD. This
 indicates that it is grossly 
under utilized and individual
 connections to the 
conveyance system are
 severely limited. 

The Committee felt that the SCN should be issued to the Society to
 ensure that the connection
 of individual unit shall be
 connected to the 
conveyance system to 
maximize capacity utilization.

 The said CETP 

Societies discharging its

 functions under Section 4 

under Rule 3(i) to obtain 

requisite information 

regarding individual 

connections with 

conveyance system 

leading to CETP. This 

information to be furnished to

 DPCC and to the 

Appropriate Authority to 

invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.
The society will submit a 
Bank Guarantee of Rs. Fifty
 Thousands (valid for Six
 months) and also submit an affidavit to confirm correction of 
deficiencies by 31.12.07.
 BG will be forfeited if the
 corrections are not done. 

The copy should be sent to 
MD (DSIDC) and Comm. 
of Industries. 


Chairman     Member Secretary
SEE
       Dr. S.K Gupta             M. Dwaraknath                 EE 
          
 AEE 
DPCC
       DPCC

    MSWM Cell    Member (Acd. Inst)   Member (Env. Deptt.)     MSWM Cell   MSWM Cell

Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	  Name
	Decision taken on 26.06.2007
	Action Taken
	Consent Status
	Status


	Decision

	3.

Badli CETP

(12 MLD) 
	MS, DPCC to issue a letter to MD, DSIDC, Commissioner of Industries & President, CETP Society to remove the deficiencies observed by the DPCC officials during the inspection on 17-04-07, within 3 months. In case of non compliance, consent to Operate will be re-considered.
	Letter  issued on 08.08.07              
	Consent to operate issued on 28.02.07 to CETP society for period of three years and valid up 28.12.09.
	The compliance of consent  condition  not received from CETP Society, however as per last 3 months test reports of DPCC lab, Fluoride level is within the prescribed norms.

No reply received from CETP society and Commissioner of Industries regarding rectification of deficiencies. However, DSIDC has submitted a letter dated 03.08.2007 stating that the CETP has already been transferred under the CETP Act to CETP Society. The appropriate authority for initiating action is Jt. Commissioner of Industries. 
A copy of  letter has been received from Joint Commissioner industries regarding the stopping of the connection of Sewer Lines of the adjoining area into the conveyance system of the CETP Badli Industrial Estate & desalting of chocked Conveyance system as well as repairing of broken covers of Manholes etc. 

· During the inspection on 11.07.07, the following were  observed  
· Flow intake range -  0.78 to 1.56 MLD.

· Flow meter sent to repair 

· Grit chamber, Equalization tank work field with significant quantity of silt/sludge.

· Pre chlorination as well as post chlorination were non-operational.

· Dosing of Alum and Bleaching not being carried out due to defective pipe line.

· 2 number of pressure gauges ( out of 8 ) attached to ACF and 2 gauges (out of 12) of DMFs work found non-operational.

· 2 Aeration (out of 3) found out of order.

· 1 vacuum filter found out of order and other also partially operational due to non-operational of vacuum pump.

· No flow meter installed at outlet of CETP.  

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during last three months are as under:
Sept

Aug

July

Inlet

Outlet

Inlet

Outlet

Inlet

Outlet

Cr-4.6 

TDS-2120

TSS-256      Cr-2.1

_

_

_


	This CETP was inspected on 17.4.07 and again on 11.7.07 the following deficiencies were noted in first time and the second time as under: -

The CETP society has neither corrected the deficiencies nor sent the reply. In view of the above, issue SCN for revoking of consent u/s 27 of the Water Act.  

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 1.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

 The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.
The Society will submit a Bank Guarantee of Rs. Five Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.  


Chairman     Member Secretary
SEE
       Dr. S.K Gupta             M. Dwaraknath                 EE 
          
 AEE 
DPCC
       DPCC

    MSWM Cell    Member (Acd. Inst)   Member (Env. Deptt.)     MSWM Cell   MSWM Cell

Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Name
	Decision taken on 26.06.2007
	Action Taken
	Consent Status
	Status


	Decision

	4.

Wazirpur CETP 

(24 MLD) 
	MS, DPCC to issue a letter to MD, DSIDC, Commissioner of Industries & President, CETP Society to remove the deficiencies observed by the DPCC officials during the inspection on 13-04-07, within 3 months. In case of non compliance, consent to Operate will be re-considered.
	Letter  issued on 08.08.2007                            
	Consent to operate issued on 23.02.07 to CETP society for period of three years and valid up 27.12.09.
	No reply received from CETP society and Commissioner of Industries regarding rectification of deficiencies. However, DSIDC has submitted a letter dated 03.08.2007 stating that the CETP has already been transferred under the CETP Act to CETP Society. The appropriate authority for initiating action is Jt. Commissioner of Industries. 

· During the inspection on 19.07.07, the following were  observed  
· Flow intake range -   3 to 4 MLD.

· Flow meter installed at inlet found in operation.

· pH of  ineffulent observed as 2.7.

· Vacuum filter (both), flush mixture (2 nos) were not in operation since last few days.

· Receiving chamber an grit chamber filled  with silt/sludge.

· Pressure gauge attached to ACFs and DMFs not in operational conditional.

 As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during last three months are as under:
Sept

Aug

July

Inlet

Outlet

Inlet

Outlet

Inlet

Outlet

pH- 2.9            Ni-3.8           Cu-7.6             Cr-30          Cr+6-3.0    

BOD-36       TDS-3760     Fluoride-2.4

pH-2.5         Ni-3.2          Cu-8.0               Cr-35 

TDS-3270

pH- 2.2         TSS-276           Cr-16.8

TDS-5160 


	The unit has not 
complied with the 
directions given after 
inspection on 13.4.07.
 A SCN notice for 
closure / revocation of 
consent be issued.

The unit has further not bothered to correct deficiencies found during the inspection on 19.7.07. It was also found that against the installed capacity of 24 MLD, the CETP Society 
is operating it at only 3.5 MLD. This indicates that it is grossly under utilized 
and individual connections to the conveyance system are severely limited. 

The Committee felt that
 the SCN should be 
issued to the Society to
 ensure that the 
connection of individual
 unit shall be connected
 to the conveyance 
system to maximize 
capacity utilization.

 The said CETP 

Societies discharging

 its functions under 

Section 4 under 

Rule 3(i) to obtain 

requisite information 

regarding individual 

connections with 

conveyance system

 leading to CETP. 

This information to be 

furnished to DPCC and 

to the Appropriate 

Authority to invoke 

penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.The society will submit a Bank Guarantee of Rs. Ten Lakhs (valid 
for Six months) and also
 submit an affidavit to 
confirm correction of 
deficiencies by 31.12.07
. BG will be forfeited 
if the corrections not 
done by 31.12.07. The 
unit is given a last 
chance to correct its
 deficiencies by 31.12.07 failing which the consent will be revoked and heavy
 penalty will be imposed
 on CETP society. CETP 

society must operate 

the CETP plant 

professionally, efficiently,

 effectively. Copy should be sent to MD (DSIDC) and Comm. of Industries.


Chairman     Member Secretary
SEE
       Dr. S.K Gupta             M. Dwaraknath                 EE 
          
 AEE 
DPCC
       DPCC

    MSWM Cell    Member (Acd. Inst)   Member (Env. Deptt.)     MSWM Cell   MSWM Cell

Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Name
	Decision taken on 26.06.2007
	Action Taken
	Consent Status
	Status


	Decision

	5.

Jhilmil CETP (16.8 MLD)
	MS, DPCC to issue a letter to MD, DSIDC, Commissioner of Industries & President, CETP Society to remove the deficiencies observed by the DPCC officials during the inspection on 16-04-07, within 3 months. In case of non compliance, consent to Operate will be re-considered.


	Letter  issued on 08.08.2007                            

              
	Consent to operate issued on 28.02.07 to CETP society for period of three years and valid up 07.01.2010.
	No reply received from Commissioner of Industries regarding rectification of deficiencies. However, DSIDC has submitted a letter dated 03.08.2007 stating that the CETP has already been transferred under the CETP Act to CETP Society. The appropriate authority for initiating action is Jt. Commissioner of Industries. 
SCN issued to the Society  on 08.08.07 to remove the deficiencies observed by the DPCC officials during the inspection on 11-04-07,  CETP Society has submitted reply detailed as under:

· Desilting of equalization tanks will be done after monsoon after drying the silt.

· Regarding flow, CETP society has replied that CETP society had not   control over the design of the plant. Grit is removed daily from grit chamber.

· Regarding large quantity of oil & Grease was observed in both equalization tanks, society submitted that Oil & Grease Skimmer & Separator is planned.

· All record are maintained at the CETP. The flow meter at outlet is planned.

· Regarding parameters of Cl & TDS, society has submitted that as per EPCA Guidelines, Chloride and TDS are exempted parameters as ground water is being used as process water in the industry. However, no such guideline issued by EPCA. 

· During the inspection on 11.07.07, the following were  observed  
· Flow intake range -   3.2 MLD.

· Both equalization tanks were found filled with significant quantity of  silt/sludge.

· No settling was observed in grid chamber.

· Large quantity of oil and grease was observed in both equalization tanks.

· 1 vacuum filter found was found non operational.

· 3 no receiving pumps ( out of 6) were found under repair.

· No flow meter installed at outlet of CETP.

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during last three months are as under:
Sept

Aug

July

Inlet

Outlet

Inlet

Outlet

Inlet

Outlet

TSS-264

_

TSS-260

TDS-2744

TSS-252        Cu-3.2           Cr-2.6    

BOD-35      TDS-2410


	Directions issued after Inspection on 16.4.07 have been responded by the society. However, the inspection of 11.7.07 still found certain deficiencies which should be communicated to the society by the SCN u/s 33 of Water Act. While the July and Aug. monitoring reports showed certain norms not in compliance, the September report finds the CETP functioning with in the norms. 

It was also found that against the installed capacity of 16.8 MLD, the CETP Society is operating it at only 5.0 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.
The Society may be asked to be cautious and correct all deficiencies by 31.12.07 and submit an affidavit, failing which a BG of Rs. 5 lakh may be imposed on the society.  

The copy should be sent to MD (DSIDC) and Comm. of Industries.  


Chairman     Member Secretary
SEE
       Dr. S.K Gupta             M. Dwaraknath                 EE 
          
 AEE 
DPCC
       DPCC

    MSWM Cell    Member (Acd. Inst)   Member (Env. Deptt.)     MSWM Cell   MSWM Cell

Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Name
	Decision taken on 26.06.2007
	Action Taken
	Consent Status
	Status
	Decision

	6.

Nangloi CETP

 (12 MLD) 
	A letter under the signature of                 Chairman, DPCC to be issued   to MD, DSIDC with a copy to Commissioner of Industries & President, CETP Society asking to apply for consent to operate within a month and remove the deficiencies observed.
	DO letter was issued on 17.07.07              
	Consent to operate issued on 15.02.04 to DSIDC for period of three year and valid up 27.07.07.

CETP society submitted application for consent to operate on 27.06.07 
	Consent application for consent to operate was submitted by the CETP Society on 27.06.2007. 

No reply received from CETP society and Commissioner of Industries regarding rectification of deficiencies. However, DSIDC has submitted a letter dated 03.08.2007 stating that the CETP has already been transferred under the CETP Act to CETP Society. The appropriate authority for initiating action is Jt. Commissioner of Industries. 
During the inspection on 18.07.07, the following were  observed :
· Flow intake range -   2 MLD.

· Pressure gauges attached to DMFs & ACFs found in non operational condition.
· Flow meter installed at outlet of CETP found out of order.  
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during last three months are as under:
Sept

Aug

July

Inlet

Outlet

Inlet

Outlet

Inlet

Outlet

TSS-440

TDS-2630

TSS-788         Cr-2.6

TDS-3200

TSS-416

BOD-42        TDS-3900


	The 
deficiencies 
noted in the inspection of 18.7.07 may 
be 
communi-

cated to the
 unit and 
time given
 upto 31.12.07 to correct the deficiencies. The lastest 
inspection 
of sept. 
indicates that TDS parameters not meeting the  norms.

It was also
 found that 
against the 
installed 
capacity of 
12 MLD, the
 CETP 
Society is 
operating it 
at only 1.0 
MLD. This 
indicates that it is grossly under utilized and individual 
connections
 to the 
conveyance
 system are
 severely 
limited. 

The 
Committee 
felt that the
 SCN should be issued to the Society to ensure that 
the 
connection
 of individual unit shall be connected to the conveyance 
system to 
maximize 
capacity 
utilization.

 The said 

CETP 

Societies 

Discharging

 its functions

 under 

Section 4 

under Rule

 3(i) to obtain requisite information regarding individual

 connections

 with 

conveyance 

system leading to CETP. This information to be furnished

 to DPCC

 and to the 

Appropriate

 Authority to

 invoke 

penalty under Chapter 4, Section 19 & 20 of the CETP Act

, 2000.
The society
 will submit 
a Bank 
Guarantee of Rs. Two Lakhs Fifty Thousands (valid for 
Six months) 
and also 
submit an 
affidavit to confirm correction of deficiencies by 31.12.07.
 BG will be 
forfeited if the corrections are not done by 31.12.2007. 

The copy 
should be 
sent to MD
 (DSIDC) and Comm. of Industries.  


Chairman     Member Secretary
SEE
       Dr. S.K Gupta             M. Dwaraknath                 EE 
          
 AEE 
DPCC
       DPCC

    MSWM Cell    Member (Acd. Inst)   Member (Env. Deptt.)     MSWM Cell   MSWM Cell

                                          Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007

	Name
	Decision taken on 26.06.2007
	Action Taken
	Consent Status
	Status
	Decision

	7.

SMA Indl. Area 

CETP (12 MLD) 
	MS, DPCC to issue a letter to MD, DSIDC, Commissioner of Industries & President, CETP Society to  remove the deficiencies observed by the DPCC officials during the inspection on 13-04-07, If they want Consent .
	Letter  issued on 08.08.2007                            

              
	Consent to operate issued on 15.09.04 to DSIDC for period of three year and valid up 27.07.07.

CETP society submitted application for consent to operate on 11.04.07.
	No reply received from CETP society and Commissioner of Industries regarding rectification of deficiencies. However, DSIDC has submitted a letter dated 03.08.2007 stating that the CETP has already been transferred under the CETP Act to CETP Society. The appropriate authority for initiating action is Jt. Commissioner of Industries. 
· During the inspection on 19.07.07 the following were observed.
· During the inspection CETP was not in operation since last few days. 

· During inspection it was observed that waste water is being thrown out side of the premises on public land along with silt / sludge. Due to that a pond has become in existence near railway line. 

· The sludge which is generated from the process is not being stored as per the guide lines of storage of Hazardous Waste Rules. At present it is being dumped in open raw land. 

· It is come to the notice that Waste Water and silt / sludge from equalization tank are being removed by the order / direction of DSIDC.

· The existing conveyance system to CETP still choked. Due to that total quantity of Waste Water is not being coming / being received in CETP. As informed DJB is in process of cleaning conveyance system.
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during last three months are as under:
Sept

Aug

July

Inlet

Outlet

Inlet

Outlet

Inlet

Outlet

pH- 4.0           TSS-572             Ni-3.8         Cr-4.9

TDS-3140

pH- 5.3    TSS-536      Ni-3.1           Cu-4.2              Cr-2.5    

TDS-3000

TSS-444    

TDS-3690


	The unit was inspected on 19.7.07 and gross deficiencies were found. Also the sept. report show TDS in excess of the norms . 

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 1.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.
The society will submit a Bank Guarantee of Rs. Five Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done by 31.12.2007. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.  


Chairman     Member Secretary
SEE
       Dr. S.K Gupta             M. Dwaraknath                 EE 
          
 AEE 
DPCC
       DPCC

    MSWM Cell    Member (Acd. Inst)   Member (Env. Deptt.)     MSWM Cell   MSWM Cell

Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Name
	Decision taken on 26.06.2007


	Action Taken
	Consent Status
	Status
	Decision

	8.

GTK CETP 

(12 MLD) 
	A letter under the signature of                Chairman, DPCC to be issued   to MD, DSIDC with a copy to Commissioner of Industries & President, CETP Society asking to apply for consent to operate within a month and remove the deficiencies observed.
	DO letter was issued on 17.07.07              .
	CETP Society has not applied for Consent to operate so far.
	· Consent application not received from CETP society, 

· No reply received from CETP society and Commissioner of Industries regarding rectification of deficiencies. However, DSIDC has submitted a letter dated 03.08.2007 stating that the CETP has already been transferred under the CETP Act to CETP Society. The appropriate authority for initiating action is Jt. Commissioner of Industries. 
· During the inspection on 19.07.07, the following were observed.
· The flow meter installed in the inlet of CETP was not functioning as same was out of order. 

· Pressure gauges attached to ACFs and DMFs not in operational condition.

· One floating aerator of equalization tank found out of order.

· Sludge kept in open. There is no space for storage of sludge at present.

· Poly tech as treatment chemical, is being used in place of Alum

· Flow intake range 2-2.5 MLD

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during last three months are as under:
Sept

Aug

July

Inlet

Outlet

Inlet

Outlet

Inlet

Outlet

TSS-970        Cu- 4.1           Cr-3.4    

TDS-3850

TSS-1068        Cu- 3.9          Cr-10.6  

_

_

TDS-2120


	The unit was inspected on 19.7.07 and gross deficiencies were found. Also the sept. report show TDS in excess of the norms . 

CETP society is also directed to submit application for Consent to Operate immediately.

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 2.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

 The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.
The society will submit a Bank Guarantee of Rs. Five Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done by 31.12.2007. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.  


Chairman     Member Secretary
SEE
       Dr. S.K Gupta             M. Dwaraknath                 EE 
          
 AEE 
DPCC
       DPCC

    MSWM Cell    Member (Acd. Inst)   Member (Env. Deptt.)     MSWM Cell   MSWM Cell

                                                                          Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Name
	Decision taken on 26.06.2007
	Action Taken
	Consent Status
	Status
	Decision

	9.

Lawrence Road CETP (12 MLD) 
	M.S, DPCC to issue a letter to MD, DSIDC, Commissioner of Industries & President, CETP Society to apply for  consent to operate and remove the deficiencies observed by the DPCC officials during the inspection on 17-04-07.
	Letter issued on 08.08.2007.                            

              
	Consent to operate issued on 15.09.04 to DSIDC for period of three year and valid up 27.07.07.

Not applied for Consent  after  expiry.


	· Consent to operate expired on 27-07-07 and no consent application/reply received from DSIDC/CETP society/Commissioner of Industries in respect of letter dated 08.08.2007. 

· During the inspection on 12.307.07, the following were  observed  
· Flow intake ranges App. 1-2.0 MLD.

· One vacuum filter (out of 2) found in non operational condition.

· 2 ACFs out of 6 nos. and 3 DMFs out of 9 nos. were found operational during the inspection.

· Small quantity of effluent going out of the premises, which is emanating from Grit Chamber, with out any treatment.

· Dosing of Bleaching powder not being carried out.

· Pre chlorination as well as post chlorination were found non operational.

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during last three months are as under:
Sept

Aug

July

Inlet

Outlet

Inlet

Outlet

Inlet

Outlet

TSS-700

TSS-112      BOD-66    TDS-2630       Sulphide-5.6

TSS-372

BOD-64    TDS-3810

TSS-928

BOD-40         Cl-1220          TDS-5100


	Inspection of 12.7.07 gross deficiencies which have not been rectified the lab reports indicate several norms be flouted. 

It was also found that against the installed capacity of 12 MLD, the CETP Society is operating it at only 2.0 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.
The society will submit a Bank Guarantee of Rs. Five Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done by 31.12.2007. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.  


Chairman     Member Secretary
SEE
       Dr. S.K Gupta             M. Dwaraknath                 EE 
          
 AEE 
DPCC
       DPCC

    MSWM Cell    Member (Acd. Inst)   Member (Env. Deptt.)     MSWM Cell   MSWM Cell

Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Name
	Decision taken on 06.06.2007
	Action Taken
	Consent Status
	Status


	Decision

	10.

OKHLA 

CETP

 (24 MLD) 

	MS, DPCC to issue a letter to the society to remove the deficiencies observed by the DPCC officials during the inspection on 11-04-07.

 A letter to be issued to the Society to create additional HW storage facility in the CETP premises by the society to keep the generated HW from the CETP in accordance with HW Rules, Considering the recommendation of SCMC. 

	SCN issued on 25-07-2007, and copy of minutes of meeting sent to SEE (H.W.).

              
	Consent to operate issued on 15.09.04 to DSIDC for period of three year and valid up 27.07.07.

CETP society submitted application for renewal of consent to operate on 13.02.07.
	· CETP Society submitted the consent application for renewal of  consent on 13-02-07.

SCN issued to the Society to remove the deficiencies observed by the DPCC officials during the inspection on 11-04-07.

· No reply received from CETP Society in respect of letter dated 25.07.2007 . CETP Society has submitted aletter on 06.09.07 that they have already constructed the additional storage capacity for storage of Haz. Waste.
  During the Inspection on 23.07.2007, following were observed :- 

· As reported both REPS I & II operated and maintained by DSIDC.

· Flow observed to be in the range of   0.9 – 3.4 MLD against installed capacity of 24 MLD.

· Pressure gauges attached to DMF  found not in operational condition.

· One aerator (out of two), one alum mixture was found out of order, and flow meter at inlet of CETP was not found at site, as reported same was sent to repair.

As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during last three months are as under:
Sept

Aug

July

Inlet

Outlet

Inlet

Outlet

Inlet

Outlet

TSS-260

BOD-34       TDS-2440

Cr-3.3

TDS-2495

_

BOD-36      TDS-2800


	The deficiencies found on inspection on 11.4.07 have not been rectified in full. The deficiencies noted on 23.7.07 may be communicated to the society. The lab report show BOD, TDS above the norms 

It was also found that against the installed capacity of 24 MLD, the CETP Society is operating it at only 3.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the Society to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The said CETP Societies discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.
The society will submit a Bank Guarantee of Rs. Ten Lakhs (valid for Six months) and also submit an affidavit to confirm correction of deficiencies by 31.12.07. BG will be forfeited if the corrections are not done by 31.12.2007. 

The copy should be sent to MD (DSIDC) and Comm. of Industries.


Chairman     Member Secretary
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Name
	Decision taken on 26.06.2007
	Action Taken
	Consent Status
	Status


	Decision



	11.

NARELA CETP (22.5 MLD)
	Reminder letter under the signature of Chairman, DPCC to MD, DSIDC
	DO letter was issued on 17.07.07.
	Consent to establish granted on 20.01.04 for a period one year. DSIDC applied for consent to operate on 03.03.06. 
	In response of D.O.Letter,  Reply dated 03.8.07 received from MD-DSIDC that test reports quoted are of Dec.2006 when plant was under maintenance and subsequent results submitted by DPCC have shown that the plant is meeting the norms. However, as per the DPCC laboratory latest report dated 26.07.2007, reveals that parameter of BOD (33 mg/l) & TDS (4070) are not meeting the prescribed standard. As per DPCC lab report dated 14.09.07, BOD (32mg/l) found exceeding the prescribe standards. However, as per DPCC lab report dated 10.10.07, final outlet discharge effluent found meeting the prescribe standards.

· During the inspection on 30.07.07, the following were  observed  
· Flow intake range -   7-8 MLD. 

· Flow meter installed at inlet of CETP found out of order. 
· No chemical dosing being done due to non-availability of chemical.
· Significant quantity of silt/sludge found in grit chamber, equalization tanks, tube settler & aeration tank.
· Only two aerators (out of 6 nos.) found in operational condition.
· All ACF (14 nos.) found not in operational during the inspection.
· Regular testing of the effluent is not being done in the laboratory situated in the CETP.
· No flow meter installed at outlet of CETP. 
As per DPCC analysis report, variation/ deviation from the prescribed norms for CETP during last three months are as under:
Sept

Aug

July

Inlet

Outlet

Inlet

Outlet

Inlet

Outlet

**

**

_

BOD-32

**

**


	While the unit showed compliance of the norms in the Sept. In the inspection 13.7.07 some deficiencies were found. The unit may correct all its deficiencies by 31.12.2007, failing which a BG of Rs. 5 lakh will be impose on the unit. 

It was also found that against the installed capacity of 22.5 MLD, the CETP is operating it at only 1.5 MLD. This indicates that it is grossly under utilized and individual connections to the conveyance system are severely limited. 

The Committee felt that the SCN should be issued to the DSIDC to ensure that the connection of individual unit shall be connected to the conveyance system to maximize capacity utilization.

The DSIDC discharging its functions under Section 4 under Rule 3(i) to obtain requisite information regarding individual connections with conveyance system leading to CETP. This information to be furnished to DPCC and to the Appropriate Authority to invoke penalty under Chapter 4, Section 19 & 20 of the CETP Act, 2000.
The copy should be sent to MD (DSIDC) and Comm. of Industries. 
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Name
	Decision taken on 26.06.2007
	Action Taken
	Consent Status
	Status


	Decision

	12.

Okhla Industrial Estate CETP ( 1.2 MLD)
	Meeting of Dr. B.K Guha Committee to be convened for deciding the issues of the necessity of remaining 03 CETPs as directed by EPCA. The recommendation of the committee may be sent to the EPCA.


	A meeting of B.K. Guha committee was held on 03.08.2007. Minutes of meeting/ recommendation of the committee are being   sent to EPCA.                       

              
	DSIDC applied for Consent to Establish
	· DSIDC applied for Consent to Establish on 06-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and recommended that an independent CETP may be installed for this industrial area.

                               
	Member Secretary, DPCC to study Dr. BK Guha Committee report and discuss with Prof. S.K. Gupta. Committee will be taken up this matter in next meeting. 
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                                                                          Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Name
	Decision taken on 26.06.2007
	Action Taken
	Consent Status
	Status


	Decision

	13.

Najafgarh Road Industrial area, CETP ( 9.6 MLD)

	Letter to be issued under the signature of Chairman, DPCC to MD, DSIDC, requesting to inform DPCC about the action taken for resuming the construction work of CETP.
	DO letter was issued on 17.07.2007.              
	DSIDC applied for Consent to Establish
	· DSIDC has submitted a letter dated 03.08.2007 in respect of DO letter 17.07.2007, that the EPCA has already directed not to go for further construction in view of spare capacity in other functional CETPs. As regards settling the dispute with the contractor, DSIDC looking into it as per the terms of the contract separately.

· DSIDC applied for Consent to Establish on 03-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and recommended that this area should have separate CETP, since there is no surplus capacity in the CETP in the nearby vicinity. 
	Member Secretary, DPCC to study Dr. BK Guha Committee report and discuss with Prof. S.K. Gupta. Committee will be taken up this matter in next meeting.
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Name
	Decision taken on 26.06.2007
	Action Taken
	Consent Status
	Status


	Decision

	14.

Mohan Co-operative Industrial Estate CETP (1.8 MLD)
	Meeting of Dr. B.K Guha Committee to be convened for deciding the issues of the necessity of remaining 03 CETPs as directed by EPCA. The recommendation of the committee may be sent to the EPCA.
	A meeting of B.K. Guha committee was held on 03.08.2007. Minutes of meeting/recommendation of the committee are being   send to EPCA.                       


	DSIDC applied for Consent to Establish
	· DSIDC applied for Consent to Establish on 06-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and recommended that the effluent from the Mohan Co-op. Industrial Estate may be treated in the CETP at Okhla Industrial Area.


	Member Secretary, DPCC to study Dr. BK Guha Committee report and discuss with Prof. S.K. Gupta. Committee will be taken up this matter in next meeting.
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SEE
       Dr. S.K Gupta             M. Dwaraknath                 EE 
          
 AEE 
DPCC
       DPCC

    MSWM Cell    Member (Acd. Inst)   Member (Env. Deptt.)     MSWM Cell   MSWM Cell

                                                                        Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Name
	Decision taken on 26.06.2007
	Action Taken
	Consent Status
	Status


	Decision

	15.

Naraina Industrial Area, CETP ( 21.6 MLD)
	To carry out an inspection and place the inspection report in next CMC meeting for decision.
	Inspection was carried out on 23.07.2007. 
	DSIDC applied for Consent to Establish
	· DSIDC applied for Consent to Establish on 02-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

·  EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and it was appraised by the representative of DSIDC that CETP is under installation and it is at final stage of construction and after commissioning of the same may be handed over to CETP Society of the area. 

Inspection of CETP was carried out by DPCC officials on 23.07.2007 and following were  observed:

· CETP was under construction.

· Most of the units of CETP mentioned in layout plan have been completed.

· With regards to civil work most of the work have been completed except road and drainage work.

· With regard to electrical work cabling & lighting work are yet to be done. Same is under progress.

· Pipe fitting under progress in chemical dosing system, sludge thickener & DMF/ACFs.

· Electrical panel was also found under installation.

· There are so many machinery are yet to be installed and also lots of works are pending as observed at site.

· The representative of the construction agency i.e. M/s. SPML told that due to non availability of funds the work is not being done fastly.


	The CETP is reported under construction for a long time. MS may write to MD (DSIDC) to complete this work by 31.12.07 and handover to CETP society by 31.12.07.
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Decisions taken by CMC (MSW) in its 5th Meeting held on 19.10.2007
	Name
	Decision taken on 26.06.2007
	Action Taken
	Consent Status
	Status


	Decision

	16.

Anand Parvat  CETP ( 24 MLD)
	Meeting of Dr. B.K Guha Committee to be convened for deciding the issues of the necessity of remaining 03 CETPs as directed by EPCA. The recommendation of the committee may be sent to the EPCA.


	A meeting of B.K. Guha committee was held on 03.08.2007. Minutes of meeting/ recommendation of the committee are being   sent to EPCA.                       

              
	DSIDC applied for Consent to Establish on 05.08.02.


	· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and recommended that an independent CETP may be installed for this industrial area.

                               
	Member Secretary, DPCC to study Dr. BK Guha Committee report and discuss with Prof. S.K. Gupta. Committee will be taken up this matter in next meeting.


Chairman     Member Secretary
SEE
       Dr. S.K Gupta             M. Dwaraknath                 EE 
          
 AEE 
DPCC
       DPCC

    MSWM Cell    Member (Acd. Inst)   Member (Env. Deptt.)     MSWM Cell   MSWM Cell

Agenda For Meeting(CETP)
	S. No.
	Name of CETP
	Installed Capacity
	Operating Agency
	Intale flow (Sept)

	1
	Mayapuri
	12 MLD
	CETP Society
	4.2 MLD

	2
	Mangolpuri
	2.4 MLD
	CETP Society
	1.5 MLD

	3
	Badli
	12 MLD
	CETP Society
	1.5 MLD

	4
	Wazirpur
	24 MLD
	CETP Society
	3.5 MLD

	5
	Jhilmil
	16.8 MLD
	CETP Society
	5 MLD

	6
	Nangloi
	12 MLD
	CETP Society
	1 MLD

	7
	SMA
	12 MLD
	CETP Society
	1.5 MLD

	8
	GTK Road
	12 MLD
	CETP Society
	2.5 MLD

	9
	Lawrence road
	12 MLD
	DSIDC
	2 MLD

	10
	Okhla
	24 MLD
	CETP Society
	3.5 MLD

	11
	Narela
	22.5 MLD
	DSIDC
	1.5 MLD

	12
	Najafgarh road
	9.6 MLD
	Construction suspended
	 

	13
	Naraina
	21.6 MLD
	Under construction by DSIDC
	 

	14
	Okla Estate
	1.2 MLD
	Kept in abeyance by EPCA
	 

	15
	Anand Parbat
	24 MLD
	Kept in abeyance by EPCA
	 

	16
	Mohan co-operative estate
	1.8 MLD
	Kept in abeyance by EPCA
	 



Agenda For Meeting(MSW)

	S. No.
	Name of Unit
	Address

	1
	Timarpur Incineration Plant Site
	Timarpur


Agenda For Meeting(TPS)
	S. No.
	Name of Power Plant
	Address

	1
	Pargati Power Corp. Ltd
	Bawana

	2
	Rajghat Power Station
	Rajghat

	3
	Pargati Power Station
	ITO

	4
	I. P. Gas Turbine Power Plant
	ITO

	5
	NTPC, BTPS
	Badarpur

	6
	BTPS (Proposed -1000MW unit)
	Badarpur

	7
	I P Thermal Power Station
	IP Estate


Agenda For Meeting (Reference Cases)
	S. NO.
	Reference

	1
	Report of malpractices by Wazirpur Associations and harasment of factory owners of non polluting units.

	2
	Representation received from M/s Industrial Carbons Pvt. Ltd regarding working of activated carbon filters in CETPs and for setting up a joint venture for regeneration facility in Delhi.


Agenda For Meeting(WTP)

	S. No.
	Name 
	Capacity

	1
	Haiderpur Water Treatment Plant
	200 MGD

	2
	Nangloi Water Treatment Plant
	40 MGD


Agenda For Meeting(STP)

	S. No. 
	Name of STP
	Installed capacity
	Date of sampling
	Type of treatment

	1
	Dr. Sen Nursing Home
	2.2 MGD
	05.09.07
	Physio-chemical + Biological

	2
	Delhi Gate
	2.2 MGD
	05.09.07
	Physio-chemical + Biological

	3
	Kondli Phase-I
	10 MGD
	26.09.07
	Biological

	4
	Kondli Phase-II
	25 MGD
	26.09.07
	Biological

	5
	Kondli Phase-III
	10 MGD
	26.09.07
	Biological

	6
	Oxidation pond (Nehru Vihar)
	6 MGD
	28.09.07
	Oxidation Pond

	7
	Kesho pur (Plant no. I & II)
	60 MGD
	25.09.07
	Biological

	8
	Mehrauli
	5 MGD
	12.09.07
	Biological

	9
	Yamuna Vihar Ph-I
	10 MGD
	21.09.07
	Biological

	10
	Yamuna Vihar Ph-II
	10 MGD
	21.09.07
	Biological

	11
	Rithala Ph-I
	40 MGD
	21.09.07
	Biological

	12
	Rithala Ph-II
	40 MGD
	21.09.07
	Biological

	13
	Pappan kalan
	20 MGD
	25.09.07
	Biological

	14
	Najafgarh
	5 MGD
	25.09.07
	Biological

	15
	Nilothi
	40 MGD
	19.09.07
	Biological

	16
	Rohini
	15 MGD
	21.09.07
	Biological

	17
	Coronation Pillar (Ph-I, II, III and old clarifier)
	40 (4 x 10) MGD
	28.09.07
	Biological

	18
	Vasant Kunj (Plant 1 & 2)
	5.2 MGD
	26.09.07
	Biological

	19
	Narela
	10 MGD
	28.09.07
	Biological

	20
	Okhla (Plant -I, II, III & IV)
	124  MGD (12+30+37+45)
	12.09.07
	Biological

	21
	Okhla (Plant -V)
	16 MGD
	12.09.07
	Biological

	22
	C Dot Campus (Mehrauli)
	125 kLD
	 
	 

	23
	Holambi
	2 MGD
	 
	 

	24
	Bakarwala
	3 MGD
	 
	 

	25
	Molarband
	3 MGD
	 
	 

	26
	Tikri khurd
	2 MGD
	 
	 

	27
	Gitorni
	5 MGD
	 
	 

	28
	Pusa Campus
	29 MGD
	 
	 

	29
	CTO Project, Mathura lane, Janpath
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