Agenda for 16th CMC (MSW Cell) meeting to be held on 20.04.2010
16th meeting of the Committee constituted for deciding the consent under the Air and Water Acts, for CETPs, STPs, WTPs & Power Plants cases, Special Reference cases and follow up action on the pending issues of the Local Area Environment Committee, is scheduled to be held on 20.04.2010.
Agenda 1- Construction and demolition (C & D) waste processing and recycling unit at Jahangirpuri, Delhi.
Agenda 2 - Cases of CETPs – w.r.t 16 CETPs.
Agenda 3 - Cases of STPs – w.r.t. 28 STPs.
Agenda 4 - Cases of Water Treatment Plants – w.r.t seven (7) plants.
Agenda 5 - Follow up action on the pending issues of the Local Area                         Environment Committee:

a) Matter regarding effluent generated in Patparganj Industrial Area.

b) Matter regarding conveyance system of WIA.
c) Removal of encroachment by DDA in WIA.

d) Construction of Road in WIA by MCD.’

e) Matter regarding illegal hazardous waste dumping sites.  

f) Matter regarding TSDF site at Ghumenhera.

g) Matter regarding gas supply to WIA.

h) Matter regarding E-waste.
Agenda 6- Cases of power plants w.r.t 8 power plants. 
Agenda 7- Cases of Municipal Solid Waste Management Project and Slaughter                    House- 17 units.

************************************
Agenda No. 1

Construction and Demolition (C&D) Waste Project of M/s IL&FS Waste Management & Urban Services Limited

Name of Unit:  M/s IL&FS Waste Management & Urban Services Limited,                           adjacent to Block-31, Gate No. 1, Hanuman Mandir Road,                           Near MCD Colony, Jahangir Puri, Delhi-110033 (near                           Prayas Building).
Activity: Processing of Construction and Demolition Waste Debris.

Consent Status:
Applied for Consent to Establish under Air & Water Acts on 13.07.2009.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Consent to Establish under the Air & Water Acts granted to the unit since it is the project related to Climate Change Agenda of Delhi; with condition that unit shall take adequate measures and ensure proper channelization/ control system for fugitive dust emissions from various operations and other activities of the unit. Issue Consent to Establish without waiting for the minutes.

Action taken/ Status after the meeting held on 19.01.2010:

1. Consent to Establish under Air and Water Acts issued on 20.01.2010.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
Shift to BMWM Cell, as the matter is being dealt by them.
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Agenda No. 2
Jhilmil & Friends Colony Indl Area CETP ( 16.8 MLD)
Consent status of CETP

· Consent to operate issued on 28.02.07 to CETP society for period of three years and valid up 07.01.2010. 

· Applied for Renewal of Consent on 04.01.2010.
· Applied for renewal of authorization under HMW Rules on 26.12.2006
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier.
Action Taken Report
· A letter regarding rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier  was issued on 17.02.10
· A letter was issued on 16.02.10 regarding “Installation of TOC Analyzer/ BOD Biosensor at Jhilmil & Friends Colony Indl. Area CETP”.

· In response of our letter dated 17.02.10 a reply has received on 5.03.10 regarding the rectification of deficiencies. Copy of same is enclosed with agenda

· A letter was received on 29.03.10 regarding the “Installation of TOC Analyzer/ BOD Biosensor at Jhilmil & Friends Colony Indl. Area CETP” stating that Jhilmil CETP has being designed/ installed and commissioned on physio-chemical treatment process not on biological treatment technology and thus society feels no need to install TOC Analyzer/ BOD Biosensor.

CETP was inspected by team of DPCC officials on 29.03.10 and observations made are as under: 
· Flow meter installed after equalization tank found in operation. Meter reading- 33435
· Out of two equalization tank, at present only one equalization tank is in use and other one is being dried to de-silt the silt.
· Pressure gauge installed with 4 DMFs and 6 ACFs has not been replaced so far
· One vacuum filter found out of order and another is also not functioning properly.

· Cleaning of pre chlorination tank is required due to scum.

· No proper arrangement for removal of oil and grease.

· Suitable V- notch arrangement is required in Tube settler weir plate.
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	December, 09
	                     January, 10


	Inlet
	Outlet
	Inlet
	Outlet

	TSS-276          
	Cl-1500                  TDS-3450

Fluoride- 2.4
	-
	Cl-1100

	February, 10
	                     


	Cu-4.1          
	Cl-1020               
	
	


All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
Issue CTO(R). Also issue a letter for rectification of deficiencies observed during the last two inspections and indicating the parameters which are exceeding the prescribed limits during the monitoring except TDS and also ask the unit to submit fresh application for authorization under HWM Rules.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

     DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
GTK Road Indl Area CETP ( 6 MLD)
Consent status of CETP
· CTE issued to DSIIDC on 20.01.04 valid upto 19.01.05. 

· CTO issued to DSIIDC on 15.09.04 valid upto 27.07.07.

· Not applied for CTO(R ) by CETP society.
· Authorization under HMW Rules issued on 27.01.05 valid upto 26.12.07.

· Not applied for renewal of authorization.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier.
Also, issue a SCN for launching prosecution for not filing consent application in spite of number of letters.

Action taken report 
· A letter regarding rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier was issued on 18.02.10 and SCN for launching prosecution was issued 
· A letter was issued on 16.02.10 regarding “Installation of TOC Analyzer/ BOD Biosensor at GTK Road Indl. Area CETP”.
· In response to our letter dated 18.02.10 CETP has submitted its reply; copy of the same is enclosed with agenda. Further, in regard to launching prosecution CETP has submitted its reply, legal cell of DPCC has opinioned that “ gone through the records of the file it is very much clear that CETP Society has not applied for renewal of consent under water act 1974 apart from continuing deficiencies in meetings prescribed standards , despite numerous letters for rectification of deficiencies . Even after receiving notice for applying for consent and in absence prosecution shall be launched, CETP society had sent very wrong, baseless reply. ( page 419/c – 422/c) Further latest inspection still confirms the fact of deficiencies in meeting standards. In these circumstances for case must be considered for prosecution. 

	December, 09
	                     January, 10


	Inlet
	Outlet
	Inlet
	Outlet

	         
	               
	TSS -1156

        Zn - 6.05

Cr(T) -7.14
	Cl-1600

	                          February, 10
	                     

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-1072         
	Cl- 1120               
	
	


All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:

Issue letter to the Society directing them to apply for CTO (R) failure of which may lead to the appropriate action under the provisions of Air, Water Acts and CETP Act, with copy to Commissioner of Industries.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)

Lawrence Road CETP (12 MLD)
Consent status of CETP

· Consent to operate expired on 27-07-07. 
· Applied for renewal of consent on 14.12.2007. 
· Applied for renewal of authorization under HWM Rules on 06.12.07.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier.
Action Taken Report
· A letter regarding rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier was issued on 18.02.2010. But no reply received so far.
· A letter was issued on 16.02.10 regarding “Installation of TOC Analyzer/ BOD Biosensor at Lawrence Road CETP”.

CETP was inspected by team of DPCC officials on 26.03.2010 and observation made is as under: 
· Flow meter at inlet found non-operational.

· Ist equalization tank after the grit chamber is being used as a storage tank for two raw effluent.

· Out of two agitators in two equalization tanks only one agitation in second equalization tank is found operational.

· Cleaning of tube settlers is required. 
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	December, 09
	
January, 10

	Inlet
	Outlet
	Inlet
	Outlet

	Non Functional
	TSS- 304

Cr (Total)- 4.02
	BOD-37

Cl- 1200

TDS- 4490


	          February, 10
	
             


	Inlet
	Outlet
	Inlet
	Outlet

	TSS-284
	             BOD-44

           TDS-4820
	
	


All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
Issue CTO(R). Also issue a letter for rectification of deficiencies observed during the  inspection and indicating the parameters which are exceeding the prescribed limits during the monitoring except BOD  and also ask the unit to submit fresh application for authorization under HWM Rules.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Badli Industrial Estate CETP ( 12 MLD)
Consent status of CETP

· Consent to operate issued on 28.02.07 to CETP society for period of three years and valid up 28.12.09. 

· Applied for Renewal of Consent on 30.11.2009.
· Applied for Renewal of authorization under HWM Rules on 20.01.2009.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier.
Action Taken Report
· A letter regarding rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier was issued on 18.02.10.
· A letter was received from Badli Industrial estate CETP Society regarding “Maintenance of Conveyance System laid down in Badli Industrial Area” on 03.02.10.

· A letter was issued on 16.02.10 regarding “Installation of TOC Analyzer/ BOD Biosensor at Badli Industrial Estate CETP”.

· CETP submitted its reply to our letter issued on 18.02.10 stating that as mentioned in our letter in Para 2 regarding non compliance of certain parameters at inlet e.g TSS and Cr (Total), it is submitted that it depends upon effluent reaching the plant which also receives sewage water from the adjoining jhugies and other unauthorized adjoining colonies.

· Regarding conveyance system, they stated that it is clogged at several places and is overflowing on the road and getting mixed with open drains for which they have been in correspondence with DJB to take necessary measures to clean the system at regular intervals and remove the blockage of the system. 

· They also mentioned in letter that their TDS value has never crossed the prescribed norms except for one or two occasions. Further, there is no provision in the plant to control TDS and also requested to kindly withdraw the harsh penalty of imposing a bank guarantee.  

CETP was inspected by team of DPCC officials on 16.03.10 and observations made are as under: 
-  About 60% to 70% sludge is filled in equalization tank.

-  Out of two vacuum drum filters one is out of order.
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	
December, 09
	
             January, 10


	Inlet
	Outlet
	Inlet
	Outlet

	TSS-1690         Cr(T)-3.1
	             -
	TSS-644

Cu-5.44


	Fluoride-2.45


	February,10
	
             

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-488


	             TDS-2740
	
	


All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
Issue CTO (R). Also issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and ask the unit to apply for authorization under HWM Rules, within 1 month.

Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
MAYAPURI CETP  (12 MLD)
Consent status of CETP

· Applied for consent to operate on 07.05.07.

· Applied for renewal of authorization under HMW Rules on 07.05.07.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier.
Action Taken Report
· A letter regarding rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier was issued on 17.02.10
· A letter was issued on 16.02.10 regarding “Installation of TOC Analyzer/ BOD Biosensor at Mayapuri CETP”
· Reply is submitted by CETP society regarding our letter dated 17.02.10 in which they have mention about non compliance of parameters with prescribed norms stating that CETP has been designed for inlet parameters such as TSS,TDS,BOD, pH, COD. Rest of all parameters has not been considered while designing the plant. The inlet parameters are not controllable as we have no means to change the characteristics of inlet effluent received in the CETP. Since the plant is designed for only 5 parameters the parameters other than these like Cl, Fl, oil and grease etc. will not be treated upto the desired outlet parameters laid by DPCC.

·  Regarding TDS at the outlet it was decided that TDS is high due to extensive use of ground water. 

· For deficiencies observed during inspection CETP society clarified that they have 2 vacuum filter units which they use alternatively as per the requirement. They also mention that de-silting of grit chamber is done regularly .As per their procedure for cleaning the grit chamber , one of the grit chamber is closed for 4-6 hrs while all the flow through the other. At the evening when the grit is dry it is evacuated in morning.

· About sludge and scumming observed in equalization tank they stated that equalization tank has no underflow sludge valve, due to which cleaning of sludge deposited in the tank cannot be done. They also that all the mesh presents at different units are cleaned in every 2-3 hrs and the foaming in the final tank was observed due to turbulence created by the falling water.

· CETP society also conveyed that imposing bank guarantee is not justified and thus requested to waving off of bank guarantee imposed on them. 

CETP was inspected by team of DPCC officials on 12.03.10 and observations made are as under: 

· Sludge present in equalization tank.

· Media replacement work is being undertaken in DMFs.

· Flow meter installed after equalization pump house found in operation

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	December, 09
	
January,10

	Inlet
	Outlet
	Inlet
	Outlet

	-
	-
	TSS- 292


	Cl-1600

Fluoride-2.4


	February,10
	


	Inlet
	Outlet
	Inlet
	Outlet

	       TSS-408


	        TDS-2200
	
	


Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
Issue CTO (R) without waiting for minutes. Also Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and ask the unit to apply for authorization under HWM Rules, within 1 month.

Chairman
  M. S.        Member        Member
SEE
   EE
  AEE 

 DPCC         DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
MANGOL PURI CETP (2.4 MLD)

Consent status of CETP

· Consent to operate issued on 27.07.2007 and valid upto 04.02.2010.

· Not re applied for CTO.

· Authorization under HMW Rules issued on 27.01.05 valid upto 26.01.07

· Not applied for renewal of authorization under HMW Rules.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier.

Action Taken Report

· A letter regarding rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier was issued on 18.02.10

· A letter was issued on 16.02.10 regarding “Installation of TOC Analyzer/ BOD Biosensor at Mangolpuri CETP”.

· CETP submitted its reply regarding deficiencies observed in monthly monitoring stating that technical committee is looking after the proper functioning of the plant and the parameters Cl and TDS which are found to be exceeding permissible limits are not within their control as plant is not designed to control aforesaid parameters. DPCC’s suggestion for regular cleaning of scum in Aeration Holding Tank is being looked after and all necessary precaution shall be taken. 

· CETP submitted its reply regarding Installation of TOC Analyzer (s) on 08.03.2010 stating that the matter is being looked after for necessary compliance, and the compliance report will be intimated to DPCC in near future.

· A letter issued by CETP society on 5.03.2010 stated that DPCC’s request for deposition of Bank Guarantee has been discussed and considered, Managing Committee is of opinion that the problems cannot be solve through such deposits.

CETP was inspected by team of DPCC officials on 26.03.10 and observations made are as under:

· Flow meter is installed at Primary Clarifier found in operation. 

· No proper arrangements for sludge removal from sludge thickener.

· 3 DMFs and 2 ACFs found in operation.
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	

December, 09
	
January,10

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-512
	             TDS-5100


	TSS-384

Cu-3.1
	Cl-2700

TDS-5280

	       

February,10
	


	Inlet
	Outlet
	Inlet
	Outlet

	TSS-404
	             TDS-5620

                Cl-2150


	
	


All Values are in mg/l expect pH


Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010
Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and ask the unit to apply for CTO(R) under Air and Water Acts, within 1 month.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)

                                 Wazirpur Indl Area CETP ( 24 MLD)
Consent status of CETP

· Consent to operate issued on 23.02.07 and valid up 27.12.09. 

· Not Applied for Renewal of Consent.
· Applied for renewal of authorization under HMW Rules on 15.04.06.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier.
Action Taken Report
· A letter regarding rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier was issued on 17.02.10. 
· However no reply received so far.
· A letter was issued on 16.02.10 regarding “Installation of TOC Analyzer/ BOD Biosensor at Wazirpur Indl. Area CETP”
· CETP society replied to our letter issued on 16.02.10 regarding Installation of TOC Analyzer/ BOD Biosensor stating that they are discharging treated effluent to water body through a guard tank after proper homogenization and hence instrument may not be of any significance.

CETP was inspected by team of DPCC officials on 18.12.09 and observations made are as under:
· Flow meter at inlet of CETP (before receiving chamber) found non operational.

· Equalization tank is filled with significant quantity of sludge / silt.
· Vacuum drunk filter is under with maintenance.

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	December, 09
	
January, 10

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-412         

Cr (T)-52.2

Ni-15

Cu-25.4
	       TDS-5090

Sulphide- 3.8
	Non Functional


	February,10
	


	Inlet
	Outlet
	Inlet
	Outlet

	TSS-484     

Ni-47.5

Cu-35.5
	       TDS-4030


	


All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and ask the unit to apply for CTO (R) under Air and Water Acts and Authorization under HWM Rules, within 1 month.

Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)

DSIDC Nangloi & Udyog Nagar Indl Area CETP ( 12 MLD)
Consent status of CETP
· Applied for consent to operate on 27.06.2007.

· Applied for renewal of authorization under HWM Rules on 18.01.2007. 

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier.

Action Taken Report
· A letter regarding rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier was issued on 18.02.10.
· A letter was issued on 16.02.10 regarding “Installation of TOC Analyzer/ BOD Biosensor at DSIIDC & Udyog Nagar Indl Area CETP”
· A reply letter was received issued by CETP Society  regarding our letter issued on 18.02.10 stating that parameters like TDS, Chlorine, etc neither can be treated nor be eliminated from the effluent as the plant is not designed to treat these parameters. There is no process in CETP to control TDS and have also requested to wave the bank guarantee and issue consent to the plant. 

· In reply to our letter issued on 16.02.10 CETP society requested DPCC to provide them reliable sources with detailed information of TOC Analyzer(s) enabling them to install the same at CETP.

CETP was inspected by team of DPCC officials on 26.03.2010 and observations made are as under: 
· Two flow meters (one for udyog nagar and one for DSIIDC shed) found in operation.
· Replacement of filter cloth in one vacuum drums filter is required.
· Out of 9 DMFs & 6 ACFs, 4 DMFs and 3 ACFs are being used for one cycle and others are being used as standby.

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	December, 09
	
January, 10

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-464         
	          TDS-2350

Fluoride- 2.4
	TSS-332


	Cl-1800

TDS- 3460

Fluoride- 2.45


	February, 10
	


	Inlet
	Outlet
	Inlet
	Outlet

	TSS-896       
	            Cl- 2400

        TDS-4750
	
	


All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
Issue CTO (R). Also Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and ask the unit to apply for authorization under HWM Rules, within 1 month.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)

SMA Indl Area CETP ( 12 MLD)
Consent status of CETP

· Consent to operate issued on 15.09.04 and valid up 27.07.07. 
· Applied for Renewal of Consent on 11.04.07.
· Not re-applied for renewal of consent. 

· Applied for renewal of authorization under HWM Rules on 11.04.07

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier.

Action Taken Report
· A letter rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier was issued on 17.02.10. However no reply has received so far.
· A letter was issued on 16.02.10 regarding “Installation of TOC Analyzer/ BOD Biosensor at SMA Indl Area CETP”.
CETP was inspected by team of DPCC officials on 16.03.10 and observation made is as under: 
· Flow meter at inlet found operational.

· Plastic drunks have been provided for collection of silt near grit chamber. 

As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	December, 09
	
January, 10

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-704  
Nickel-5.46  
Cr(T)-22.4

Oil & Grease- 22.4
	         TDS-3240


	TSS- 284

Cr (Total)-4.45
	         Cl-1400

Fluoride-2.3

	 

February, 10
	


	Inlet
	Outlet
	Inlet
	Outlet

	TSS-372  

	         TDS-2760

      Cl-1080
	
	     


Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and ask the unit to apply for CTO(R) under Air and Water Acts and Authorization under HWM Rules, within 30 days.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
                                         OKHLA CETP  (24 MLD)
Consent status of CETP

· Applied for Consent to Operate on 28.07.04. Consent to operate issued on 15.09.2004 and valid up 27.07.07. 
· Applied for renewal of consent on 13-02-07.
· Not re- applied for renewal of consent.
· Applied for renewal of authorization under HMW Rules on 13.02.07.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier. Also, inform the CETP Society that the sludge generated from the plant is to be treated as hazardous waste as per the notification/Rules of MoEF, GOI.
Action Taken Report
· A letter regarding rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier. Also, inform the CETP Society that the sludge generated from the plant is to be treated as hazardous waste as per the notification/Rules of MoEF, GOI was issued on 22.02.10. However no reply has been received so far.
· As decided in DPCC meeting held on 9.12.2009, a letter for installation of TOC Analyzer(s) or BOD Biosensor(s) at Okhla Indl. Area CETP was issued on 16.02.10

· In response to our letter dated on 16.02.10 CETP has submitted a copy of letter addressed to Chief Project Manager (E&M), DSIIDC stating that since the DSIIDC has constructed the CETP it is requested that they should only take necessary action.

CETP was inspected by team of DPCC officials on 12.03.2010 and observations made are as under: 
· Two flow meter found at intake but with totaliser.

· There are two aerators in equalization tank out of which one is out of order.
· There are 24 DP gauges installed with DMFS out of 24 gauges 18are out of order.
· There are 15 ACFS all are not in operation and effluent is being by passed.
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-

	                   December, 09
	
January, 10

	Inlet
	Outlet
	Inlet
	Outlet

	TSS-320      
  
	BOD-42                  TDS-2030


	TSS-280
	BOD-33


	                   February, 10
	


	Inlet
	Outlet
	Inlet
	Outlet

	TSS-388
	BOD-38           
	
	


All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:

Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and ask the unit to apply for CTO(R) under Air and Water Acts and Authorization under HWM Rules, within 1 month.

Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

 DPCC        
DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)                    

NARELA CETP (22  MLD)
Consent status of CETP
· Consent to establish granted on 20.01.04 for a period one year. Applied for consent to operate on 03.03.06. 
· Not Applied for Renewal of Consent.
· Applied for authorization under HMW Rules on 17.02.06.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:
Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier.

Action Taken Report
· A letter regarding rectification of deficiencies observed during the inspection and monitoring of waste water and submission of Bank Guarantee as sought earlier was issued on 17.02.10. However no reply has received so far.
· A letter was issued on 16.02.10 regarding “Installation of TOC Analyzer/ BOD Biosensor at Narela CETP”
CETP was inspected by team of DPCC officials on 31.03.10 and observations made are as under: 
- Flow meter installed near Raw Effluent Pumping Station is found non        operational. 

- All the 16 sludge drying beds are fully occupied and there is no further space for disposal of sludge.

- Treated water from clarifier is being by passed to the post chlorination tank as DMFs and ACFs are not working due to non availability of media. 

- No arrangement is made for proper disposal of slit from grit chamber. 
As per DPCC analysis report, parameters not complying with the prescribed norms during following months are as under:-
	

December, 09
	
January,10

	Inlet
	Outlet
	Inlet
	Outlet

	Zinc-20.4


	BOD-33

Cl-1800
	TSS- 272


	TSS-108

BOD-34

Fluoride-2.9


	Feburary,10
	


	Inlet
	Outlet
	Inlet
	Outlet

	TSS-372
	BOD-44

Cl-2350

TDS-5160

Fluoride-2.4
	
	


All Values are in mg/l expect pH
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
Issue letter for rectification of deficiencies observed during the inspection and monitoring of waste water and ask the unit to apply for CTO(R) under Air and Water Acts and Authorization under HWM Rules, within 1 month.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Udyog Vihar (Bawana) Industrial Area CETP ( 35 MLD)
Consent status of CETP

· Applied for Consent to Establish on 05.08.02. Consent to Establish was granted on 20.01.2004 for a period of one year.
· Not applied for Consent to Operate. 
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Ask the DSIIDC to apply for Consent to Operate and confirm the date of start of operation of CETP so that it will be considered for granting CTO.

Action Taken Report
· A letter asking to apply for Consent to Operate and confirm the date of start of operation of CETP so that it will be considered for granting CTO was issued on 22.02.10. However no reply has received so far.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:
Expedite the inspection and if required issue reminder letter to DSIIDC to apply for Consent to Operate and confirm the date of start of operation of CETP so that it will be considered for granting CTO.
Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)

Najafgarh Road Industrial area, CETP ( 9.6 MLD)
Consent status of CETP

· DSIDC has submitted a letter dated 03.08.2007 in respect of DO letter 17.07.2007, that the EPCA has already directed not to go for further construction in view of spare capacity in other functional CETPs. As regards settling the dispute with the contractor, DSIDC looking into it as per the terms of the contract separately.

· DSIDC applied for Consent to Establish on 03-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

Report was examined by Dr. B.K Guha Committee and recommended that this area should have separate CETP, since there is no surplus capacity in the CETP in the nearby vicinity.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009:

Member Secretary to write to new MD, DSIIDC to expedite the work of completion of CETP.

Action Taken Report

 A letter regarding Status as well as expected date for completion of CETPs was issued on 02.06.09.

DSIIDC has submitted a letter dated 01.06.09 wherein it has been informed that the constructional work of CETP has been awarded to M/S J.V. Associates in July-2002 but they abandoned in Oct., 2003 due to strong opposition  by  locals. Only 10 to 12 percent work has been carried out at site by the contractor before abandoning the work. No further work is being carried out in this CETP. DSIIDC has filed a case for recovery of the paid amount form the contractor. 

Further, the issue of construction of CETP Najafgarh Road was placed before the 226th meetings of the Board of Directors of DSIIDC held on 08.05.09 and it was desired by Board of Directors that DPPC should be requested to take up the matter with Commissioner of Industries regarding settlement of local protest, appropriateness of CETP and release of funds for the construction of CETP Najafgarh. 

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Member Secretary to call a meeting with DSIIDC to expedite the work of completion of CETP.

Action Taken Report
· Member Secretary, DPCC has convened a meeting on 26.02.2010 with     Sh. Sharad Kumar (Chief Plant Manager, DSIIDC) and minutes of meeting has been sent to DSIIDC for further necessary action. However no action taken report has been received so far.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.0410:

Issue D.O. letter to COI from MS, DPCC, with a copy to MD, DSIIDC. 


 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)

Naraina Industrial Area, CETP ( 21.6 MLD)

Consent status of CETP

· DSIDC applied for Consent to Establish on 02-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

·  EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and it was appraised by the representative of DSIDC that CETP is under installation and it is at final stage of construction and after commissioning of the same may be handed over to CETP Society of the area. 

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009:

Ask the DSIIDC to apply for Consent to Operate and confirm the date of start of operation of CETP.
Action Taken Report

A letter was issued on.28.05.09.

However no reply received.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:
Issue reminder to DSIIDC to apply for Consent to Operate and confirm the date of start of operation of CETP.
Action Taken Report
· A letter asking to apply for Consent to Operate and confirm the date of start of operation of CETP was issued on 22.02.10.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.0410:

Expedite the inspection and if required issue reminder letter to DSIIDC to apply for Consent to Operate and confirm the date of start of operation of CETP so that it will be considered for granting CTO.
 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Okhla Industrial Estate CETP ( 1.2 MLD)
Consent status of CETP

· DSIDC applied for Consent to Establish on 06-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

Report was examined by Dr. B.K Guha Committee and recommended that an independent CETP may be installed for this industrial area
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009:

No Action.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

No action.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.03.10:

No Action.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Anand Parbat CETP ( 24 MLD)

Consent status of CETP

· DSIDC applied for Consent to Establish on 05.08.02.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP. 

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and recommended that an independent CETP may be installed for this industrial area.

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009
No Action.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

No action.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.03.10:

No Action.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Agenda No. 3

Dr. Sen Nursing home Nallah STP  (2.2 MGD)

Consent Status 

Consent to Operate valid up to 25-02-08. 
Consent to operate (Renewal) was issued on 08.02.10 valid upto 12.05.11


Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009:

D.O. letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies. 

Action Taken Report
As decided in CMC (MSWM) D.O letters dated 04.06.09 were issued.  After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.   

Subsequent to the meeting of EPCA, a letter was issued to the unit regarding smell problem in Lodi Garden, as the treated water is supplied from this plant. No reply received.

Not applied for authorization under HWM Rules.
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue renewal of consent and ask the unit to apply for authorization under HWM Rules.

Action Taken Report
A letter dated 12.02.10 was received form the unit which stated that no Hazardous Waste is generated by the unit hence the authorization under HWM Rules is not required by it.

Consent to operate (Renewal) was issued on 08.02.10, in which the consentee was also asked to submit an application for authorization under HWM Rules. 
After examining the monthly analysis report for the months of Dec, 2009 to Feb 2010 it was found that parameters are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:

No Action.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Delhi Gate Nallah STP, (10 MLD)

Consent Status 

Consent to operate issued on 15.2.2007 & valid upto 11.10.09. 

Applied for Renewal of Consent on 03.02.10.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

No action
Action Taken Report
After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.  
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Ask the unit to apply for renewal of consent.

Action Taken Report
As the unit has already applied for renewal of consent on 03.02.10 thus we have not sent any letter for renewal of consent.

After examining the monthly analysis report for the months of Dec 2009 to Feb 2010 it was found that parameters are meeting the prescribed standards.  
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:

Issue CTO(R).

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
KONDLI STP , Ph-I (10 MGD)

Consent Status 

Consent to Operate issued on 20.08.2008 and valid upto 18.04.2009. 

Renewal of Consent to Operate issued on 08.02.2010 and valid upto 16.08.2012. 

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009:

D.O. letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies. 
Action Taken Report
As decided in CMC (MSWM) D.O letters dated 04.06.09 was issued.  After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.   
Unit has applied for CTO® on 17.08.09.
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue renewal of consent.

Action Taken Report
Renewal of Consent was issued on 08.02.10.

After examining the monthly analysis report for the months of Dec 2009 to  Feb, 2010 it was found that parameters are meeting the prescribed standards in Feb 2010 ; However parameters are not meeting the prescribed standards w.r.t Phosphate in Jan 2010 . The plant was found non operational due to maintenance in the month of Dec 2009

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:

No Action.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
KONDLI STP, Ph-II  (10 MGD)
Consent Status 

Consent to Operate issued on 20.08.2008 and valid upto 18.04.2009. 
Consent to Operate issued on 08.02.2010 and valid upto 16.08.2012. 
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009:

D.O. letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies. 
Action Taken Report

As decided in CMC (MSWM) D.O letters dated 04.06.09 was issued. After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are not meeting the prescribed standards.   
Unit has applied for CTO® on 17.08.09.
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue renewal of consent.

Action Taken Report
Renewal of Consent to operate was issued on 08.02.10
After examining the monthly analysis report for the months of Dec 2009 to Feb 2010 it was found that parameters are not meeting the prescribed standards w.r.t Phosphate in Feb 2010 ; However the it was found that  parameters are  meeting the prescribed standards  for the months of Dec 2009 and Jan 2010.
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:
Issue letter for rectification of deficiencies observed after analysis of treated effluent.
Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE    DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
KONDLI STP, Ph-III , (10 MGD)
Consent Status 

Consent to Operate issued on 22.09.05 and valid upto 02-12-07. Renewal of Consent issued on 20.08.2008 & valid upto 02.12.2010.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

No action

Action Taken Report
After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

No action, as the consent is valid.

Action Taken Report
After examining the monthly analysis report for the months of Dec 2009 to Feb 2010 it was found that parameters are not meeting the prescribed standards w.r.t phosphate in Feb 2010. However, it is found that parameters are meeting the prescribed standards in Jan 2010 and Dec 2009.

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:

Issue letter for rectification of deficiencies observed after analysis of treated effluent.
 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Nehru Vihar, Oxidation Pond STP (13.5 MGD)
Consent Status 
Consent issued on21.09.05 and  valid up to 28.11.07. 
Consent to operate (renewal) issued on 08.02.10 and valid up to 24.10.2010

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

No action

Action Taken Report
After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue renewal of consent.

Action Taken Report
Renewal of Consent to operate was issued on 08.02.10.

After examining the monthly analysis report for the months of Dec 2009 to Feb 2010 it was found that parameters are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:
No Action.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Keshopur STP (60 MGD (40+20)

Consent Status 

Consent to Operate issued on 21.09.05 and valid upto 24-09-07 for 60 MGD. 

Renewal of Consent to operate issued on 08.02.10 and valid upto 06.01.11. 

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009:

D.O. letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies. 

Action Taken Report

As decided in the CMC (MSWM) D.O letters dated 04.06.09 was issued.  After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are not meeting the prescribed standards, w.r.t TSS, BOD and Phosphate.   

Decision of Consent Management Committee (Orange) w.r.t cases of MSW Cell dated 19.01.2010:
Issue renewal of consent.

Also, issue letter to DJB to rectify the deficiencies to comply with the norms laid down.

Action Taken Report

Renewal of Consent was issued on 08.02.10 

A letter dated 15.02.10 was issued to DJB to rectify the deficiencies to comply with the norms laid down but no reply has been received so far.

After examining the monthly analysis report for the months of Dec 2009 to Feb 2010 it was found that both plants were under maintenance and were found non- operational for the month of Jan 2010 to Feb 2010. 

However for the month of Dec 2009 it was found that parameters are not meeting the prescribed standards w.r.t TSS, BOD and Phosphate.  
Decision of Consent Management Committee (Orange) w.r.t cases of MSW Cell dated 20.04.2010:

Issue letter for rectification of deficiencies observed after analysis of treated effluent.
 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Mehrauli  STP (5 MGD)
Consent Status 

Consent issued on 20.03.2007 & valid upto 15.12.09. 

Not Applied for Renewal of Consent.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

No action

Action Taken Report
After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.  
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue letter seeking application for renewal of consent.

Action Taken Report
A letter dated 12.02.10 has been issued, seeking application for renewal of consent; however no reply has been received so far.

After examining the monthly analysis report for the month of Dec 2009 it was found that parameters are not meeting the prescribed standards w.r.t TSS.
However the monthly analysis report for the months of Jan 2010 to Feb 2010 shows that parameters are meeting the prescribed standards. 

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:
Issue letter to the unit seeking application for CTO(R), with a copy to CEO, DJB.
 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Yamuna Vihar Phase –I STP (10 MGD)

Consent Status 

Consent to Operate issued on 28.2.2007 and valid upto 16.11.07. 

Renewal of Consent issued on 20.08.2008 valid upto 16.11.2010.

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

No action

Action Taken Report
After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.   
Decision of Consent Management Committee (Orange) w.r.t cases of MSW Cell dated 19.01.2010:

No action, as the consent is valid.

Action Taken Report
After examining the monthly analysis report for the months Dec 2009 of Feb 2010 it was found that parameters are meeting the prescribed standards for all the three months.  

Decision of Consent Management Committee (Orange) w.r.t cases of MSW Cell dated 20.04.2010:

No Action.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Yamuna Vihar Phase –II STP  (10 MGD)

Consent Status 

Consent to operate issued on 28.2.2007 valid upto 28.12.09. 

Renewal of consent issued on 08.02.10 valid up to 13.12.2012
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009:

D.O. letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies. 

Action Taken Report

As decided in CMC (MSWM) D.O letters dated 04.06.09 was issued. After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.   
Applied for Renewal of Consent on 14.12.09.

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue renewal of consent.

Action Taken Report

As decided in CMC (MSW) renewal of consent has issued on 08.02.10. 

After examining the monthly analysis report for the months Dec 2009 to Feb 2010 it was found that parameters are meeting the prescribed standards in the months of Jan to Feb 2010. However parameters are not meeting the prescribed standards w.r.t Phosphate in Plant 2 in Dec 2009  
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.10

No Action.
Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Rithala STP– Ph-I, (40 MGD)
Consent Status 

Consent to Operate valid upto 04.05.06. 
Applied for Renewal of Consent on 29.06.2006 and again on 01.07.09.

Renewal of Consent to Operate was issued on 08.02.10 valid upto 30.06.12. 

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

No action

Action Taken Report

After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.  
Applied for Renewal of Consent on 29.06.2006 and again on 01.07.09.
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue renewal of consent.

Action Taken Report

Renewal of Consent to Operate has been issued on 08.02.10.

After examining the monthly analysis report for the months of Dec 2009   to Feb 2010 it was found that parameters are not meeting the prescribed standards w.r.t. TSS in Feb 2010. However, it was found that parameters are meeting the prescribed standards for the months of Jan 2010 and Dec 2009
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:
Issue letter for rectification of deficiencies observed after analysis of treated effluent.
 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Rithala  STP– Ph-II, ( 40 MGD)

Consent Status 

Previous Consent valid upto 21.01.06. Applied for renewal of consent on 20.01.2006. 
Not  applied for renewal of consent.

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

No action

Action Taken Report
After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue letter seeking application for renewal of consent.

Action Taken Report
A letter dated 12.02.10 has been issued seeking application for renewal of consent. However, no reply has been received so far.

After examining the monthly analysis report for the months of Dec 2009 to Feb 2010 it was found that parameters are not meeting the prescribed standards w.r.t. Phosphate in Feb 2010 and Dec 2009 ; However  it was found that parameters are  meeting the prescribed standards  in Jan 2010.
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:

Issue letter for rectification of deficiencies observed after analysis of treated effluent and also seek application for CTO(R).
 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Papankalan STP ( 20 MGD)
Consent Status 

Consent issued on 25.08.2008 valid upto 06.01.2011.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009:

D.O. letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies. 

Action Taken Report
As decided in CMC (MSWM) D.O letters dated 04.06.09 was issued. After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

No action, as consent is valid.

Action Taken Report
After examining the monthly analysis report for the months of Dec 2009 to Feb, 2010 it was found that parameters are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:

No Action.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Najafgarh STP, ( 5 MGD)
Consent Status 

Consent issued on 25.08.2008 valid upto 06.01.2011
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

D.O. Letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies. 

Action Taken Report

As decided in CMC (MSWM) D.O letters dated 04.06.09 was issued. After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

No action as consent is valid.

Action Taken Report

After examining the monthly analysis report for the months of Dec 2009 to Feb, 2010 it was found that parameters are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:

No Action.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Nilothi STP (40 MGD)

Consent Status 

 Consent to Operate expired in 02-12-06. 
 Consent issued on 08.02.2010 valid upto 25.11.2010

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

No action

Action Taken Report

After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue renewal of consent.

Action Taken Report

Renewal of consent has been issued on 08.02.10.

 Examination of the monthly analysis report for the months of Dec 2009 to Jan 2010 shows that the unit’s parameters are meeting the prescribed standards.   
Monthly analysis reports for the month of Feb 2010 shows that, for the unit parameters are not meeting the prescribed standards w.r.t. TSS.    
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:
Issue letter for rectification of deficiencies observed after analysis of treated effluent.
 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Rohini STP (15 MGD)

Consent Status 

Applied for Consent to operate on 01-05-07. 

Consent to Operate issued on 08.02.2010 valid upto 30.04.2010
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009:

D.O. letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies. 

Action Taken Report

As decided in CMC (MSWM) D.O letters dated 04.06.09 was issued. After examining the monthly analysis reports for the month of Aug., to Nov., 2009 it has been observed that during the time of monitoring STP found non-operational since March-2009.

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue Consent to operate.

Action Taken Report

Consent to operate was issued on 08.02.10 

After examining the monthly analysis reports for the months of Dec, 2009 to Feb 2010, it has been observed that during the time of monitoring STP was found non-operational due to no flow.

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:

Issue letter seeking application for CTO(R).

Issue an advisory letter to CEO, DJB regarding treatment of waste water from Rohini drain. 

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Coronation Pillar STP (40 MGD)

Consent Status

Consent to operate issued on 28.2.2007 valid upto 12.03.2009. 

Renewal of Consent to operate issued on 08.02.2010 valid upto 11.03.2012. 

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

No action
Action Taken Report
After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.   

Old clarifier found non operational during inspection on 09.11.2009 by the officials of lab.

Applied for renewal on 12.03.2009.
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue renewal of consent.

Action Taken Report
Renewal of Consent to operate has been issued on 08.02.2010. 

After examining the monthly analysis report for the months Dec 2009  to  Feb 2010 it was found that for the month of Feb 2010  parameters are meeting the prescribed standards for Ph-I, II & Old Clarifier however, parameters are not meeting the prescribed standards w.r.t  TSS, BOD, Phosphate for Ph-III . 
In Dec 2009 and Jan 2010 for  Phase I, II and III parameters are meeting the prescribed standards, However the Old Clarifier unit was found Non operational .    

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:

Issue letter for rectification of deficiencies observed after analysis of treated effluent.
Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Vasant Kunj STP (5.2 MGD)

Consent Status 

Consent to Operate issued on 22.09.05 valid up to 11-12-07. 

 Renewal of Consent to Operate issued on 08.02.10 valid up to 28-01-11. 

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

No action.

Action Taken Report
After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards in case of plant 1 but not by Plant II w.r.t Po4.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue renewal of consent.

Also issue a letter for rectification of deficiencies to comply with the norms laid down.

Action Taken Report
 A letter dated 15.02.10 has been issued for rectification of deficiencies to comply with the norms laid down but no reply has been received. 

 Consent to Operate (Renewal) issued on 08.02.10. 

After examining the monthly analysis report for the months Dec 2009  to  Feb, 2010 it was found that in Feb 2010 parameters are meeting the prescribed standards in case of plant 1 but not by Plant II w.r.t Po4.  
In Jan 2010, parameters are meeting the prescribed standards in case of plant II but not by Plant I w.r.t Po4.  
In Dec 2009 it was found parameters are meeting the prescribed standards.
CPCB has issued directions under section 18(1) (b) of the Water (Prevention and Control of Pollution) Act 1974 in the matter of discharge of treated sewage at Vasant Kunj STP to the lake on the District Park, Chaudhary Harsukh Marg, Safdarjung Enclave.

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:

Issue letter for rectification of deficiencies observed after analysis of treated effluent.
 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Narela STP (10 MGD)

Consent Status 

Consent to Operate valid upto 14.01.2005. Renewal of Consent issued on 7-11-2007 valid up to 13-1-2008. 
Applied for renewal of consent on 3-1-2008, valid upto 13.01.2011
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

D.O. Letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies.

Action Taken Report
As decided in CMC (MSWM) D.O letters dated 04.06.09 was issued.  After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue renewal of consent.

Action Taken Report
Renewal of consent was issued on 13.08.08, it is valid upto 13.01.2011.

 After examining the monthly analysis report for the month of Feb 2010 (as on 04.02.10) it was found that parameters are not meeting the prescribed standard w.r.t. Phosphate.   
However, another analysis report in the month of Feb 2010 (as on 22.02.10) shows that the parameters are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:

No Action.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
OKHLA STP , [Phase- I, II, III & IV, (12+30+37+45), Total 124 MGD)
Consent Status 

Consent to operate was granted by CPCB on 23.01.1987 (valid upto 31.12.88), 

Applied on 03.04.1998 issued by DPCC on 14.06.99 (valid upto 31.05.2000), 

Applied on 10.05.2000 issued by DPCC on 18.04.2001 (valid upto 17.04.2002).

Applied on 08.10.2002 issued by DPCC on 20.01.2004 (valid upto 17.04.2005).

Applied for renewal on 10.03.2005 for Phase I, II, III & IV Plant (124 MGD)
Consent is renewed for all the four phases on 03.06.2008 & valid upto 09.03.2011.

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

D.O. Letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies.

Action Taken Report
As decided in CMC (MSWM) D.O letters dated 04.06.09 was issued. After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards in case of plants 1,2 and 3. Plant 4 is not meeting the norm laid down for Po4.  

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue letter to DJB to rectify the deficiencies to comply with the norms laid down as PO4 is not within the limit.

Action Taken Report
A letter dated 12.02.10 was issued to DJB to rectify the deficiencies to comply with the norms laid down as PO4 is not within the limit, but no reply has been received so far.

However, the monthly analysis reports of Dec 2010 show that parameters are meeting the prescribed standards in case of plants 1,4; Plant 3 is not meeting the norm laid down for Po4 and Plant 2 is not meeting the standards of TSS, BOD  and Phosphate.
The monthly analysis report for the month of Feb 2010 show that parameters are meeting the prescribed standards in case of Plant 1 ; Not meeting the standards w.r.t phosphate for plant 2 and 4 : Not meeting the standards w.r.t BOD and Phosphate in Plant 3
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:
Issue letter for rectification of deficiencies observed after analysis of treated effluent.
 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Okhla STP,Phase-V (16 MGD)

Consent Status 

Consent is renewed on 29.05.2008 & valid upto 16.12.2010. 
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :
D.O. Letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies.

Action Taken Report
As decided in CMC (MSWM) D.O letters dated 04.06.09 was issued.  
After examining the monthly analysis report for the month of Nov 2009 found that STP is non-operational. 

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

No action, as consent is valid.

Action Taken Report
After examining the monthly analysis report for the months of Dec 2009 and  Feb 2010 it was found that, parameters are not meeting the prescribed standards w.r.t phosphate.   
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:

Issue letter for rectification of deficiencies observed after analysis of treated effluent.
 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
STP at C-DOT Campus, Chattarpur, Mehrauli, New Delhi-30. (125 KLD)

Consent Status 

Consent to operate expired on 12.4.2007.

Renewal of Consent issued on 03.06.2008 valid upto 10.03.2011.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

No action. 

Action Taken Report
After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Ask the unit to apply for renewal of consent as its validity is going to expire on 10.3.2010.

Action Taken Report
The letter for renewal of consent could not be issued as actual date of expiry is 10.03.11 but due to typographical mistake the validity was written as10.03.2010.

 After examining the monthly analysis report for the months of Jan 2010 and Dec 2009 it was found that parameters are meeting the prescribed standards for the month of Jan 2010.  However parameters are not meeting the prescribed standards w.r. t Phosphate for the month of Dec 2009
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:

No Action.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Bakkarwala STP, (3 MLD)
Consent Status 

Consent to Operate issued on 12.02.08 valid up to 20.05.2010.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

No action. 

Action Taken Report
After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

No action, as the consent is valid.

Action Taken Report
After examining the monthly analysis reports from  Dec 2009 to Feb 2010 it was found that parameters are not  meeting the prescribed standards w.r.t. TSS and BOD in Dec 2009 , parameters are meeting the prescribed standards in Jan 2010, However  parameters are not  meeting the prescribed standards w.r.t. TSS in Feb 2010.
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:
Issue letter for rectification of deficiencies observed after analysis of treated effluent and also seek application for CTO(R).
 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

  DPCC        DPCC        Env. Deptt.      Acd. Inst          (MSWM Cell)
Molar Band STP (3 MLD)
Consent Status 

Consent to Operate issued on 12.02.08 valid upto 20.05.2010.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

D.O. Letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies.

Action Taken Report
As decided in CMC (MSWM) D.O letters dated 04.06.09 was issued.  After examining the monthly analysis report for the month of Nov 2009 it was found that parameters are not meeting the prescribed standards w.r.t. TSS, BOD and Po4.   
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue letter for rectification of deficiencies to comply with the norms laid down.

Action Taken Report
A letter dated 12.02.10 has been issued for rectification of deficiencies to comply with the norms laid down.

A reply letter was received on 11.03.10 stating that Molar Band STP was handed over to Mr P.C. Sharma, SDW, DJB on 12.05.08; and thus he should be contacted for the rectification of deficiencies in the STP Plant.

After examining the monthly analysis report for the months of Dec 2009 and Feb 2010. It was found that for Feb 2010 parameters are not meeting the prescribed standards w.r.t. TSS, BOD and PO4. .

The plant was found Non operational at the time of monitoring in the month of 

Dec 2009.

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:
Issue letter for rectification of deficiencies observed after analysis of treated effluent and also seek application for CTO(R).
 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Holambi Kalan STP, (2 MLD)
Consent Status 

Consent to Operate issued on 14.05.04 valid upto 08.10.06.

Not applied for Renewal of consent.

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

D.O. Letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies.

Action Taken Report
As decided in CMC (MSWM) D.O letters dated 04.06.09 was issued.  The plant is non operational and is to be taken over by DJB from Dept of JJ Clusters.
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue letter seeking application for renewal of consent.

Also inspect and report to find out the operational status.

Action Taken Report
A letter dated 12.02.10 was issued seeking application for renewal of consent, but no reply has been received so far.
Also unit was inspected on 08.04.10 by the official(s) of DPCC and the findings are as under:
· At the time of inspection the unit was found Closed/non operational.

· As informed by the local authorities the unit has remained closed since the past two or two and a half years (approx).

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:
Issue a letter to DJB seeking clarification regarding non operation of the STP. 

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Tikri Khurd STP (2 MLD)
Consent Status 

Consent to Operate expired on 12.06.06. 
Not applied for renewal.

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

D.O. Letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies.

Action Taken Report

As decided in CMC (MSWM) D.O letters dated 04.06.09 was issued.  The plant is non operational and is to be taken over by DJB from Dept of JJ Clusters.

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue letter seeking application for renewal of consent.

Also inspect and report to find out the operational status.

Action Taken Report
As decided in CMC (MSWM) a letter was issued on 12.02.10. The unit has not submitted an application for renewal of consent so far. 
During inspection the plant was found closed/ non operational, as per local inquiry the unit has closed from last two years.
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:

Issue a letter to DJB seeking clarification regarding non operation of the STP. 

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Ghitorni STP,  (5 MGD)
Consent Status 

Not applied for consent.

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

D.O. Letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies.

Action Taken Report
As decided in CMC (MSWM) D.O letters dated 04.06.09 was issued.  Letter received from DDA stating that the plant is non operational since long due to absence of raw sewage to the plant.   

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:
Issue letter seeking consent application.

Also inspect and report to find out the operational status.

Action Taken Report
A letter dated 12.02.10 was issued seeking consent application, but no reply has been received so far.

Also unit was inspected on 09.04.10 by the official(s) of DPCC and the findings are as under:

· The unit was found closed. 

· As informed by Sh. Santram, Guard, DJB, telephonically the unit was closed / non-operational from last two-three Years (approx.). 
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:
Issue an advisory letter to CEO, DJB.

Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
STP at National Bureau of Plant Genetic Resources ICAR, Pusa Campus, (80 KLD)
Consent Status 

Consent to Operate expired on 07.06.07. 
Not applied for renewal of consent.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 :

Issue reminder for not meeting the norms & Bank Guarantee as sought earlier.   

Action Taken Report
Reminder was issued on 28.05.09 to comply with norms & Bank Guarantee Rs. 1 lakh. Letter dated 12.06.09 were received on 17.06.09 form NBPGR. And has submitted the Test Certificate from Delhi Water and General test Lab (P) Ltd. Forwarded by CPWD.  Test Certificate is for samples of waste water before inlet and waste water after outlet tested on 15.05.09 to 18.05.09 by Delhi Water & General Test Lab (P) Ltd. 302, B-11, Commercial Complex, Ranjeet Nagar, New Delhi-110008.
BG not submitted.
After examining the monthly analysis reports for the month of Nov 2009, it was found that parameters w.r.t. TSS; BOD & PO4 are not meeting the prescribed standards.

Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 19.01.2010:

Issue letter seeking application for renewal of consent and rectification of deficiencies to comply with the norms laid down for parameters TSS, BOD and PO4.

Action Taken Report

Letter dated 12.02.10 for seeking application for renewal of consent and rectification of deficiencies to comply with the norms laid down for parameters TSS, BOD and PO4. However, no reply received so far.

After examining the monthly analysis reports for the months Dec 2009 to Jan 2010, it was found  for the month of Jan 2010 ,  parameters are not meeting the prescribed standards w.r.t. TSS; BOD & COD. However; for the month of Dec 2009 Parameters are not meeting the prescribed standards w.r.t TSS and BOD 
BG not submitted.
Decision of Consent Management Committee (Orange) w.r.t. cases of MSW Cell dated 20.04.2010:

Issue a letter to the unit seeking application for CTO(R) with a copy to Director of National Bureau of Plant Genetic Resources ICAR.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Agenda No. 4
Haiderpur  Water Treatment Plant
Consent status:

· Consent to Establish issued on 08.02.10 valid upto 07.02.2011.

· Consent to Operate issued on 08.02.10 valid upto 12.02.2011.
Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 : 

D.O. Letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies. 

Action Taken Report

As decided in CMC (MSWM) D.O letter dated 04.06.09 was issued regarding operation and treatment of STPs.  A perusal of report of monitoring done in month of Nov., 2009 are meeting the prescribed standards.  
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue consent to establish and consent to operate.

Inform DPCC laboratory to monitor the quality of waste water discharged by the plant instead of analyzing the quality of drinking water.

Action Taken Report
· As decided in CMC (MSW) consent to establish and consent to operate was issued on 08.02.2010. 

· Further DPCC Laboratory has informed to monitor the quality of waste water discharged by the plant instead of analyzing the quality of drinking water.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:

No Action.
 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
                                 Nangloi Water Treatment Plant
Consent status:

· Consent to Establish issued on 03.11.08 valid upto 09.10.2009.

· Not applied for CTO. 

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 : 

D.O. Letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies. 

Action Taken Report

As decided in CMC (MSWM) D.O letter dated 04.06.09 was issued. A perusal of monitoring report done in month of Nov., 2009 are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue letter seeking application for consent to operate.

Inform DPCC laboratory to monitor the quality of waste water discharged by the plant instead of analyzing the quality of drinking water.

Action Taken Report
· As decided in CMC (MSW) a letter for submission of application for renewal of consent was issued on 11.02.2010. However unit has not submitted any application so far. 

· Further DPCC Laboratory has informed to monitor the quality of waste water discharged by the plant instead of analyzing the quality of drinking water.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:

Issue reminder seeking application for consent to operate.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Wazirabad Water Treatment Plant

Consent status:

· Consent to Establish issued on 08.02.10 valid upto 07.02.2011.
· Not applied for consent to operate.

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 : 

D.O. Letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies. 

Action Taken Report

As decided in CMC (MSWM) D.O letter dated 04.06.09 was issued. A perusal of monitoring report done in month of Nov., 2009 are meeting the prescribed standards.   

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue consent to establish and ask the unit to apply for consent to operate.

 Inform DPCC laboratory to monitor the quality of waste water discharged by the plant instead of analyzing the quality of drinking water.

Action Taken Report
· As decided in CMC (MSW) consent to establish and a letter for submission of application for consent to operate were issued on 08.02.2010 & 11.02.2010 respectively.  

· Further DPCC Laboratory has informed to monitor the quality of waste water discharged by the plant instead of analyzing the quality of drinking water.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:

Issue reminder seeking application for consent to operate.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

  DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Chandrawal  Water Treatment Plant-I

(35 MGD)

Consent status:

· Consent to Establish issued on 08.02.10 valid upto 07.02.2011.
· Not applied for consent to operate.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue consent to establish and ask the unit to apply for consent to operate.

 Inform DPCC laboratory to monitor the quality of waste water discharged by the plant instead of analyzing the quality of drinking water.

Action Taken Report
· As decided in CMC (MSW) consent to establish and a letter for submission of application for consent to operate were issued on 08.02.2010 & 11.02.2010 respectively.  

· Further DPCC Laboratory has informed to monitor the quality of waste water discharged by the plant instead of analyzing the quality of drinking water.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:

Issue reminder seeking application for consent to operate.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Chandrawal  Water Treatment Plant-II

(55 MGD)
Consent status:

· Consent to Establish issued on 08.02.10 valid upto 07.02.2011.
· Not applied for consent to operate.

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 : 

D.O. Letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies. 
Action Taken Report

As decided in CMC (MSWM) D.O letter dated 04.06.09 was issued. A perusal of monitoring report done in month of Nov., 2009 are meeting the prescribed standards.  
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue consent to establish and ask the unit to apply for consent to operate.

 Inform DPCC laboratory to monitor the quality of waste water discharged by the plant instead of analyzing the quality of drinking water.

Action Taken Report
· As decided in CMC (MSW) consent to establish and a letter for submission of application for consent to operate were issued on 08.02.2010 & 11.02.2010 respectively.  

· Further DPCC Laboratory has informed to monitor the quality of waste water discharged by the plant instead of analyzing the quality of drinking water.

Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:

Issue reminder seeking application for consent to operate.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Bhagirathi Water Treatment Plant

Consent status:

· Consent to Establish issued  on 08.02.10 valid upto 07.02.2011.
· Not applied for consent to operate.

Decision of Consen Management Committee (MSW) in its meeting dated 12.05.2009 : 

D.O. Letter from Chairman, DPCC to CEO, DJB for not meeting the norms & other deficiencies. 
Action Taken Report

As decided in CMC (MSWM) D.O letter dated 04.06.09 was issued. A perusal of monitoring report done in month of Nov., 2009 are meeting the prescribed standards.   
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Issue consent to establish and ask the unit to apply for consent to operate.

 Inform DPCC laboratory to monitor the quality of waste water discharged by the plant instead of analyzing the quality of drinking water.

Action Taken Report
· As decided in CMC (MSW) consent to establish and a letter for submission of application for consent to operate were issued on 08.02.2010 & 11.02.2010 respectively.  

· Further DPCC Laboratory has informed to monitor the quality of waste water discharged by the plant instead of analyzing the quality of drinking water.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:

Issue reminder seeking application for consent to operate.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)
Sonia Vihar Water Treatment Plant
Consent status:

· Consent to operate granted on 13.03.2007 valid upto 08.12.2009.
· Not applied for CTO(R) . 

Decision of Consent Management Committee (MSW) in its meeting dated 12.05.2009 : 

No action.

Action Taken Report

A perusal of monitoring report done in month of Nov., 2009 are meeting the prescribed standards.   
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 19.01.2010:

Ask the unit to apply for renewal of consent.

 Inform DPCC laboratory to monitor the quality of waste water discharged by the plant instead of analyzing the quality of drinking water.

Action Taken Report
· As decided in CMC (MSW) a letter for submission of application for renewal of consent was issued on 11.02.2010. However unit has not submitted any application so far. 

· Further DPCC Laboratory has informed to monitor the quality of waste water discharged by the plant instead of analyzing the quality of drinking water.
Decision of Consent Management Committee (Orange) wrt cases of MSW Cell dated 20.04.2010:

Issue reminder seeking application for consent to operate.

 Chairman
   M. S.         Member        Member
 SEE
   EE
  AEE 

   DPCC        DPCC        Env. Deptt.    Acd. Inst          (MSWM Cell)

	S. No.
	Decision taken in CMC (MSW) meeting held on 28.02.08
	Decision taken in CMC(MSW) meeting held on 23.01.2009
	Decision taken in CMC(MSW) meeting held on 12.05.2009
	Decision taken in CMC(MSW) meeting held on 19.01.2010
	Decision taken in CMC(MSW) meeting held on 20.04.2010

	A
	Installation of CETP at Patparganj Indl Area:

As reported by DSIDC officials, untreated effluent of Patparganj Industrial Area is being treated by PWD. An inspection is to be done of Patparganj Industrial Area to check whether PWD is treating domestic waste, by SEE (MSWM). A letter may be sent to PWD in this regard, and inspection report submitted in file in 15 days.
Action by: MSWM Cell

Action Taken Report:
Letter has been issued to SE (PWD) on 25.03.05 (C/174).

The area has been inspected by SEE (MSW) along with officials from DSIIDC and Industry Department on 11.04.08. The inspection report has been forwarded and Chairman, DPCC desired that this may be discussed in CMC (MSW). A list of Industries who has applied for the consent under orange category in DPCC from Patparganj Indl. Area (PIA) was also sent to DSIIDC on 10.04.08. Sewerage plan of Patparganj Industrial Area has been received from PWD. Officials from concerned departments have been called in the meeting.

	Representative of DSIIDC informed that they have received report from IIT. DSIIDC will take further action for taking approval from Chief Secretary, Delhi w.r.t. installation of CETP in Patparganj Indl. Area on the basis of report of IIT, Delhi.

Action Taken Report:  

Letter issued on 23.02.09 & its reminders on 08.04.09. DSIIDC requested to take up the matter at appropriate level in Delhi Govt. for construction of CETP at PIE vide letter dated 09.04.09. Subsequently, a letter was issued on 06.05.09 to Commissioner of Industries with copy to EPCA & CS.  Reply is still awaited.     
	MS to talk to commissioner of Industries and expedite the installation of CETP at Patparganj.
Action Taken Report:

Letter has been issued on 16.06.09 to the Commissioner of Industries, Govt. of NCT of Delhi.
No reply is received from industry deptt.
	Issue D.O. letter to COI from Chairman, DPCC  seeking clarification regarding installation of CETP at Patparganj. 

ATR:
D.O. letter to COI from Chairman, DPCC, issued on 10.03.2010. Reply awaited.
	Issue reminder D.O. letter from MS, DPCC to COI, seeking clarification regarding installation of CETP at Patparganj.

	S N
	Decision taken in CMC (MSW) meeting held on 28.02.08
	Decision taken in CMC(MSW) meeting held on 23.01.2009
	Decision taken in CMC(MSW) meeting held on 12.05.2009
	Decision taken in CMC(MSW) meeting held on 19.01.2010
	Decision taken in CMC(MSW) meeting held on 20.04.2010

	B (1)
	Removal of encroachments on the roads of WIA:

A letter will be sent to Sh. Naresh Kumar, Additional Commissioner, MCD, regarding removal of Encroachment on the roads of DSIDC sheds, so that work of conveyance system may be completed by DJB within two months. The copy of this letter will be sent to Managing Director, DSIDC by MS, immediately.

Action Taken Report:

Letter has been issued to Sh. Naresh Kumar, Additional Commissioner, MCD on 25.03.08 with a copy to MD, DSIIDC (C/177). Reply is awaited. Representative from MCD & DSIIDC called for the meeting.


	Put up in next CMC (MSW) meeting.

Action Taken Report:  

Reminder letters were issued on 08.04.09.  Reply is still awaited.  
	Sh. B. Kumar, SEE to visit the area and assess the time of encroachment with photographs and submit a report to chairman for D.O. letter to Commissioner, MCD.

Action Taken Report:
SEE (MSW & Planning) visited the area and photographs of the encroachments in the lanes of the DSIIDC sheds were taken. 
	Issue reminder D.O letter from Chairman, DPCC to Commissioner, MCD with a copy to Pr. Secretary (UD) enclosing copies of previous letters.

ATR:
D.O. letter from Chairman, DPCC to Commissioner, MCD with a copy to Pr. Secretary (UD), issued on 23.03.2010. Reply awaited.
	Issue reminder D.O. letter from MS, DPCC to Commissioner, MCD with a copy to Pr. Secretary (UD) enclosing copies of previous letters.

	S N
	Decision taken in CMC (MSW) meeting held on 28.02.08
	Decision taken in CMC(MSW) meeting held on 23.01.2009
	Decision taken in CMC(MSW) meeting held on 12.05.2009
	Decision taken in CMC(MSW) meeting held on 19.01.2010
	Decision taken in CMC(MSW) meeting held on 20.04.2010

	C
	Removal of encroachment by DDA in WIA:
A letter will be issued to the new Vice Chairman, DDA by Chairman, DPCC, enclosing a copy of the previous letter. File to be submitted immediately. 

Action by: MSWM Cell

Action Taken Report:

Letter has been issued to VC, DDA on 21.04.08 (C/217). Reply is awaited. Representative from DDA called for the meeting.

	Put up in next CMC (MSW) meeting.

Action Taken Report:  

Letter dated 04.03.09 received from Dy. Director, LM(NZ),  DDA, Addressed to Dy. Director (Indl.), DDA mentioning that being a land owning agency, necessary approval for removal of existing encroachments, may please be accorded from Competent Authority and intimate to his office for removal of the same. 
	Send copies of all previous letters to Pr. Secretary, UD for taking necessary action. Copy also be sent to Pr. Secretary to LG.

Action Taken Report:
A letter was issued on 12.06.09. However, Action Taken Report is not received till date.
	Issue D.O. letter to VC, DDA from Chairman, DPCC with copy to Secretary to LG, GNCTD and CS, GNCTD giving reference and enclosing copy of previous reference to take measures to prevent dumping of waste water and MSW. 

ATR:
D.O. letter to VC, DDA from Chairman, DPCC with copy to Secretary to LG, GNCTD and CS, GNCTD, issued on 23.03.2010. Reply awaited.
	Issue reminder D.O. letter from MS, DPCC to VC, DDA with copy to Secretary to LG, GNCTD and CS, GNCTD giving reference and enclosing copy of previous reference to take measures to prevent dumping of waste water and MSW. 

	S N
	Decision taken in CMC (MSW) meeting held on 28.02.08
	Decision taken in CMC(MSW) meeting held on 23.01.2009
	Decision taken in CMC(MSW) meeting held on 12.05.2009
	Decision taken in CMC(MSW) meeting held on 19.01.2010
	Decision taken in CMC(MSW) meeting held on 20.04.2010

	D
	Construction of roads in WIA:

MCD informed that all the work w.r.t. main circular roads & A Block in Wazirpur Industrial Area, will be completed within the scheduled time of 6 months i.e. May, 2008. SEE may submit a monthly progress report on this in each CMC (MSW).

Action by: MSWM Cell

Action Taken Report:

Letter has been issued to DC (Rohini Zone), MCD on 25.03.08 (C/175). Reply is awaited. Representative from MCD called for the meeting.


	Status report in next CMC (MSW) meeting.

Action Taken Report:  

Letters were issued on 23.02.09 and 30.03.09.  Action Taken Report received vide letter dated 15.04.09.  Accordingly, MCD has constructed 4.37 Km, 4.04 Km & 3.16 Km roads of 30′, 45’ & 60’ wide roads respectively.   The work of 2.56 km road of 45’ is under progress and after necessary approval construction up to 60’ wide roads will be completed by September, 2010.  After necessary approval of 80’ road, work will be taken up in hand.     
	Put up a D.O. letter from Chairman, DPCC to Commissioner, MCD indicating their previous deadline and now revised deadline. 
Action Taken Report:  

A D.O. letter to Commissioner, MCD was issued on 21.07.09. No reply is received till date.
	Inspection be carried out to know the present status.

 Issue D.O. letter from Chairman, DPCC to Commissioner, MCD.

ATR:
D.O. letter from Chairman, DPCC to Commissioner, MCD issued on 10.03.2010. Reply awaited.
Unit was inspected.
	Issue a letter to Commissioner, MCD for completion of roads in WIA.

	S N
	Decision taken in CMC (MSW) meeting held on 28.02.08
	Decision taken in CMC(MSW) meeting held on 23.01.2009
	Decision taken in CMC(MSW) meeting held on 12.05.2009
	Decision taken in CMC(MSW) meeting held on 19.01.2010
	Decision taken in CMC(MSW) meeting held on 20.04.2010

	E
	Matter regarding illegal hazardous waste dumping sites: 

Reminder letters will be sent to the concerned officials.

Action by: MSWM Cell

Action Taken Report:

Reminder letter have been sent on 25.03.08. No reply received so far. Officials of the concerned departments have been called for the meeting.

	Reminder to be issued to DDA for getting action taken report on 5 remaining sites. Letters also be issued to land owning agencies of 10 sites from which waste has not been removed as per the inspection report.

Action Taken Report:  

ATR have been received in respect of 18 sites out of 23 sites. However, inspections of these 18 sites reveals that waste was still exist at 10 sites. Reminder letters has been issued to all land owning agencies for ATR on 17.03.09 & 06.05.09.  ATR is still awaited.   
	Letters from Chairman, DPCC to the concerned HODs of Industries, DSIIDC, DDA and Northern Railway.
Action Taken Report:  

As per recent office order dated 12.08.09, file transferred to concerned CMC for further necessary action.

CMC informed that some of the areas have been inspected by SCMC alongwith the officials of CPCB and DPCC and the report in this regard is awaited.
	Put up the file administratively to apprise CS, GNCTD. Issue D.O letter to land owning agencies. 

ATR:

ATR regarding above said matter is not received from CMC so far. 
Since the matter pertains to CMC, Therefore it may be transferred to CMC.
	Ask CMC to take necessary action o the matter and shift the matter to them if entire action is to be taken by them.

	S N
	Decision taken in CMC (MSW) meeting held on 28.02.08
	Decision taken in CMC(MSW) meeting held on 23.01.2009
	Decision taken in CMC(MSW) meeting held on 12.05.2009
	Decision taken in CMC(MSW) meeting held on 19.01.2010
	Decision taken in CMC(MSW) meeting held on 20.04.2010

	F
	Matter regarding TSDF site, at Gumenhera:

1. Deputy Commissioner (South West) will hold a meeting on 03-03-2008 regarding TSDF site at Ghumanhera.

2. Shifting of Hazardous waste stored in Delhi to Kanpur or Udaipur has to be explored by MS continuously and reported to Chairman.

3. Draft Expression of Interest (EOI) for Hazardous Waste Site is to be prepared and put upon file.                                                                                             
Action by: MS / CMC-III

Action Taken Report:

As informed EE, CMC-III, there is no progress in the matter.

	Status report in next CMC (MSW) meeting.

Action Taken Report:  

A letter was also issued to Dy. Secretary, Deptt of Env., GNCTD on 13.02.09 for taking action regarding acquiring land for TSDF site.  
	Put up in next meeting.

ATR/REMARKS:

Matter is being dealt by CMC.
CMC informed that the process of acquiring land for the site is underway by the Department of Environment, GNCTD.
	Director, Dept of Environment informed that 50 acres of land was given by DSIIDC.

Inform the progress made on the issue in the next meeting.

ATR:

ATR regarding above said matter is not received from CMC so far. 
Since the matter pertains to CMC, Therefore it may be transferred to CMC.
	No Action.

	S N
	Decision taken in CMC (MSW) meeting held on 28.02.08
	Decision taken in CMC(MSW) meeting held on 23.01.2009
	Decision taken in CMC(MSW) meeting held on 12.05.2009
	Decision taken in CMC(MSW) meeting held on 19.01.2010
	Decision taken in CMC(MSW) meeting held on 20.04.2010

	G
	Matter regarding gas supplies to WIA:

Matter to be followed up with reminders to the gas supplying company by MS.

Action by: MS / CMC-II

Action Taken Report:

A letter dated 19.04.08 received from IGL, wherein they requested for the list of industrial buyers in WIA for requirement of natural gas.

	Follow up with IIT, Delhi.

Action Taken Report:  

Reminders were issued to IIT, Delhi on 23.02.09 and 30.03.09.  Response from IIT, Delhi is still awaited.  SEE (MSW) has contacted with Prof. Anil Saroha of IIT, Delhi to expedite the proposal.  
	Follow up with Prof. Anil Saroha of IIT, Delhi.
ATR:
SEE spoke to Prof. Anil Saroha of IIT, Delhi.
	MS, DPCC to take a meeting with Prof. Anil Saroha to expedite the matter.

ATR:

MS, DPCC had taken a meeting with Prof. Anil Saroha on 5th March, 2010 at 03:00 PM to expedite the matter. 

During the meeting EEs of CMC had appraised that DPCC Board in its meeting held on 09.12.2009, took a decision that all the units using coal fired boilers to convert into oil fired immediately. Necessary papers have been retained from the main file, which is being dealt by CMC. Then that main file related to action taken by CMC was sent to concerned CMC for required action at their end. ATR regarding above said matter is not received from CMC so far.
	Transfer this case to CMC.

	S N
	Decision taken in CMC (MSW) meeting held on 28.02.08
	Decision taken in CMC(MSW) meeting held on 23.01.2009
	Decision taken in CMC(MSW) meeting held on 12.05.2009
	Decision taken in CMC(MSW) meeting held on 19.01.2010
	Decision taken in CMC(MSW) meeting held on 20.04.2010

	H
	Matter regarding electronic waste:

Sh. A.N. Singh, Scientist, Department of Environment along with the DPCC officials will prepare Expression of Interest (EOI) for electronic waste for five processes i.e. Collection & transportation, dismantling, extracting the valuable metal, recycling the valuable metal and disposal of the non recyclable metal and submit the file within 30 days.

Action by: Plg. Cell

Action Taken Report:

File of e-waste is under submission. Sh. A.N. Singh, Scientist, Department of Environment is preparing EOI with the help of consultant.

One EOI for study already prepared by Planning Cell & A.N. Singh, Scientist jointly.
	Put up in next CMC (MSW) meeting.

Action Taken Report:  

As informed by the Plg. Cell, status remains same.
	Take the status from Sh. A.N. Singh (Scientist Env. Deptt.). 
ATR: Sh. A. N. Singh, Scientist informed that MCD and NDMC were requested to install E-waste collection bins and which shall be disposed off through NCR based E-waste recyclers authorized by CPCB/MoEF. 
	Progress be informed to the Committee in next meeting.

ATR:

The matter regarding e waste is being dealt by BMW Cell as per office order dated 12.08.2009 and the said matter/ issues involved were taken by the BMW Committee No. 1 in its meeting held on 24.02.2010 and 02.03.2010 and as decided a public notice regarding disposal of e-waste through registered recyclers has already been issued on 11.03.2010 and rest of the issues/ matter is being dealt in the concerned file. Regarding 41 EOIs received for Collection & transportation, dismantling, extracting the valuable metal, recycling the valuable metal and disposal of the non recyclable metal, the concerned file is with Department of Environment which has to decide further action in the matter. Since the matter pertains to CMC, Therefore it may be transferred to CMC.
	Transfer this case to BMWM Cell.


