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	DELHI POLLUTION CONTROL COMMITTEE

4TH FLOOR, ISBT BUILDING, KASHMERE GATE, DELHI-6

visit us at : http://dpcc.delhigovt.nic.in





F.No.DPCC/MSWM/2008/ 3190-3196  


      Dated: 17-02-2009
Subject:- Minutes of the 13th meeting of the Committee Constituted for deciding the Consent under the Air and Water Acts, for MSWM Cell held on 23rd January, 2009. 

Please find enclosed herewith the Minutes of the 13th meeting of the Committee Constituted for deciding the Consent under the Air and Water Acts, for LAEC matters, MSW Projects & Power Plants, CETPs, STPs, and WTPs cases held on 23rd January, 2009. 
(B Kumar)

Sr. Env. Engineer

MSWM Cell
1. PS to Chairman, DPCC- for kind information of Chairman please.
2. Member Secretary, DPCC. 
3. Prof. S.K.Gupta Head Chemical  Engineering  Deptt. ,IIT Delhi
4. Dr. Anil Kumar, SSO (Env. Deptt.)
5. EE, MSWM Cell, DPCC.
6. AEEs, MSWM Cell, DPCC.

Copy to:-

1. Incharge, Computer Cell, DPCC-soft copy of minutes is also enclosed for placing the aforementioned minutes of the committee on the Website of DPCC.
(B Kumar)

Sr. Env. Engineer

MSWM Cell
Decision taken in the 13th meeting of CMC (MSW) held on 23.01.09  in the conference room of Chairman, DPCC

Agenda 1.

Agenda No. 1- Action Taken Report with respect to follow up action on the pending issues of the Local Area Environment Committee.
	S N
	Decision taken in CMC (MSW) meeting held on 28.02.08
	Decision taken in CMC (MSW) meeting held on 12.05.08
	Decision taken in CMC (MSW) meeting held on 29.07.08
	Decision taken in CMC (MSW) meeting held on 10.10.08
	Decision taken in CMC(MSW) meeting held on 05.12.2008
	Decision taken in CMC(MSW) meeting held on 23.01.2009

	A
	As reported by DSIDC officials, untreated effluent of Patparganj Industrial Area is being treated by PWD. An inspection is to be done of Patparganj Industrial Area to check whether PWD is treating domestic waste, by SEE (MSWM). A letter may be sent to PWD in this regard, and inspection report submitted in file in 15 days.
Action by: MSWM Cell
Action Taken Report:
Letter has been issued to SE (PWD) on 25.03.05 (C/174).

The area has been inspected by SEE (MSW) along with officials from DSIIDC and Industry Department on 11.04.08. The inspection report has been forwarded and Chairman, DPCC desired that this may be discussed in CMC (MSW). A list of Industries who has applied for the consent under orange category in DPCC from Patparganj Indl. Area (PIA) was also sent to DSIIDC on 10.04.08. Sewerage plan of Patparganj Industrial Area has been received from PWD. Officials from concerned departments have been called in the meeting.

	DSIDC has confirmed that they will get the feasibility study done following due procedures and submit the report to CMC (MSW), DPCC within 03 months including the quantum of total water generated in PIA. The feasibility report shall also have the recommendation for transportation of waste water generated to Jhilmil CETP or construction of separate CETP at PIA. 
Action Taken Report:
A letter was issued to DSIIDC on 03.06.08 (C/421). DSIIDC has awarded the study to                   Dr. A.K. Nema Assistant Professor IIT vide letter dated 08.07.08. Representative from DSIIDC called for the meeting.
	Put up in next CMC (MSW) meeting.

Action Taken Report:
DSIIDC has replied on 03.010.08 that IIT has informed that he Techno Feasibility report for storage & Transporting the effluent from Patparganj Indl. Estate Area to CETP Jhilmil shall be submitted by them by end of October, 2008 as due to rainy season the effluent was diluted and the representative samples could not be collected in this period.

	To be taken up in CMC(MSW)  in November, 2008.
Action Taken Report:  

DSIIDC has informed on 25.11.08 that M/s I.I.T. has been requested to expedite the report and get it submitted by end of this month.

	Wait for the report. Letter from Ministry may be sent to DSIIDC and COI.
Action Taken Report:  

Letter issued on  

14.01.09. Reply is awaited.  

DSIIDC also informed that IIT Delhi has submitted its draft report, which has been processed for approval & IIT Delhi shall be submitted its final report after amendments as advised to them in the draft repot.       
	Representative of DSIIDC informed that they have received report from IIT. DSIIDC will take further action for taking approval from Chief Secretary, Delhi w.r.t. installation of CETP in Patparganj Indl. Area on the basis of report of IIT, Delhi.
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	B (1)


	DJB shall send the list of 30 units which have not paid the requisite fee for permission from DJB, for connection into conveyance system to DPCC with a copy to CETP Society, Wazirpur. In case industrial units do not pay the requisite fee, DPCC will pay the fee to DJB and recover from the units later as the urgency of connecting individual lines to the conveyance system is more important in pubic interest than the amount of Rs, 500/- charged to each unit by DJB. However, DJB will sanction the permission to industrial units immediately.

Action Taken Report:

Letter has been issued to DJB on 01.04.08 (C/181). Reply is awaited. Further as per approval notices u/s 33(A) of water Act have been issued to 30 units on 04.04.08 & the list of 30 units were received from DJB. The status of notice issued and their replies is enclosed. Accordingly, 17 units have connected their sewer line to conveyance system, 5 units have taken necessary approval from DJB, 4 unit did not submitted their reply and notices received back undelivered from 2 units. No proper reply from 1 unit.
	1. Out of 30 units which have not responded so far are given one month final times after which necessary penal action under the Water Act will be taken. 

Action Taken Report:

1. Notices u/s 33 (A) of Water Act were again issued to five units on 03.06.08 who have not responded earlier. Three units have submitted their reply that they have connected/obtained permission for the connection, whereas, two units not respond so far.  Status of the units is enclosed.  

	The two remaining units which are not connected with the conveyance system of WIA. Issue notice by CMC (Orange) for this purpose on the basis of name and address of the units. In the meantime, SIT may inspect both the units and report in CMC meeting held on 06.08.2008.

Action Taken Report:
The following information is furnished by EE (CMC –II ) : No reply is received to show cause notice u/s 33 A of Water Act issued to following two units (a) M/s Ramesh Brothers, A-109/1, Wazirpur Industrial Area (b) M/s Alta Motie Enterprises, C-54/1,  Wazirpur Industrial Area.

SIT has also inspected both the units.


	Final reminder for compliance within a month. To be taken up in November, 2008 CMC (MSW).

Action Taken Report:
CMC-II has issued reminder notice to both the units on 12.11.2008. M/s Ramesh Brothers has replied on 19.11.2008 that they have connected sewer line of their premises to the conveyance system & got the permission of DJB. No response is received from M/s Alta Motie Enterprises,                   C-54/1, Wazirpur Industrial Area.
	Notice for closure with proper speaking order be issued by concerned CMC.
Action Taken Report:
As informed by CMC-II, a reply received from the unit stating that they have obtained permission from DJB for connection of sewer line to conveyance system. Thus all the units to whom notices had been issued have connected their sewer line to conveyance system.
	No Action.
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	B (2)
	A letter will be sent to Sh. Naresh Kumar, Additional Commissioner, MCD, regarding removal of Encroachment on the roads of DSIDC sheds, so that work of conveyance system may be completed by DJB within two months. The copy of this letter will be sent to Managing Director, DSIDC by MS, immediately.

Action Taken Report:

Letter has been issued to Sh. Naresh Kumar, Additional Commissioner, MCD on 25.03.08 with a copy to MD, DSIIDC (C/177). Reply is awaited. Representative from MCD & DSIIDC called for the meeting.


	The concerned MCD officials Sh. Anil Mittal has confirmed that he will take a copy of the letter written to Addl. Commissioner, MCD and get the encroachment removed within 15 days.

Action Taken Report:

Letter has been issued to Sh. Naresh Kumar, Additional Commissioner, MCD on 03.06.08 with a copy to MD, DSIIDC (C/420). Reply is awaited. Representative from MCD & DSIIDC called for the meeting.
	Representative from MCD informed that the drive for removal of encroachment is proposed on 8th August, 2008. MCD will send ATR after removal of encroachments.

Action Taken Report:

Letter has been issued to Sh. Naresh Kumar, Additional Commissioner, MCD on 14.08.09 with a copy to MD, DSIIDC (C/420). As no reply is received despite various telephonic 

Reminder to                   

Sh. Anil Mittal, another reminder was issued on 08.10.08.


	Letter from chairman, DPCC to commissioner MCD quoting previous references.

Action Taken Report:
D.O. Letter issued on 21.11.2008. No reply is received till date.

	To be taken up in next CMC (MSW).

Action Taken Report:
Despite issuance of reminder letter and telephonic request to concerned officials in MCD, action taken report / reply from MCD is still awaited.  WIA was visited on 16.01.09 by EE, AEE & TE and it was observed that encroachment still exists in the DSIDC sheds. 
	Put up in next CMC (MSW) meeting.
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	C
	A letter will be issued to the new Vice Chairman, DDA by Chairman, DPCC, enclosing a copy of the previous letter. File to be submitted immediately. 

Action by: MSWM Cell
Action Taken Report:

Letter has been issued to VC, DDA on 21.04.08 (C/217). Reply is awaited. Representative from DDA called for the meeting.

	The DDA official present is shifting the responsibility to the Engineering Wing, DDA. He is directed to ensure reply within 01 week. 
Action Taken Report:

Letter was issued to VC, DDA on 13.06.08 (C/436). Reply is awaited.

	Follow up action.
Action Taken Report:

Another D.O. letter was issued to VC, DDA on 08.09.08. Reply dated 04.09.08 received from Deputy Director (Industrial), DDA.  Accordingly, an inspection of the area for removal of encroachment was proposed on 10.09.08.  This letter was received in MSWM Cell on 23.09.08.    

	Ask for compliance report from DDA.  

Action Taken Report:

D.O. Letter issued on 21.11.2008. A letter dated 18.11.08 is received from EE (DDA) address to                Dy. Director (Industrial), DDA with a request for removal of encroachment form the land owning agency, since he is the land owning agency of Wazirpur Industrial Area. 
	Status report in next CMC (MSW).
Action Taken Report:
Another letter issued on 15.01.09.  Reply is awaited.  
	Put up in next CMC (MSW) meeting.
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	D
	Construction of roads in WIA:

MCD informed that all the work w.r.t. main circular roads & A Block in Wazirpur Industrial Area, will be completed within the scheduled time of 6 months i.e. May, 2008. SEE may submit a monthly progress report on this in each CMC (MSW).

Action by: MSWM Cell
Action Taken Report:

Letter has been issued to DC (Rohini Zone), MCD on 25.03.08 (C/175). Reply is awaited. Representative from MCD called for the meeting.


	The MCD official present has confirmed that 3.5 Km road completed and remaining 6.5 Km will be completed by October, 2008.
Action Taken Report:

Letter was issued to DC (Rohini Zone), MCD on 03.06.08 (C/418). Reply is awaited. Representative from MCD called for the meeting.


	A letter may be written from Chairman, DPCC to the Commissioner, MCD to resolve the issue. MS to put up the draft before 06.08.2008.
Action Taken Report:

A letter was written on 08.08.08 from Chairman, DPCC to the Commissioner, MCD.  A detail by action taken report was received on 25.09.08 from MCD.  It was informed that in category 30’-00” ROW & Below,  4.19 km length of Road is being constructed out of 10.76 km of total length and 2.57 km length of road has completed and rest of 1.62 km is in progress and will be completed  within next month. For balance 6.57 km  the scheme of Phase-II has been prepared and send to Delhi Govt. for approval.

In category 45’-00” ROW,  6.6 km length of road out of 21.9 km is being constructed out of which 2.82 km of road has completed and the rest 3.78 km will be completed within next six months. For balance 15.35 km  the scheme of Phase-II has been prepared and send to Delhi Govt. for approval.

In category 60’-00” ROW, 3.16 km out of 7.29 km of total length is being constructed for balance 4.13 km the scheme of Phase –II has been prepared send to Delhi Govt. for approval.   
	Ask the compliance report within a month. To be taken up in Nov. 2008 CMC (MSW). 
Action Taken Report:

Letter issued on 03.11.2008. Ex. Enginner (Pr.), MCD has submitted present progress status on 21.11.2008 vide which they have informed that administrative approval of various amounts for phase-II under Central Road Fund has been accorded for expenditure sanction.
	Ask MCD to give the full details with chart of road completion. Physical verification report in next CMC (MSW).
Action Taken Report:
A letter issued on 02.01.09.  A reply dated 13.01.09 was received from MCD alongwith map and informing that they have constructed 7.41 km of Road equivalent of 12 feet and 3.3 km of Road is under construction.  WIA was visited by EE, AEE & TE on 16.01.09 to verify the facts.  MCD has constructed most of the road Group –A of WIA. 490m (60’) of road in Block-A and 120 m (45’) in block-B of WIA is completed. In Group-A & Block-A work is still in progress.     
	Status report in next CMC (MSW) meeting.
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	E
	Matter regarding illegal hazardous waste dumping sites: 

Reminder letters will be sent to the concerned officials.

Action by: MSWM Cell
Action Taken Report:

Reminder letter have been sent on 25.03.08. No reply received so far. Officials of the concerned departments have been called for the meeting.

	EE (MSWM) will visit all the 23 dump sites identified by M/s Ramky consultant and submit the factual report by next month for appropriate action under the HWM Rules. 
Action Taken Report:

All the 23 sites were inspected. Following are the observations regarding status of the sites in comparison of previous inspection:- 

· At 17 sites remain same. 

· At 3 sites quantity of HW decreased.

· At 1 site quantity of HW increased.

· At 2 sites no HW observed.  

A letter was sent to WBSPCB for obtaining measures taken for re-habitation of such site in West Bengal on 01.07.08.  Reply is awaited.  

With regard to letters issued to land owning agencies of the sites i.e. DDA, DSIIDC, Industry Department and Northern Railway, replies as received from DSIIDC and Copies of two letters issued by Director (Environment), DDA to CE (NZ) and CE (WZ) of DDA for taking measures for stoppage of further dumping of HW at the sites were received. However, no reply received from   Industry Department and Northern Railway.
	MS to issue a reminder to land owning agencies for the removal of illegal dumping sites Case is coming up in Hon’ble Supreme Court in next week. 
Action Taken Report:

Reminder letters issued to DSIIDC, DDA, Northern Railway, Department of Industries and MCD on 18.08.08. Replies were received from Northern Railway, Industry Department, DSIIDC & DDA that necessary action for removal of illegal dumping site is being taken DSIIDC has informed that the Waste   from the Plot No. G-1032 DSIIDC Narela  has been removed. Industry Department and DSIIDC have issued notices to the occupier of hazardous waste sites.  DDA has informed that they have forwarded the letters to concern Eng. to send the compliance report immediately.  MCD has informed that there is no malba lying in the said road/ lanes of G-1 Udyog Nagar.   
	Ask the compliance report from DDA within a month. Work done so far to be intimated to SCMC. To be taken up in November, 2008 CMC (MSW).
Action Taken Report:

Action taken report intimated to SCMC on 17.11.2008. 

Compliance report wrt 2 sites out of 15 sited received from DDA. Reminder letter for seeking compliance of remaining sites was issued on 17.11.2008.

	AEE & EE along with trainee (MSW) to inspect to check whether the statement is true. The directions given by CPCB will also be considered by inspecting team and give report by 19.01.2009. Issue reminder to VC, DDA for giving factual information about 11 sites out of 15.
Action Taken Report:
ATR in respect of 5 units is still awaited. Rest of the 18 sites was inspected by EE, AEE & TE.  Status of these sites is enclosed. It was observed that out of 18 sites, waste has been removed from 8 sites. Waste at remaining 10 sites still exists. 
	Reminder to be issued to DDA for getting action taken report on 5 remaining sites. Letters also be issued to land owning agencies of 10 sites from which waste has not been removed as per the inspection report.


.

Chairman

  M. S.
        

Member      


Prof. S.K Gupta


SEE


EE


AEE 

  
 DPCC
  

DPCC      

Env. Deptt.


Member (Acd. Inst)      

(MSW) 

MSWM Cell

MSWM Cell

Agenda No. 1- Action Taken Report with respect to follow up action on the pending issues of the Local Area Environment Committee

	S N
	Decision taken in CMC (MSW) meeting held on 28.02.08
	Decision taken in CMC (MSW) meeting held on 12.05.08
	Decision taken in CMC (MSW) meeting held on 29.07.08
	Decision taken in CMC (MSW) meeting held on 10.10.08
	Decision taken in CMC (MSW) meeting held on 05.12.2008
	Decision taken in CMC (MSW) meeting held on 23.01.09

	F
	Matter regarding TSDF site, at Gumenhera:

1. Deputy Commissioner (South West) will hold a meeting on 03-03-2008 regarding TSDF site at Ghumanhera.

2. Shifting of Hazardous waste stored in Delhi to Kanpur or Udaipur has to be explored by MS continuously and reported to Chairman.

3. Draft Expression of Interest (EOI) for Hazardous Waste Site is to be prepared and put upon file.                                                                                             
Action by: MS / CMC-III
Action Taken Report:

As informed EE, CMC-III, there is no progress in the matter.

	MS to pursue with DSIIDC for Kanjawala land being acquired by DSIIDC for which Chief Secretary already given order in writing. 
Action Taken Report:

A presentation was made before Chief Secretary of Delhi Govt. on 11.01.08 regarding TSDF at Ghumanhera village of Delhi. Communication in this regard is awaited.  

Regarding TSDF site at Kanjawala, M.S. has discuss the matter with MD, DSIIDC, he clarified that he has not got possession of the land for which the DSIDC had paid money.  Hence, no land can be given to Department of Environment in view of the aforesaid fact.
	MS to pursue the matter.
Action Taken Report:

As informed by CMC-III, a reminder letter issued on 10.10.2008 to DSIIDC regarding allotment of land for TSDF site.  
	Follow up with secretary (Revenue). To be put up in November, 2008 CMC (MSW).
Action Taken Report:

As informed by CMC-III, no response is received from DSIIDC & Secretary (Revenue). 

	Follow up action by concerned CMC.
Action Taken Report: Env. Department informed to SCMC on 21.11.08 that the land for TSDF at Ghumanhera could not be taken for development because it is designated as Green belt in MPD-2021. Further, Govt. is in process of acquiring land for Industrial development at Khanjawala wherein it has been requested to allot 50 acres of land. File sent to govt. for the approval.

	Status report in next CMC (MSW) meeting.
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	G
	Matter regarding gas supplies to WIA:

Matter to be followed up with reminders to the gas supplying company by MS.

Action by: MS / CMC-II
Action Taken Report:

A letter dated 19.04.08 received from IGL, wherein they requested for the list of industrial buyers in WIA for requirement of natural gas.
	The CETP Society confirmed that within 01 month that they will provide the list required by IGL for industrial buyers of natural gas. 
Action Taken Report:

No list of industries has been supplied by the CETP Society.
	The required details of price, delivery of gas etc. may be ascertained from IGL and submitted to association of WIA so that the list can be provided to IGL as required by them. 
Action Taken Report:

As informed by CMC-II, a public notice has been proposed regarding phasing out coal as fuel and shift to other cleaner fuels preferably CNC/PNG in their processes. Draft copy enclosed.

	Advertisement be released in this week (Sunday).
Action Taken Report:

As informed by CMC-III, a public advertisement was released on 05.10.08 in times of India & Punjab Kesari  asking the units / associations to furnish to DPCC for phasing out coal as fuel and shift to other cleaner fuels preferably CNG/PNG in their processes.    No response is received from any unit/ associations.  
	SEE to coordinate the Committee with IIT experts to assen the total amount of gas required for all industrial units in WIA. This report will be submitted before 19.01.2009.
Action Taken Report:
A letter was issued to IIT, Delhi on 02.01.09 and concern was contacted in IIT and they informed that a proposal in this regard is being prepared for submission to DPCC.  
	Follow up with IIT, Delhi.
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	H
	Matter regarding electronic waste:

Sh. A.N. Singh, Scientist, Department of Environment along with the DPCC officials will prepare Expression of Interest (EOI) for electronic waste for five processes i.e. Collection & transportation, dismantling, extracting the valuable metal, recycling the valuable metal and disposal of the non recyclable metal and submit the file within 30 days.

Action by: Plg. Cell
Action Taken Report:

File of e-waste is under submission. Sh. A.N. Singh, Scientist, Department of Environment is preparing EOI with the help of consultant.

One EOI for study already prepared by Planning Cell & A.N. Singh, Scientist jointly 

	Transaction Adviser to finalized EOI. MS to pursue.
Action Taken Report:

 EOIs have been invited through public notice issued in various newspapers. Last date of submission of the EOIs was 30.06.08.

41 numbers of EOIs were received and the same have been submitted on file for sending to Transaction Adviser / Consultant of Delhi Govt. Sh Pradeep Panwar.
	M.S to speak to the Transaction Advisor.
Action Taken Report:

41 EOIs have been examined and the request for proposal (RFP) is under preparation by the consultants.   
	To be discussed in Chief Secretary’s meeting on 17.10.2008.
Action Taken Report:

As informed by Plg. Section, that the 41 EOIs are under submission to the transaction adviser, Govt. of NCT of Delhi to identify the suitable agencies for the E-waste. However, no information about further progress, has been received from the transaction adviser.    

	Call on 19.01.2009 in next CMC (MSW) meeting.

Action Taken Report:

 As informed by the Plg. Cell.  The 41 EOIs were received and the same are sent to the consultant, GNCTD, to identify suitable agencies for the development of e-waste disposal and management facility.  The matte is now being looked after by Sh. A.N. Singh (Scientist, Env. Deptt.). Sh. A.N. Singh (Scientist, Env. Deptt.) informed that Request for Proposal (RFP) document under preparation.
	Put up in next CMC (MSW) meeting.
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Badarpur Thermal Power Station
Status of Consent: Consent issued on 27.07.2007 and valid up to 21.03.2010.

Action Taken:

This power station was also inspected by Zonal office Lucknow of CPCB on 23.08.07 & observed that particulate matter emission from unit II & V was within the limit. They recommended:

· BTPS should install ash pond effluent recirculation system.

· BTPS should install dedicated fly ash collection system.

· Ash dyke should be designed to withstand the hydraulic load of ash while raising its height, since area downstream of ash pond is densely populated.

- CPCB has desired that BTPS takes majors to implement the above recommendations within a time frame agreed mutually and asked to submit time targeted Action Plan & ATR.
Decision taken in meeting held on 19.10.07:

A letter may be issued to General Manager to comply with CPCB directions given during inspection by CPCB on 23.8.07. This compliance must be done by 31.12.07. 

Action taken/ Status w.r.t. the meeting held on 19.10.07:

· Letter issued on 5.11.07 communicating above decision. 

· No reply received so far.

Decision taken in meeting held on 09.01.08:

MS to speak to the concerned General Manager. The deficiencies noted by the inspection team of CPCB have not been corrected and not replied to. Letter be issued with the last opportunity giving to the unit to comply with the CPCB directions during inspection and complied with it fully.

Action taken/ Status w.r.t. the meeting held on 09.01.08:

A last opportunity letter issued on 31.01.08. A reply dated 28.01.08 was received from the power plant (C/327-328 of the file). Power Plant submitted that:

1. Regarding ash pond overflow recycling:

Corporate Engg., NTPC has been conducted for exploring and conducting a techno-economic feasibility study regarding the installation of this system.

2. Installation of dry ash collection system at plant:
The Dry Ash Extraction and Transportation System (DAETS) for 2X 210 MW of BTPS has already been awarded and is in execution stage. For 3X 95 MW units also there is a proposal of DAETS and for that the talks are going on with NTPC Vidyut Vyapar Nigam (NVVN) Ltd.

3.  Regarding ash dyke design aspect to withstand the hydraulic load while raising its height:
All the necessary precautions have already been taken by Corporate Engg., NTPC in the design aspect of ash dyke raising.

The above said reply has been forwarded to CPCB vide letter dated 11.02.08 after necessary approval on file. 

Decision taken in meeting held on 28.02.2008:

Letter to be issued bearing the directions for meeting the standard of Particulate Matter of 50 mg/Nm3 along with the copy of the minutes wherein it was decided that the standard for Particulate Matter has been made stringent of 50 mg/Nm3. In case high emission is caused due to high ash content in coal, the ash content may be reduced in the fuel (coal).
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Action taken/ Status w.r.t. the meeting held on 28.02.2008:

· Letter issued to BTPS on 24.03.08 to meet the standard of 50 mg/Nm3 for Particulate Matter. 

· They informed that-  “Comprehensive renovation and modernization package specification for improvement in ESP efficiency to achieve emission <50 mg/Nm3 in 2X210 MW units has been finalized at an estimated cost of Rs 40 crores and expected date of NIT for this package is by the end of June, 2008. Further to meet the MOEF guidelines to use coal having ash less than 34% on annualized average basis, the following action have been taken:-

· Use of imported coal having very ash ~8% started at 

· Emission <50 mg/Nm3 in 3X95 MW units.

· BTPS has also not submitted any time bounded programme to achieve emission <50 mg/Nm3.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

In case of two units considered for upgradation, let them confirm the status in next CMC. As regard three remaining units, issue reminder for their response. 

Action taken/ Status after the meeting held on 12.05.08:

· Letter issued to BTPS on 29.05.08.  BTPS submitted their reply vide letter dated 18.06.08 stating that they are taking possible care to maintain ESP of units 3X95 MW to keep emission within norms from these units.  However, it is also a fact that running of 3X95 MW for long will not be possible and DTL and CERC have directed that only minimum expenditure should be incurred on these units to keep them running till Commonwealth Games are over (i.e. 2010-11), after which phase out may be planned. BTPS has also submitted schedule of 2X210 MWESP modifications.  

· DPCC Monitoring results for the months of May & June 2008 are as under and meeting the standards: 

	S.No.

 
	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	
	
	May,08
	June,08
	May ,08
	June ,08
	May ,08
	June,08

	1.
	Duct of unit no. 1A
	86
	53
	368
	360
	314
	345

	2.
	Duct of unit no. 1B
	56
	47
	340
	364
	314
	345

	3.
	Duct of unit no. 2A
	65
	46
	368
	356
	367
	323

	4.
	Duct of unit no. 2B
	63
	49
	380
	352
	367
	323

	5.
	Duct of unit no. 3A
	67
	58
	388
	340
	334
	375

	6.
	Duct of unit no. 3B
	66
	52
	400
	319
	334
	375

	7.
	Duct of unit no. 4A
	74
	67
	472
	420
	314
	346

	8.
	Duct of unit no. 4B
	80
	72
	480
	440
	314
	346

	9.
	Duct of unit no. 5A
	59
	66
	480
	440
	397
	304

	10.
	Duct of unit no. 5B
	63
	58
	484
	432
	397
	364
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Decision of Consent Management Committee in its meeting dated 29.07.2008:
No action.

Action taken/ Status after the meeting held on 29.07.08:

· A letter on advice of CPCB and recommendation of CMC (MSW) in its meeting held on 29.07.08 has been issued on 18.08.08 for adding one more consent condition for periodic monitoring and reporting of ash and sulphur content and use of beneficiated coal.  A reply dated 01.09.08 received with the monitoring reports of ash and sulphur content.

· DPCC Monitoring results for the months of July & August, 2008 are as under and meeting the standards: 

	S.No.

 
	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	
	
	July,08
	Aug,08
	July,08
	Aug,08
	July,08
	Aug,08

	1.
	Duct of unit no. 1A
	83
	56
	426
	440
	323
	296

	2.
	Duct of unit no. 1B
	66
	65
	453
	0480
	323
	296

	3.
	Duct of unit no. 2A
	85
	96
	469
	456
	304
	300

	4.
	Duct of unit no. 2B
	68
	110
	480
	480
	304
	300

	5.
	Duct of unit no. 3A
	52
	72
	490
	392
	342
	320

	6.
	Duct of unit no. 3B
	65
	68
	502
	352
	342
	320

	7.
	Duct of unit no. 4A
	102
	56
	543
	500
	342
	367

	8.
	Duct of unit no. 4B
	87
	59
	53
	512
	342
	367

	9.
	Duct of unit no. 5A
	92
	67
	538
	440
	388
	367

	10.
	Duct of unit no. 5B
	98
	59
	548
	486
	388
	367


Decision of CMC (MSW) in its meeting dated 10.10.2008:

No action.

Action taken/ Status after the meeting held on 10.10.08:

· DPCC Monitoring results for the months of Oct. & Nov., 2008 are as under:

	 S.No.

 
	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	
	
	Oct,08
	Nov,08
	Oct,08
	Nov,08
	Oct,08
	Nov,08

	1.
	Duct of unit no. 1A
	61
	77
	400
	416
	268
	321

	2.
	Duct of unit no. 1B
	65
	85
	416
	424
	268
	321

	3.
	Duct of unit no. 2A
	71
	86
	392
	392
	273
	316

	4.
	Duct of unit no. 2B
	70
	71
	400
	384
	273
	316

	5.
	Duct of unit no. 3A
	#
	83
	#
	440
	#
	299

	6.
	Duct of unit no. 3B
	#
	86
	#
	448
	#
	299

	7.
	Duct of unit no. 4A
	59
	70
	440
	500
	344
	390

	8.
	Duct of unit no. 4B
	53
	52
	456
	512
	344
	390

	9.
	Duct of unit no. 5A
	62
	#
	472
	#
	281
	#

	10.
	Duct of unit no. 5B
	64
	#
	480
	#
	281
	#


·  DPCC Monitoring reports for waste water from Ash Pond for the month of November, 2008.

	Name of the Plant 
	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	
	Remarks 

	
	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	STP/

ETP/

CMB
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	
	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature
	0.50
	
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	Badarpur Thermal Power Station 
	12.11.2008
	7.8
	22
	<1.0
	7.5
	9.0
	Nil 
	STP
	7.7
	20
	1.2
	18
	64
	--
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· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

No Action.

Action taken/ Status after the meeting held on 05.12.08:

· DPCC Monitoring results for the months of Dec, 2008 are as under:

	S.No.

 
	Sampling Location


	Concentration in mg/Nm3 during Dec, 2008

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	1.
	Duct of unit no. 1A
	81
	412
	268

	2.
	Duct of unit no. 1B
	72
	420
	268

	3.
	Duct of unit no. 2A
	69
	432
	312

	4.
	Duct of unit no. 2B
	92
	440
	312

	5.
	Duct of unit no. 3A
	63
	460
	331

	6.
	Duct of unit no. 3B
	86
	448
	331

	7.
	Duct of unit no. 4A
	85
	528
	304

	8.
	Duct of unit no. 4B
	74
	540
	304

	9.
	Duct of unit no. 5A
	63
	532
	304

	10.
	Duct of unit no. 5B
	57
	520
	304


·  DPCC Monitoring reports for waste water from Ash Pond for the month of Dec, 2008.

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	STP/

ETP/

CMB
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature 
	0.50
	
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	14.01.09
	7.2
	26
	<1.0
	7.3
	8.5
	Nil 
	STP
	7.2
	22
	1.6
	21
	140
	--


Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

No Action.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

I.P. Thermal Power Station

Status of Consent: 

· Consent issued on 19.03.07 and valid up to 27.04.08.

· Applied for Renewal of consent on 17.04.08
Action Taken:

This power station was also inspected by Zonal office Lucknow of CPCB on 20.08.07 & observed that particulate matter emission from unit 3 & 5 was exceeding the limit. They recommended:

· IPTPS should adopt better ESP maintenance practices and ash evacuation system for controlling the emission of particulate matter.

· IPTPS should also take necessary action for better ash pond management to maintain the concentration of suspended solids within the prescribed limit.

· IPTPS should improve over all housekeeping immediately.

· CPCB has desired that IPTPS takes majors to implement the above recommendations within a time frame agreed mutually and asked to submit time targeted Action Plan & ATR.

Decision taken in meeting held on 19.10.07:

A letter may be issued to General Manager to comply with CPCB directions given during inspection by CPCB on 20.8.07.This compliance must be done by 31.12.07. 

Action taken/ Status w.r.t. the meeting held on 19.10.07:

· Letter issued on 5.11.07 communicating above decision. 

· No reply received so far.

Decision taken in meeting held on 09.01.08:

MS to speak to the concerned General Manager. The deficiencies noted by the inspection team of CPCB have not been corrected and not replied to. Letter be issued with the last opportunity giving to the unit to comply with the CPCB directions during inspection and complied with it fully.
Action taken/ Status w.r.t. the meeting held on 09.01.08:

Replies dated 07.01.08 was received from the power plant (C/243-252 of the file). Power plant submitted that:

1. Thermal Power Station should adopt better ESP maintenance practices and Ash evacuation system for controlling the emission of particulate matter:-



DGM (Opr.) IPS stated that the test results of online monitoring/stack (ESP results) unit wise as furnished by Mgr (ESP) are well within the prescribed limit of 50 mg/Nm3. The test results unit-wise are attached as Annexure-I at C/247-249. On examination of these results the stack emission for unit no. 3 was not meeting the prescribed limit of 50 mg/Nm3. In the results sheet it is mentioned that only old ESP was an operation and new ESP installed accidentally failed down and under reconstruction yet. The methods/Practices adopted for ESP maintenance, submitted by the power plant may be seen at Annexure-II(C/246). He has also submitted that Segregating valves are installed on ESP Hoppers of Unit No. 5 and will be installed gradually on other units. MoU with Cement manufacturers were signed for dry ash collection directly from ESP Hoppers.

2. Thermal Power Station should also take necessary actions for better ash pond management to maintain the concentration of suspended solids within the prescribed limit:-


DGM (Opr.) IPS stated that the test results in respect of TSS of the effluent of Ash Pond as furnished by Mgr (Civil) are well with in the prescribed limits. The ATR enclosed as Annexure-III(C/245). He has also stated that in view of closing of I.P. Station by the year 2010, the action for zero discharge at Ash pond has been dropped being costly affair.

3. Thermal Power Station should improve overall housekeeping:-

The Power Plant submitted that:

a. The area wise house-keeping in respect of water channel/Drain cleaning of
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 B-Channel for maintaining proper flow of sludge / Ash slurry up to DW water tank, cooling water channel, coal mill channel, Ash slurry channel are being regularly maintained through Annual Maintenance Contract for reusing the decanted water for ash transportation.

b. The housekeeping for cleaning of operation floor area at ash pond, Boiler furnace bottom, coal mill reject is also being carried out through separate Annual maintenance contract for suppression of the fugitive dust.

c. Besides above, the activities for disposal of old scrap / waste material from the I.P. site are also being perused with D&R Department and the disposal of old/scrapped cooling towers Units No. 1 are already in hand to keep up the good housekeeping at the plant.
The above said reply has been forwarded to CPCB vide letter dated 11.02.08 after necessary approval on file.

Decision taken in meeting held on 28.02.2008:

Letter to be issued bearing the directions for meeting the standard of Particulate Matter of 50 mg/Nm3 along with the copy of the minutes wherein it was decided that the standard for Particulate Matter has been made stringent of 50 mg/Nm3. In case high emission is caused due to high ash content in coal, the ash content may be reduced in the fuel (coal).

Action taken/ Status w.r.t. the meeting held on 28.02.2008:

· Letter issued to IPTPS on 24.03.08 to meet the standard of 50 mg/Nm3 for Particulate Matter. 

· A reply dated 01.05.08 received from IPTPS along with data of online monitoring w.e.f. 15.02.08 to 16.03.08. This data is not for all the days between this period and meeting the prescribed limit of 50 mg/Nm3 except a result of unit for on 14.03.08, which is 57 mg/Nm3. The power plant also informed that “in case of new ESP of Unit# 3 which fell accidentally is still under re-erection, ash evacuation system of new ESPs are also under final commissioning stage to get  improved results, stack emission with 50 mg/Nm3 in all Units”. 

· Noise monitoring report for DG set is not meeting the prescribed standards.

· DPCC monitoring reports show that all the operational ducts of this power station are not meeting the standard of 50mg/Nm3 for particulate matter except in duct of unit no. IV on 12.12.07. The Particulate matter in the stacks as per last six DPCC monitoring report are as under:

	S. No.
	Date of monitoring
	Particulate matter in duct of (in mg/Nm3  )

	
	
	Unit No.- II
	Unit No.-III
	Unit No.-IV
	Unit No.-V

	1
	03.10.07
	#
	#
	86
	#

	2
	16.11.07
	96
	89
	51
	#

	3
	12.12.07
	82
	69
	45
	#

	4
	28.01.08
	#
	103
	78
	#

	5
	26.02.08
	80
	101
	124
	#

	6
	19.03.08
	142
	76
	82
	#


# Shut down/ under maintenance.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

Due to installation of new ESP with unit no. 3, after commissioning the result will improve for unit no. 3 only. There is no proposal to improve efficiencies of other three remaining units. Reminder should be issued. Noise monitoring of D.G. Set is also not meeting the prescribed limit. Therefore, they may be asked to take adequate measure to have noise emissions within the limit. 
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Action taken/ Status after the meeting held on 12.05.08:

I. Letter issued to IPTPS on 29.05.08. Reply is awaited. 

II. A complaint received from NCAER through CPCB against this plant regarding noise pollution due to emission of huge quantity of steam at short intervals, say monthly or twice in three months.  The complainant has replied vide letter dated 24.06.08 on the bases of telephonic discussion with officials of this plant and a letter also issued to IPTPS on 24.06.08 for their comments and action taken. 

III. PM level is exceeding the prescribe limit of 50 mg/Nm3 in all operating ducts in DPCC monitoring for the months of May & June, 2008. Results are as under:- 

	S.No.

 
	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	
	
	May,08
	June,08
	May ,08
	June ,08
	May ,08
	June,08

	1.
	Duct of unit no. II
	63
	84
	300
	340
	190
	286

	2.
	Duct of unit no. III
	76
	#
	312
	#
	234
	#

	3.
	Duct of unit no. IV
	85
	75
	312
	352
	254
	286

	4.
	Duct of unit no. V
	90
	#
	304
	#
	241
	#


 # Shutdown/Under Maintenance 

Decision of Consent Management Committee in its meeting dated 29.07.2008:
Issue reminder letter.

 Action taken/ Status after the meeting held on 29.07.08:

· Reminder issued on 14.08.08. The unit has furnished a reply on 07.10.08 it was informed that for meeting the insertion loss of 25 dBA  for 125 KVA DG Set at IP Station, the necessary arrangements has been made i.e. the rubber gasket provided at the panel doors, perforated wooden boards were provided on the open floor of the set etc.   The noise report  from DPCC approved Laboratory will be submitted soon.  With regard to SPM  levels,  the unit has submitted their on line monitoring reports for first and last week of June, 2008 which revels that SPM levels are less than                50 mg/NM3.   The unit informed that except for the mentioned time of days as measured by DPCC, the emission results found to be within the prescribed limits. 

· A letter dated 19.08.08 received from the unit with action taken to achieve concentration of particulate matter in stack within 50 mg/Nm3 with any to fields out of service at I.P. Station, IPGCL for unit # 2, 3, 4 & 5. 

· PM level is exceeding the prescribe limit of 50 mg/Nm3 in all operating ducts in DPCC monitoring for the months of July & August, 2008. Results are as under:- 

	S.No.

 
	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	
	
	July,08
	Aug,08
	July,08
	Aug,08
	July,08
	Aug,08

	1.
	Duct of unit no. II
	100
	#
	320
	#
	241
	#

	2.
	Duct of unit no. III
	108
	67
	340
	372
	260
	205

	3.
	Duct of unit no. IV
	95
	63
	360
	360
	283
	205

	4.
	Duct of unit no. V
	103
	106
	320
	392
	341
	254


 # Shutdown/Under Maintenance 

Decision of CMC (MSW) in its meeting dated 10.10.2008:

With compliance report to be taken up in November, 2008 CMC(MSW).
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Action taken/ Status after the meeting held on 10.10.08:

· Letter issued on 27.10.2008.  Reply received on 07.11.08  the unit has submitted following details:-

1. First unit is already decommissioned and sold.  Other four units are also going to be closed with the coming of new gas based power station of Delhi at Bawana by year 2009/2010/ before starting of Common Wealth Game 2010.

2. The renewal of Consent, hence will be required upto-2009-10.

(i)  
Latest on line stack monitoring reading (Through opacity meter and found to be within limit of 50mg./Nm3 exceeds 50mg./Nm3 only when unit goes on shut down & when synchronized, remain with the support furnace oil (LDO).

(ii)  
Third party (DPCC authorized) test analysis of effluent is attached which are O.K.

(iii) 
 Further this station took steps to lessen water consumption by starting lifting of fly ash from ESP hoppers.

(iv) The acoustic enclosure of DG Set 125KVA manufacture in year 1978 have been departmentally treated to achieve insertion loss to the maximum taking into view of incurring very needful and genuinely required expenditure for the balance life of the plant upto 2009-10.  Re-Test noise results of date 17.10.08 are enclosed for your kind consideration.

It is further to mention that this DG set run only for about 5 minutes or so in two shifts of a day for trial run.  No operator is exposed near by to this, machine being kept at isolated place.

This machine is taken in use only when total grid system collapse and this stage can exist hardly maximum 10 to 15 minutes in extreme cases for the power station after which normal supply is restored.  

· DPCC Monitoring results for the months of Oct. & Nov., 2008 are as under:

	S.No.

 
	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	
	
	Oct.08
	Nov.08
	Oct.08
	Nov.08
	Oct.08
	Nov.08

	1.
	Duct of unit no. II
	#
	#
	#
	#
	#
	#

	2.
	Duct of unit no. III
	#
	#
	#
	#
	#
	#

	3.
	Duct of unit no. IV
	64
	80
	366
	328
	228
	228

	4.
	Duct of unit no. V
	#
	110
	#
	320
	#
	246


 # Shutdown/Under Maintenance 
· DPCC Monitoring reports for waste water from Ash Pond for the month of November, 2008.

	Name of the Plant 
	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	
	Remarks 

	
	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	STP/

ETP/

CMB
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	
	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature
	0.50
	
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	I.P. Power Station 
	05.11.2008
	7.5
	24
	<1.0
	7.6
	9.0
	Nil
	--
	--
	--
	--
	--
	--
	--


· A letter dated 22.11.08 received from the unit alongwith ambient air quality monitoring, data for particulate matter from point source & statement of Initial lighting up of Boilers, Progress report of the work for “Design, manufacture, supply, delivery 
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 at site un-loading, handling, civil works, erection, commission, performance testing and handing over on “Turn-key basis” the ESP system to achieve concentration of particulate matter in stack within 50 mg/Nm3 with any two fields out of service for unit # 2, 3, 4 & 5 and reading of opacity monitor (online).

· The unit was inspected by SS (Air), DPCC on 27.11.08 to know the reason of black emission on instruction from Chairman Office.  The following are the observations:- 

1. Only Unit No. 4 found operational.

2. Unit No. 2 and Unit No. 5 is not operational due to maintenance.
3. Unit No. 3 was shut down at 16:48 hours after grinding ball failure.
4. Due to grinding ball failure in ¾ Coal mill, coarse coal was feeded into boiler which gave high unburnt coal emission as ESPs not designed for such loading so black smoke emitted.
5. On 27.11.08, you have light up unit 5 and synchronize.  
· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

Issue Show Cause Notice for closure u/s 31(A) of the Air Act, 1981.


Action taken/ Status after the meeting held on 05.12.08:

· Show Cause Notice issued on 29.12.2008.  Reply received on 14.01.2009. The unit has submitted clarification regarding the Show Cause Notice for closure u/s 31(A) of the Air Act, 1981 for black emission observed from time to time including on 27.11.08 at 17.00 hrs that on 27.11.08 at 16.48 hrs, unit no.-3 had to be stopped as some foreign material came in coal mill 3-4 along with coal. The foreign material caused damage to one grinding ball of coal mill 3-4. Before this sudden occurrence/ abnormalities could be detected, some coarse coal was feeded into boiler and the caused black emission. However, as soon as this source of abnormality was detected and high opacity observed, the unit was forced to shut down at 16.48 hrs. The reply also consists of reasons regarding the light up of unit No.5 on 27.11.2008 that during the light up of unit, more care and precautions are being taken and generally the light up of unit is avoided during the day time. However, as a universal practice of thermal power plant stations, before light up, the ID Fans are started followed by FD Fans and complete boiler is purged for some time as per the design to evacuate the boiler from any unburnt/combustible gases for safety purposes. After the above purging (during this time some emission of high opacity may be observed) the boiler is light up with ESP fields being kept “ON” to minimize the SPM level.

· I.P. Station is a very old power station (more than 35 years) and is likely to be closed soon in 2009 and therefore, only very needful/prudent expenditure under various close monitoring is being allowed to run the machine in safe and economical manner.

· DPCC Monitoring results for the months of Dec, 2008 are as under:

	S.No.

 
	Sampling Location


	Concentration in mg/Nm3 during Dec, 2008

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	1.
	Duct of unit no. II
	47
	400
	285

	2.
	Duct of unit no. III
	#
	#
	#

	3.
	Duct of unit no. IV
	43
	360
	286

	4.
	Duct of unit no. V
	#
	#
	#


 # Shutdown/Under Maintenance 
· DPCC Monitoring reports for waste water from Ash Pond for the month of Dec, 2008.
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	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	STP/

ETP/

CMB
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature
	0.50
	
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	31.12.08
	--
	--
	--
	7.7
	8.8
	Nil
	--
	--
	--
	--
	--
	--
	No discharge from ash pond


Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE         AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Rajghat Power Station

Status of Consent: Applied for “Consent to Operate” on 30.06.2004.

Action Taken:

· Letter issued to Pr. Secretary (Power) on 17.07.2007.

· The unit has replied that Ministry of Power, GNCTD has taken a decision for closing the coal based power plants in near future. A request has been made that as huge funds are required for installation of ETP, permission may be given that water is used for transporting fly ash to ash ponds. 

· This power station was also inspected by Zonal office Lucknow of CPCB on 21.08.07 & observed that untreated effluent (TSS- 198 mg/l) is being discharge into to river. They recommended:

a. Adequate waste water treatment plant should be provided.

b. An interrupted access to ash pond area should be provided.

c. CPCB has desired that RTPS take measures to implement the above recommendations within a time frame agreed mutually and be asked to submit time targeted Action Plan & ATR.

Decision taken in meeting held on 19.10.07:

A letter may be issued to General Manager to comply with CPCB directions given during inspection by CPCB on 21.8.07. This compliance must be done by 31.12.07. 

Action taken/ Status w.r.t. the meeting held on 19.10.07:

i. Letter issued on 5.11.07 communicating above decision (C/353). 

ii. Though reply is awaited, a letter dated 29.12.07 (C/355) received indicating that revised proposal for installation of low cost water treatment plant to utilize waste water in ash handling plant is under consideration. RPH has also initiated the following works : 

· Cleaning of existing station drain pit about 6m diameter and 6m deep which was already available for treating the station drain water for decantation and action have been initiated for new pipes to connect and pumping the decanted water to ash pump water tank to reuse for transporting ash slurry to ash pond meeting the proposal of DPCC in the letter of the year 2004. 

· Submersible pump installed to reuse backwash water of the filters at WTP and going to drain also reduced.

· Piping connection is almost in final stage for sending the sludge slurry water from WTP (neutralization pit) to ash pond. Thus the discharge at station drain will be further reduced substantially.

· RPH has not submitted their compliance report in respect to the letter dated-5.11.07.  However requested for issuing consent to operate.

Decision taken in meeting held on 09.01.08:

MS to speak to the concerned General Manager. The deficiencies noted by the inspection team of CPCB have not been corrected and not replied to. Letter be issued with the last opportunity giving to the unit to comply with the CPCB directions during inspection and complied with it fully.
Action taken/ Status w.r.t. the meeting held on 09.01.08:

Replies dated 07.01.08 and 08.01.08 were received from the power plant (C/365-367 of the file). Power plant submitted that:

1. Regarding adequate treatment  to the effluent through station drain into the river, the action taken are;

a. One pump alongwith its discharge line are laid and already started reusing back wash water of he gravity filters as inlet to the Aerator (Clarifier) and thus reduced consumption of water and consequently effluent quantity in station drain. Procurement action for one additional pump is also in process to have permanent arrangement.
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b. Needful discharge line piping has been laid from sludge slurry water pumps (clarifier) and connected to the Ash Surry Line and sludge being discharged to the Ash pond thus reducing also the effluent quantity to the station drain.

c. The installation of pumps and lying of discharge pipelines up to the ash pump water tank will be completed by the end of March, 2008. The decanted water of the station drain pit will be utilized for transportation of fly ash in slurry form to the ash pond as per advice of DPCC.


In the meantime time, the above said station drain pit having diameter of 6 meter and depth of 6 meter meant for decantation have been cleaned after removing sludge deposited.


The effluent from various plants including balance effluent from WTP (Neutralization Pit) will be collected in this cleaned station drain pit from where the decanted water be reused for transportation of ash slurry to the ash pond and thus virtually there will be no effluent discharge to river through station drain.

2. Un- interrupted access to ash pond-area – Reg.

The grass/ wild bushes grown in the area during monsoon has been cut and the needful repair of the roads has been done to remove the interruption.

Recommendation of CPCB for dry ash collection –Reg.

Ash Silo Systems have been revived and dry fly ash collection is being done by the cement manufacturer (about 1000 MT/month).

3. Regarding bringing down the particulate matter emission;

Regulation of Bapcon Control System and Auto Rapping System is being done regularly for better operation of ESP fields; attending nozzles of hydro vector and leakages etc. in the ash evacuation system; scheduling have been planned to wash/ clean the ESP insides; straightening/ adjustment of gaps between emitting electrodes and collecting plates as per the recommendation of OEM; replacement of segregating valves & solenoids are being done during shut down to get the maximum efficiency of the combustion of fuel also regulated and use of furnace oil is being minimized to bring down the particulate matter emission through stack well within the permitted limit.

4. Regarding Zero discharge by reusing ash pond overflow water:

The scheme for reusing decanted water from ash pond overflow was initiated but kept in abeyance for some period with the instructions received from Ministry of Power, GNCTD to avoid excess O&M expenditure for the coal based power station like RPH and IPStn. Which are to close by 2010 of so in due course.

However, with the expected running of RPH beyond 2010, this case has been taken up again on the basis of CPCB’s / DPCC’s recommendation for recirculation of ash pond water for making ash slurry to conserve water. This work is expected to be completed by the end of the year 2008.

The above said replies have been forwarded to CPCB vide letter dated 11.02.08 after necessary approval on file.

Decision taken in meeting held on 28.02.2008:

Letter to be issued bearing the directions for meeting the standard of Particulate Matter of 50 mg/Nm3 along with the copy of the minutes wherein it was decided that the standard for Particulate Matter has been made stringent of 50 mg/Nm3. In case high emission is caused due to high ash content in coal, the ash content may be reduced in the fuel (coal).
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Action taken/ Status w.r.t. the meeting held on 28.02.2008:

· Letter issued to RTH on 24.03.08 to meet the standard of 50 mg/Nm3 for Particulate Matter. 

· A reply dated 02.05.08 received from RPH. They submitted that “in order to achieve the SPM level of 50mg/Nm3, they have taken up the matter with M/s. Bharat Heavy Electrical Limited, the OEM, M/s. Alstom Projects India Limited along with other concerned agencies. All these agencies have opined that the SPM level cannot be reduced directly to 50mg/Nm3 from 150mg/Nm3. The desired level can be achieved in phases. In the first phase the same will be reduced to 80mg/Nm3 by upgradation of the existing controllers of ESPs and in second phase either by increasing the volume of the collecting area of the ESP hoppers or by flue gas conditioning”.

· RTPS has also not submitted any time bounded programme to achieve emission <50 mg/Nm3.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

The unit should reduce the emission in a phase wise manner as submitted by them. In the first phase they must reduce to 80 mg/Nm3 by upgradation of the existing ESPs. A time bound programme may be submitted to achieve the emissions up to 80 mg/Nm3.

Action taken/ Status after the meeting held on 12.05.08:

· Letter issued to IPTPS on 29.05.08.  Reply dated 19.07.08 is received.  Accordingly, scheme to improve the performance of ESP with the advanced controllers and software controlled Rapping system, is worked out to achieve the stack emission within 80 mg/Nm3 in first phase. Offers are being invited from OEM/ OES- BHEL and ALSTOM. Efforts are being made to finalize order by Nov, 2008 and implement during this financial year and RPH will be able to achieve the stack emission within 80 mg/Nm3 by 31.03.09.

· A letter dated 14.07.08 was also received from RPH, requesting to issue the consent.

· DPCC Monitoring results for the months of May & June 2008 are as under and meeting the standards:   

	S.No.

 
	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	
	
	May,08
	June,08
	May ,08
	June ,08
	May ,08
	June,08

	1.
	Path “A” of unit-I
	140
	144
	312
	340
	234
	260

	2.
	Path “B” of unit-I
	124
	120
	316
	352
	234
	260

	3.
	Path “A” of unit-II
	113
	#
	320
	#
	214
	#

	4.
	Path “B” of unit-II
	87
	#
	328
	#
	214
	#


· Decision of Consent Management Committee in its meeting dated 29.07.2008:
Issue letter directing them to ensure that they will comply with the dates given. 


Action taken/ Status after the meeting held on 29.07.08:

Letter issued on 14.08.08.  Reply dated 05.09.08 received from the unit stating that the stack emission within 80 mg/Nm3 will be achieved in first phase by 31.03.09. 

· DPCC Monitoring results for the months of July & August,  2008 are as under and meeting the standards:   
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	S.No.

 
	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	
	
	July,08  
	Aug,08
	July ,08
	Aug ,08
	July,08
	Aug,08

	1.
	Path “A” of unit-I
	116
	130
	400
	380
	263
	260

	2.
	Path “B” of unit-I
	98
	124
	426
	400
	263
	260

	3.
	Path “A” of unit-II
	137
	141
	415
	420
	260
	305

	4.
	Path “B” of unit-II
	126
	144
	400
	408
	260
	305


# Shutdown/Under Maintenance 

Decision of CMC (MSW) in its meeting dated 10.10.2008:

To be take up in next month CMC(MSW) with Sept. & October 2008 monitoring reports.
Action taken/ Status after the meeting held on 10.10.08:

· DPCC Monitoring results for the months of Sept/ Oct & Nov,  2008 are as under:
	S.No.

 
	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	
	
	Oct. 08  
	Nov. 08
	Oct. 08  
	Nov. 08
	Oct. 08  
	Nov. 08

	1.
	Path “A” of unit-I
	101
	134
	360
	360
	286
	283

	2.
	Path “B” of unit-I
	126
	145
	380
	368
	286
	283

	3.
	Path “A” of unit-II
	96
	120
	340
	340
	202
	253

	4.
	Path “B” of unit-II
	93
	112
	360
	352
	202
	253


# Shutdown/Under Maintenance 
· DPCC Monitoring reports for waste water from Ash Pond for the month of November, 2008.

	Name of the Plant 
	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	
	Remarks 

	
	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	STP/

ETP/

CMB
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	
	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature
	0.50
	
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	Rajghat Thermal Power Station 
	03.11.2008
	7.8
	20
	<1.0
	--
	--
	--
	--
	--
	--
	--
	--
	--
	--


· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

It has accepted to reduce the stack emission upto 80 mg/Nm3 in first phase. PERT and CPM chart may be asked.

Action taken/ Status after the meeting held on 05.12.08:

· Letter issued on 29.12.08. Reply dated 22.01.09 alongwith required programme w.r.t. emission of PM in the stacks to reduce to 80 mg/Nm3 is received. Accordingly, the work will be completed by Aug, 2009.
· The unit has also submitted a letter dated 05.01.09 with a request to consider application for consent to operate submitted in June, 2004 alongwith fee for 10 years. 
· DPCC Monitoring results for the months of  Dec,  2008 are as under:
	S.No.

 
	Sampling Location


	Concentration in mg/Nm3

	
	
	Particular Matter
	Sulphur Dioxide
	Nox

	1.
	Path “A” of unit-I
	#
	#
	#

	2.
	Path “B” of unit-I
	#
	#
	#

	3.
	Path “A” of unit-II
	#
	#
	#

	4.
	Path “B” of unit-II
	#
	#
	#


# Shutdown/Under Maintenance 
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· DPCC Monitoring reports for waste water from Ash Pond for the month of Dec, 2008.

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	STP/

ETP/

CMB
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature
	0.50
	
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	02.01.09
	7.2
	32
	<1.0
	--
	--
	--
	--
	--
	--
	--
	--
	--
	--


Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Pragati Power Station, ITO

Status of Consent: Applied for renewal of the Consent vide ID. No. 24530 dated 18.12.07 (Earlier Consent to operate issued on 21.12.05 and valid up to 12.01.08).

Action Taken:

· Letter issued on 20/8/2007. No reply received so far.

· A letter dt 27.08.07 received from Manager (T) Environment, IPGCL-PPCL, informing that-

- MCD is not allowing to dump the Water Treatment Plant (WTP) sludge at Compost Plant /SLF site of MCD.

- The sludge is being dumped at the side of RTPS ash pond to be used by fly ash manufacturer because it contains more than 50% CaO and it is non hazardous.

- Part of this sludge gets mixed with wet ash in the ash pond as the less quantity required for bricks manufacturing.

- Requested to instruct MCD to accept the sludge.

- If it is not materialized, the disposal in ash pond / fly ash brick manufacturer stockyard will be continued and requested to moderate suitably the Terms & Conditions of the consent issued. 

Decision taken in meeting held on 19.10.07:

In response to letter received from Manager (T) Environment, IPGCL-PPCL be informed that the sludge may be used for brick manufacturing by using available technology and with the help of NGOs like Development Alternative. 

Action taken/ Status w.r.t. the meeting held on 19.10.07:

· Letter issued on 5.11.07 communicating above decision. 

· No reply received so far.

Decision taken in meeting held on 09.01.08:

MS to speak to the concerned General Manager and reminder letter to be issued. 

Action taken/ Status w.r.t. the meeting held on 09.01.08:

A reply was received from the power plant (C/339-351). The reply was not with concrete step taken for utilization of sludge. Reminder letter has been issued on 15.02.08.

Decision taken in meeting held on 28.02.2008:

To be put up in next CMC (MSW) Meeting.

Status of monthly monitoring conducted by DPCC laboratory:

· Noise monitoring report for DG set is not meeting the prescribed standards. Stack monitoring report is also not submitted as having DG set of 1250 KW.
· Monitoring reports for the month of January and Feb. 2008 were meeting the prescribed standards. However, monitoring could not be conducted in March, 2008 as the plant was found under maintenance/ shutdown on 19.03.08.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

Deficiencies may be informed to the unit, for expeditious action for their rectification. 

Action taken/ Status after the meeting held on 12.05.08:

· Letter issued on 02.06.08.  Replies dated 27.06.08 and 02.0708 were received from the unit, accordingly PPCL have initiated the process for acoustic enclosure of DG Set for compliance of standard of noise pollution as desired by DPCC and it shall be installed in due course (Replies dated 27.06.08 and 02.07.08).
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· DPCC Monitoring results for the months of May & June 2008 are as under and meeting the standards:   

	S.No
	Sampling Location 
	Concentration of Nox in ppm

	
	
	May, 08
	June,08

	1.
	Duct of unit-I
	10
	10

	2.
	Duct of unit-II
	10
	10


Decision of Consent Management Committee in its meeting dated 29.07.2008:
Reminder may be issued to comply with respect to D. G. Set norms within 60 days. Call in CMC in Sep, 2008.

Action taken/ Status after the meeting held on 29.07.08:

· Reminder issued on 14.08.08.  Reply dated 12.09.08 & 15.09.08 received from the unit stating that best efforts will be made such that the work of acoustic enclosure shall be completed by 30th October, 2008.  Test report also will be sent within this period. 

· DPCC Monitoring results for the months of July & August 2008 are as under and meeting the standards:   

	S.No
	Sampling Location 
	Concentration of Nox in ppm

	
	
	July, 08
	August,08

	1.
	Duct of unit-I
	10
	#

	2.
	Duct of unit-II
	15
	#


Decision of CMC (MSW) in its meeting dated 10.10.2008:

With compliance report to be taken up in next CMC. 

Action taken/ Status after the meeting held on 10.10.08:  
Letter issued on 27.10.08.  The unit has submitted reply on 12.11.08 an informed that PPCL has placed the order on M/s OVN Trading Engineers Pvt. Ltd. for providing Acoustic Enclosure in Emergency DG Set on 25.10.08.  The firm has started the work after completing the contractual formalities on 06.11.08.  The job is expected to be completed in the first week of Dec. 2008. 

· DPCC Monitoring results for the months of Oct & Nov 2008 are as under:   

	S.No
	Sampling Location 
	Concentration of Nox in ppm

	
	
	Oct, 08
	Nov,08

	1.
	Duct of unit-I
	#
	10

	2.
	Duct of unit-II
	#
	10


· DPCC Monitoring reports for waste waster from Ash Pond for the month of November, 2008.

	Name of the Plant 
	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	
	Remarks 

	
	
	pH
	TSS
	Oil &                Grease
	pH
	Temperature Difference 
	Free available Chlorine
	STP/

ETP/

CMB
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	
	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature
	0.50
	
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	Pragati (Gas Based) Power Station 
	05.11.2008
	--
	--
	--
	--
	--
	--
	CMB
	--
	--
	--
	--
	--
	No discharge from CMB 


· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

Consent to Operate granted.
Action taken/ Status after the meeting held on 05.12.08:  
· Consent issued on 05.01.09.  
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· DPCC Monitoring results for the months of Dec. 08 are as under:   

	S.No
	Sampling Location 
	Concentration of Nox in ppm 

	1.
	Duct of unit-I
	10

	2.
	Duct of unit-II
	15


· DPCC Monitoring reports for waste waster for the month of, Dec. 2008.

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	
	Remarks 

	
	pH
	TSS
	Oil &                Grease
	pH
	Temperature Difference 
	Free available Chlorine
	STP/

ETP/

CMB
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature
	0.50
	
	6.5-9.0
	50
	10
	30
	250
	STP Standards 

	02.01.09
	--
	--
	--
	--
	--
	--
	CMB
	6.8
	32
	1.6
	23
	60
	--


Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

No action.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

I.P. Gas Turbine Power Station

 Status of Consent: Applied for renewal of the Consent vide ID. No. 24589 dated 27.12.07 (Earlier Consent to operate issued on 23.03.07 and valid up to 04.01.08).

Action Taken: A letter dt 27.08.07 received from Manager (T) Environment, IPGCL-PPCL, informing that-

- MCD is not allowing to dump the Water Treatment Plant (WTP) sludge at Compost Plant /SLF site of MCD.

- The sludge is being dumped at the side of RTPS ash pond to be used by fly ash manufacturer because it contains more than 50% CaO and it is non hazardous.

- Part of this sludge, get mixed with wet ash in the ash pond as the less quantity required for bricks manufacturing.

- Requested to instruct MCD to accept the sludge.

- If it is not materialized, the disposal in ash pond / fly ash brick manufacturer stockyard will be continued and requested to moderate suitably the Terms & Conditions of the consent issued. 

Decision taken in meeting held on 19.10.07:

In response to letter received from Manager (T) Environment, IPGCL-PPCL be informed that the sludge may be used for brick manufacturing by using available technology and with the help of NGOs like Development Alternative. 

Action taken/ Status w.r.t. the meeting held on 19.10.07:

· Letter issued on 5.11.07 communicating above decision. 

· No reply received so far.

Decision taken in meeting held on 09.01.08:

MS to speak to the concerned General Manager and reminder letter to be issued. 

Action taken/ Status w.r.t. the meeting held on 09.01.08:

A reply was received from the power plant (C/440-452). The reply was not with concrete step taken for utilization of sludge. Reminder letter has been issued on 15.02.08.

Decision taken in meeting held on 28.02.2008:

To be put up in next CMC (MSW) Meeting.

Status of monthly monitoring conducted by DPCC laboratory:

· Noise monitoring report for DG set is not meeting the prescribed standards.

· Last three months monitoring reports for the months of January to March, 2008 were meeting the prescribed standards. However concentration of NOx was found beyond the prescribed limit of 75ppm in GT1, GT5 and GT6 which were 90ppm, 90ppm and 80ppm during monitoring on 17.12.07.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Deficiencies may be informed to the unit, for expeditious action for their rectification. 

Action taken/ Status after the meeting held on 12.05.08:

· Letter issued to IPTPS on 03.06.08.  Replies dated 27.06.08 & 19.07.08 are received.  As per letter dated 27.06.08 received on 01.07.08, Nox emission (59 ppm) was well within the norm as per monitoring dated 30.04.08 as conducted by the unit M/s. Shri Ram Institute for Industrial Research.  Accordingly, deficiencies observed in DG set for not meeting insertion loss is being attended by the station for expeditious as soon as the order is placed, the commissioning date of compliance will be intimated.

· DPCC Monitoring results for the months of May & June 2008 are as under and meeting the standards:   

	S.No
	Sampling Location 
	Concentration of Nox in ppm

	
	
	May, 08
	June,08

	1.
	GT-1
	70
	#

	2.
	GT-2
	70
	#

	3.
	GT-3
	#
	#

	4.
	GT-4
	#
	#

	5.
	GT-5
	#
	70

	6.
	GT-6
	#
	70


# STG Shutdown.  
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Decision of Consent Management Committee in its meeting dated 29.07.2008:
Reminder may be issued to comply with respect to D. G. Set norms within 60 days. 

Action taken/ Status after the meeting held on 29.07.08:

· Reminder issued on 18.08.08. Reply dated 03.09.08 received from the unit stating that the compliance report shall be forwarded to DPCC alongwith the fresh monitoring report of the DG Set noise levels after providing and commissioning of acoustic insulation.  They also informed that available DG Set is operated only for couple of minutes daily to ensure healthiness of system for meeting any emergency in case of grid failure.  The mandatory requirement is under compliance and would take couple of months. 
· A letter dated 24.11.08 also received from the unit informing that the contract for providing the acoustic package to DG Set at GTPS to reduce noise pollution has been placed on M/s OVN trading Engineers Pvt. Ltd. vide No. SM/GT/CS-1/3044/08-09/4547, dated 22.11.08 and completion period is 1 ½ -2 months.  
· DPCC Monitoring results for the months of July & August 2008 are as under and meeting the standards:   

	S.No
	Sampling Location 
	Concentration of Nox in ppm

	
	
	July, 08
	August,08

	1.
	GT-1
	70
	70

	2.
	GT-2
	70
	#

	3.
	GT-3
	#
	#

	4.
	GT-4
	#
	#

	5.
	GT-5
	60
	70

	6.
	GT-6
	#
	#


# STG Shutdown.
Decision of CMC (MSW) in its meeting dated 10.10.2008:

Issue letter to file compliance of DG Set norms within October. To be taken up in next CMC. 

Action taken/ Status after the meeting held on 10.10.08:
· Letter Issued on 27.10.2008. The unit has submitted reply on 24.11.08 and informed that the contract for providing the acoustic package to our station DG Set at OTPS to reduce noise pollution has been on M/s OVN trading Engineers Pvt. Ltd. on 22.11.08 and completion period is 1-2 months.  The party has been requested to mobilize the site at the earliest and complete the work, which shall be done within the contractual period.  
· DPCC Monitoring results for the months of Oct & Nov 2008 are as under: 
	S.No
	Sampling Location 
	Concentration of Nox in ppm

	
	
	Oct, 08
	Nov,08

	1.
	GT-1
	70
	60

	2.
	GT-2
	70
	#

	3.
	GT-3
	#
	60

	4.
	GT-4
	#
	60

	5.
	GT-5
	60
	70

	6.
	GT-6
	#
	70


# STG Shutdown.
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· DPCC Monitoring reports for waste waster from Ash Pond for the month of November, 2008.

	Name of the Plant 
	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	
	Remarks 

	
	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	STP/

ETP/

CMB
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	
	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature
	0.50
	
	6.5-9.0
	50
	10
	30
	250
	STP

Standards 

	I.P. Gas Turbine Power Station 
	05.11.2008
	--
	--
	--
	--
	--
	--
	ETP
	7.6
	36
	1.2
	28
	76
	--


· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

Consent to Operate granted.

Action taken/ Status after the meeting held on 05.12.08:
· Consent issued on 05.01.09.  

· DPCC Monitoring results for the months of Dec. 2008 are as under:   

	S.No
	Sampling Location 
	Concentration of Nox in ppm

	1.
	GT-1
	70

	2.
	GT-2
	70

	3.
	GT-3
	60

	4.
	GT-4
	#

	5.
	GT-5
	70

	6.
	GT-6
	#


# STG Shutdown.
· DPCC Monitoring reports for waste waster for the month of Dec., 2008.

	Date of Monitoring 

 
	Ash Pond Discharge 
	Condenser Cooling Water
	
	Remarks 

	
	pH
	TSS
	Oil & Grease
	pH
	Temperature Difference 
	Free available Chlorine
	STP/

ETP/

CMB
	pH
	TSS
	Oil &

Grease
	BOD
	COD
	

	Standards 
	6.5-8.5
	100
	20
	6.5-8.5
	Not more than 100C higher than intake water temperature
	0.50
	
	6.5-9.0
	50
	10
	30
	250
	STP

Standards 

	02.01.09
	--
	--
	--
	--
	--
	--
	ETP
	7.1
	36
	1.2
	26
	68
	--


Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

No action.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Pragati Power Station , Bawana

Status of Consent: Consent to establish issued for one year for 1600 MW on 27/7/2007.

Decision taken in meeting held on 26.06.2007:

Issue consent to the unit for 1600 MW considering Environmental Clearance granted by MoEF for 1600 MW.

Action taken/ Status w.r.t. the meeting held on 26.06.2007:

Consent to establish issued for one year for 1600 MW on 27/7/2007.

Decision of Consent Management Committee in its meeting dated 19.10.2007:

No action.

Remarks:-
No application for extension of  consent to establish received.

Decision of Consent Management Committee in its meeting dated 29.07.2008:
Ask the unit to file latest status report and item-wise compliance of Environmental Clearance conditions through an affidavit within one month. 

Action taken/ Status after the meeting held on 29.07.08:

Letter issued on 14.08.08.  Reply dated 12.09.08 received from the unit with para wise compliance and present status of the project.  Accordingly, contract was awarded to BHEL on 30.04.08.  Preparation of drawings, design memorandums etc. by BHEL are in progress.  BHEL has also completed the Survey and Soil Investigation of the site.  The Civil Works are schedule to commence by October, 2008.

Decision of CMC (MSW) in its meeting dated 10.10.2008:

No action. 
· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

The progress report along with PERT and CPM chart may be asked.

Action taken/ Status after the meeting held on 05.12.08:
Letter issued on 29.12.08. A reply dated 20.01.09 received form the unit enclosing with progress of the work and copy of L-1/PERT Network.   The progress of the project is as under:- 

1. Hon’ble Prime Minister laid the foundation stone.

2. Turn Key Contract awarded to BHEL.

3. Contract signed.

4. BHEL has awarded civil contract to M/s. Era who have since mobilized at site.  The construction of boundary wall is in progress since 30.09.08.

5. Pilling work has also started since 20.12.08.

6. Excavation, leveling and dressing work are also in progress.

7. Design and Engineering of various equipments is also in progress.

Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

No action.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Combined Cycle Power Plant at Sector-11, Rohini, Delhi BY NDPL

Status of Consent: Applied for Consent to establish for 108 MW on 10.07.08.

Details of the Project:

· Proposed capacity of the plant is 108 MW (Natural Gas based Combined Cycle Power Plant). 

· Plot Area     :- 



24281 sq. m 

· No. of workers 
:-


60

· Proposed date of commissioning: -
May, 2009 (Open Cycle) and August, 2009 





(Closed Cycle).

· Total Capital Investment :-

Rs. 256.48 Crores

· Water consumption: -


8640 KLD (Treated Effluent from Rithala 





STP).

· ETP proposed for treatment of 4320 KLD and after treatment effluent will be utilized for floor washing, dust suppression and greenbelt while the remaining will be discharged to nallah near the project site.  As per the norms.

· Domestic effluent:-


108 KLD to be disposed of Sewer of Drain. 

· No D.G. Set proposed 




Remarks:-  An application for hearing under EIA notification has also been received in DPCC and is under process by Consent Management Cell. Public hearing is scheduled on 22.08.08. 

Decision of Consent Management Committee in its meeting dated 29.07.2008:
No action. 

Action taken/ Status after the meeting held on 29.07.08:


Nil. 

Decision of CMC (MSW) in its meeting dated 10.10.2008:

Wait for Environmental Clearance from MOEF. To be taken up in next CMC (MSW). 

Remarks: 

Environmental Clearance is yet to be received from MOEF
· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

Wait for Environmental Clearance from MoEF.

Action taken/ Status after the meeting held on 05.12.08:
Environmental Clearance is yet to be received from MOEF.
Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Wait for Environmental Clearance.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

	Status of Fly ash generation and its utilization by Thermal Power Plants in year 2008-09

	
	
	
	
	
	
	
	
	

	The monthly tabular status of three coal based Power Plant is as given below:

	1. I.P. Thermal Power Station 

	
	
	
	
	
	
	
	
	

	S. No.
	Month
	Ash Generation & Utilization
	Ash Utilization in the main area (LTPM)

	
	
	Ash Gen. 
(LTPM)
	Ash Utilization
((LTPM)
	% Utilization 
	Bricks 
	Cement 
	Road & 
Embankment 
	Land filling
& others 

	1
	April, 2008
	0.278
	0.297
	106.83
	0.056
	--
	0.023
	0.218

	2
	May, 2008
	0.317
	0.16
	50.47
	0.06
	--
	0.104
	0.1

	3
	June, 2008
	0.246
	0.337
	136.99
	0.03
	--
	0.093
	0.203

	4
	July, 2008
	0.244
	0.316
	129.5
	0.022
	0.055
	0.074
	0.146

	5
	Aug., 2008
	0.209
	0.154
	73.68
	0.013
	0.025
	0.061
	0.042

	6
	Sept, 2008
	0.170
	0.219
	128.82
	0.035
	0.045
	0.01
	0.078

	7
	Oct., 2008
	0.193
	0.461
	238.86
	0.031
	0.035
	--
	0.385

	8
	Nov., 2008
	0.193
	0.336
	174.91
	0.035
	0.03
	--
	0.301

	9
	Dec., 2008
	0.274
	0.37
	135.04
	0.028
	0.077
	0.365
	0.265

	 
	Total 
	2.124
	2.68
	 
	0.31
	0.267
	0.73
	1.738

	
	
	
	
	
	
	
	
	

	2. Rajghat Thermal Power Station  

	
	
	
	
	
	
	
	
	

	S. No.
	Month
	Ash Generation & Utilization
	Ash Utilization in the main area (LTPM)

	
	
	Ash Gen. 
(LTPM)
	Ash Utilization
((LTPM)
	% Utilization 
	Bricks 
	Cement 
	Road & 
Embankment 
	Land filling
& others 

	1
	April, 2008
	0.19
	0.172
	84.72
	0.012
	0.011
	0.148
	0

	2
	May, 2008
	0.149
	0.232
	155.7
	0.037
	0.023
	0.172
	0

	3
	June, 2008
	0.179
	0.324
	181
	0.039
	0.036
	0.248
	0

	4
	July, 2008
	0.215
	0.163
	75.81
	0.04
	0.035
	0.087
	0

	5
	Aug., 2008
	0.201
	0.069
	34.32
	0.004
	0.027
	0.037
	0

	6
	Sept, 2008
	0.205
	0.178
	86.8
	0.03
	0.049
	0.021
	0.076

	7
	Oct., 2008
	0.206
	0.075
	36.55
	0.035
	0.004
	 
	0.035

	8
	Nov., 2008
	0.217
	0.181
	83.68
	0.022
	0.044
	 
	0.115

	9
	Dec., 2008
	0.220
	0.155
	70.45
	0.029
	0.051
	 
	0.074

	 
	Total 
	0.178
	1.549
	 
	0.248
	0.28
	0.713
	0.3

	
	
	
	
	
	
	
	
	

	3. Badarpur Thermal Power Station  

	
	
	
	
	
	
	
	
	

	S. No.
	Month
	Ash Generation & Utilization
	Ash Utilization in the main area (TPM)

	
	
	Ash Gen. 
(TPM)
	Ash Utilization
((TPM)
	% Utilization 
	Bricks/ Blocks 
	Cement 
	Road & 
Embankment 
	Land filling
& others 

	1
	April, 2008
	61936
	25550
	26.58
	--
	--
	--
	--

	2
	May, 2008
	101182
	32040
	31.67
	--
	--
	--
	--

	3
	June, 2008
	112169
	33490
	29.86
	--
	--
	--
	--

	4
	July, 2008
	114946
	83050
	72.25
	--
	--
	--
	--

	5
	Aug., 2008
	115469
	88010
	76.22
	--
	--
	--
	--

	6
	Sept, 2008
	130449
	119390
	91.52
	--
	--
	--
	--

	7
	Oct., 2008
	97132
	87920
	90.52
	--
	--
	--
	--

	8
	Nov., 2008
	90129
	101700
	112.84
	--
	--
	--
	--

	9
	Dec., 2008
	92552
	106670
	115.25
	--
	--
	--
	--

	 
	Total 
	950164 
	677820 
	 
	 63070
	16480
	21870
	379570


Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Ask Thermal Power Plants to submit monthly report on fly ash generation & its utilization and efforts for 100% fly ash utilization.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell
Agenda 3.

Modern Poultry & Egg market at Ghazipur, New Delhi.

Name of the agency: M/s Delhi Agriculture Marketing Board, 9, Institutional Area, Pankha Road, Janakpuri, New Delhi-110058.
Particulars of the project: Modern Poultry & Egg market at Ghazipur, New Delhi.
Status of Consent: 

Applied for consent to establish under Air & Water Acts vided ID. No. 24811                            dt. 24.01.08 (C/1-98).
Details of the project: 

a. Product is dressing of Poultry birds- 48 lakhs birds/ month. 

b. Raw material is Poultry birds- 576 lakhs/ annum. 

c. Proposed Investment on the project is Rs.133.5 crores.

d. Quantity of waste to be disposed per day is 30 TPD.

e. Total Plot Area is 60200 sq m and Built up area- 48160 sq m

f. Sanctioned Power Load /power required– 2925 KW

g. Proposed to be commissioned from March, 2010.

h. No of workers: 

a) During construction phase – 100 b) During operational phase-   25

i. Water consumption:

Domestic - 91000 LPD, 
Industrial cooling/ boiler feeds - 92000 LPD       processing   - 1120000 LPD,
Other (Gardening) – 108000 LPD

j. Quantity of domestic waste generated is 80000 LPD and Industrial is 1100000 LPD

k. Proposed Effluent Treatment Plant of 1200 KLD with tertiary treatment & UV Irradiation and reuse in flushing, HVAC, DG, Horticulture (C/52 of the file). A STP of 200KLD is also proposed (C/58 of the file). 

l. DG Sets proposed to be installed – 2 X 1000 KVA + 2 X 625 KVA.

m. Land allotted by DDA for this purpose (allotment letter at C/4-6)  

Remarks:

As per the provisions of EIA notification dated 14.09.06 the following construction projects are to be required Environmental Clearance from MoEF:

a) Building and Construction Projects having built up area ≥ 20000 sqm and < 150000 sqm of built up area. 

b) Townships and Area Development Projects having covering an area ≥ 50 ha and or built up area ≥150000 sqm.   

Decision taken in meeting held on 28.02.08:

Letter to be sent for EIA clearance indicating that if they have any doubt they may contact the EIA cell of MOEF and the copy of this letter will be sent to EIA Cell of MOE&F.

Action taken/ Status after the meeting held on 28.02.08:

Letter issued for Environmental Clearance on 24.03.07. Environmental clearance/ reply are still awaited from the unit or MOEF.

Decision of Consent Management Committee in its meeting dated 12.05.2008:

Issue reminder letter for Environmental Clearance. 

Action taken/ Status after the meeting held on 12.05.08:

Reminder issued on 03.06.08. Reply dated 09.06.08 received from the DAMB with a copy of letter received from MOEF regarding processing of application for EC and informed that after getting EC, copy of the same will be submitted to DPCC. 

Decision of Consent Management Committee in its meeting dated 29.07.2008:
Ask the unit to apply for authorization under HWM Rules and inspect the unit. 

Action taken/ Status after the meeting held on 29.07.08:

· Letter issued to apply for authorization. The unit has applied on 19.09.08 for Authorization under Hazardous Waste Rules.
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Unit was inspected on 11.09.08. The following observations were made during the inspection:-

1. No construction activity/excavation is started so far for the proposed project of setting up of mechanized chicken dressing plant at Gazipur, Delhi. 

2. Presently, poultry market is running in two sheds having 88 Shops, Paultry premises is very near to the MCD slaughter House.

3. Facility of slaughtering of birds through manual operation is provided by the DAMB in the adjacent portion of market for which no permission has been taken from DPCC.

4. Approx 35,000 birds are slaughtered per day. Ground water supply (one bore of 12” diameter & 5 bore of 4” diameter) is provided for washing and other ancillary activities during slaughtering of birds.

5. A large quantity of trade effluent is being discharged in open drain leading to the main drain without any treatment (Approx. 6 Lakh liters/day).

6. Effluent Treatment Plant has not been installed for the existing slaughtering activity.

Decision of CMC (MSW) in its meeting dated 10.10.2008:

Ask the unit to apply for Consent to Establish for the existing unit immediately and to install ETP within 90 days in view of the very large quantity of trade effluent being discharged. 

Action taken/ Status after the meeting held on 10.10.08:

Letter issued on 27.10.2008.  The unit has furnished a reply on 21.11.08 and submitted that the installation of ETP has already been initiated for the existing Slaughtering system and is on fast track for its commissioning at site Consent to establish/Operate is being applied.

However, they has informed that the consent to establish for the above mentioned new project may please be granted as the project is to be completed before the Common Wealth Games 2010 and to provide the hygienic food for Delhi, NCR area and also to the participants visitors in Common Wealth Games 2010 and it is also clarified by them that construction activities can only be started at site after obtaining the consent to establish from DPCC.

· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

Directions be issued by MS, DPCC for immediate installation of ETP within 60 days. Copy be given to Chief Secretary and Secretary, Agriculture. MS also to speak to VC, DAMB.

Action taken/ Status after the meeting held on 05.12.08:
Direction issued on 22.01.09. Reply is awaited.

Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Municipal Waste Complex at Gazipur Bio-gas Plant Site

Name of the agency: M/s New Delhi Waste Processing Company Ltd.
Particulars of the project: 

· Setting up of integrated Municipal Waste Complex at Gazipur Bio-gas Plant Site, Gazipur. 

· The capacity of the project would be 1200TPD. The treatment/ processing of the MSW would be based on DST-TIFAC technology of mixed municipal waste to RDF Fluff preparation and bio-gas generation from the organic waste. The power generation would be 10-12 MW.

 Status of Consent: 

Applied for consent to establish under Air & Water Acts on 22-06-07 & Consent to establish has been issued on 03.07.07 which was valid upto 21.06.08 (C/306) and expired on 22.06.08.

Status of authorization under MSW Rules: 

Applied for authorization under MSW Rules on 30.03.07 and Authorization under MSW Rules was also issued on 03.07.07 for the period of two years (C/303).

Action regarding clearance from other departments: 

Letter issued on 10.05.07 to the operator of the facility to submit:

· Detailed project report.

· Site clearance certificate from the land owning agency.

· EIA clearance from Ministry of Environment & Forests, Government of India.

· View of Air Force Base Station, Town and Country Planning, Department of UD, Govt. of India etc.

Status:
· Detailed project report is not received.

· Site clearance certificate from the land owning agency is not received.

· EIA clearance from Ministry of Environment & Forests, Government of India is not received.

· View of Air Force Base Station, Town and Country Planning, Department of UD, Govt. of India etc are not received.

Decision taken in meeting held on 26.06.07:

During the meeting it is decided that conditional Consent to Establish under Air and Water be issued as done in case of Timarpur Incineration Plant site and similarly conditional Authorization under MSW Rules be also issued. 

Action taken/ Status after the meeting held on 26.06.07:

· Consent to establish has been issued on 03.07.07. 

· As decided Authorization under MSW Rules was also issued on 03.07.07.  

Other remarks:

· Reminder letter has been issued on 25.02.08 to the operator for desired information.

· Reminder letter has also been issued on 25.02.08 to Hindon Air Force Station Base, Palam Air Force Station Base, Department of Town and Country Planning, Central Ground Water Board and Deputy Commissioner (East) for obtaining views/ comments /NOC regarding the project. 

· The comments has been received from Department of Town and Country Planning, UD vide letter dated 19.02.08 (C/337).

· Air Headquarter has issued NOC vide letter dated 26.07.07 (C/431).

· As per letter dated 24.04.08 of Deputy Director (LL), DDA addressed to General Manager, Delhi Power Company Ltd., The matter has been examined it is informed that as per MPD-2021, utility is permitted in all land use zones as intimated by Planning Department of DDA (C/436).

· Public hearing for Environmental Clearance has been conducted on 04.03.08 & proceeding is placed at (C/429). A copy of the proceeding has been forwarded to MOEF on 10.03.08 by EIA Cell.  
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Decision of Consent Management Committee in its meeting dated 12.05.2008:
Comment received from Town & Country Planning Organization, UD, Govt of India be forwarded to IL&FS and a reminder should go to others. 
Action taken/ Status after the meeting held on 12.05.08:

· Comments received from Town & Country Planning Organization, UD forwarded to IL&FS on 04.06.08 and reminder has also been issued on 04.06.08.  Reply has been received.  Accordingly they have incorporated all the comments of UD in the final EIA report submitted to MOEF for EC.  Copy of EC dated 15.04.08 is also enclosed (C/447-450).  

· No comments are received from CGWA and DC (East).  

· Consent to establish issued earlier has been expired and not applied for extension/operation of the consent.  

Decision of Consent Management Committee in its meeting dated 29.07.2008:
Ask the unit to file item-wise compliance of Environmental Clearance conditions through an affidavit within one month. 

Action taken/ Status after the meeting held on 29.07.08:
· Letter issued on 14.08.08 to project proponent for item wise compliance of  Environmental Clearance conditions through an affidavit within one month.  Letter also issued to CGWA and DC (East) for sending views/comments/NOC on 14.08.08.  

· Reply received from CGWA (C/498) with the comments.  A reply also received from project proponent with copy of Environmental Clearance and the copies of NOCs /Comments received from Airport Authority of India, Ministry of Defence, Central Ground Water Authority and DDA (C/496).

· Another reply dated 25.08.08 received from project component informing that item-wise compliance affidavit (as desired by DPCC) is submitted by the Company after selected implementation agency has finalized the construction and operations plans for the Project (C/490). 

Decision of CMC (MSW) in its meeting dated 10.10.2008:

Ask the unit to file compliance of the inputs received from various agencies within a month. To be taken up in November, CMC (MSW).

Action taken/ Status after the meeting held on 10.10.08:
Letter issued on 27.10.2008. The unit has submitted reply on 20.11.2008 and informed that for implementing the Gazipur Project we have selected the M/s Delhi International Airport Limited (in consortium with M/s Selco International Limited) through tariff based competitive bidding on 22nd October, 2008, who will complete the construction work within 2 years i.e. by Dec., 2010.

Hence, it was informed that the item-wise compliance affidavit to the Environmental clearance conditions issued by MOEF (as desired by DPCC) would be submitted by                M/s Delhi International Airport Limited (in consortium with M/s Selco International Limited) once they will finalize the project construction schedule & operations plans another EPC contractors for constructing the project.

Contd..3/-
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Thus it is requested that the matter may be suitably reconsidered.

It was also informed that all the conditions laid down by Central Ground Water Authority, Town & Country Planning office and Delhi Pollution Control committee in its Authorization & Consent to Establish clearance letter has been suitably addressed and incorporated in the EIA report prepared for the project for which MOEF has also accorded its clearance for the project.  In response to the General Conditions and Specific conditions laid down by MOEF while issuing the Environmental clearance for the project, the unit has submitted item wise response. 
· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

Issue direction to complete the project by December, 2009.
Action taken/ Status after the meeting held on 05.12.08:
· The unit has submitted two letters dated 15.12.08. Accordingly, the project has since been bid out and the consortium led by Delhi International Airport Ltd. (DIAL) with M/s Selco International Ltd. has been selected as implementing agency. Now, DIAL will soon start implementation of the project, which will take another 18-20 months time for making the project operational. Unit has requested to extend the validity of CTE for another three years. Unit has also requested to waive off the requirement of separate comments from DC (East) and amend the authorization in the name of “East Delhi Waste Processing Company Pvt. Ltd.” 
· Direction issued on 29.12.08. As per reply dated 19.01.09, M/s East Delhi Waste Processing Co. Pvt. Ltd. (EDWPCL) is a company specially incorporated to develop the project, has been transferred to the DIAL-Selco Consortium. Now, EDWPCL will implement the project, which as per planning, is expected to be operational by August, 2010.
Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta
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   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Development of Engineered Landfill site at Jaitpur/Tajpur

Name of the agency: Municipal Corporation of Delhi.
Particulars of the project: 

Development of Engineered Landfill site at Jaitpur/Tajpur

Agency applied by MCD is Birla Technical Services.

· The capacity of waste to be disposed off 1000-1500 TPD.  

· Construction, operation and maintenance of this ESL are to be carried out in 32.464 acre of abandoned stone quarry.  

· The present status of the site is as under as per brief note received from Sh. Arun Kumar (Spl. Proj.), MCD:- 

1. Survey of the quarry carried out.

2. All Geotechnical investigation including monitoring wells testing of rock/water sample completed.

3. Preliminary final designed checked and approved through IIT Delhi.

4. Final designed under submission by BTS.

5. De-watering completed in major portion/in progress in remaining isolated small pits.

6. Sumps/Pump houses established for stoppage of incoming water to the quarry.

7. Part fencing works completed.

8. Ramp under construction.

9. Sludge removed from dewatered area.

10. Site grading works in progress.

Status of authorization under MSW Rules: 

Applied for authorization under MSW Rules on 07.01.04 and Authorization under MSW Rules was also issued on 23.06.04 and valid till construction & operation of the project.

Status:
The site was inspected by DPPC official on 27.06.08 along with official from MCD and Birla Technical Services and it was observed that progress with regard to development of landfill site is very slow.  As per brief note received from MCD some public hindrance also was encountered in the month of April, 2008.  However, it is expected that by the end of this financial year, operation in one cell will be started in parallel to remaining construction activity.    

Decision of Consent Management Committee in its meeting dated 29.07.2008:
No action. 

Decision of CMC (MSW) in its meeting dated 10.10.2008:

No action. 

· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

Actual status report be submitted in next CMC to be held on 19.01.2009
Action taken/ Status after the meeting held on 05.12.08:
Letter issued on 29.12.08. EE (Special project), MCD informed that M/s. BTS has communicated their intention to exit from the contract.  Since then day by day they have reduced their manpower and workforce and as on date no work is going on at site.   Since M/s. BTS to whom the work was awarded has virtually abandoned the project unilaterally, the next course of action with regard to execution of the project is to be decided.  There are two possibilities which are as under:-  

1. The design submitted by M/S. BTS was sent to Prof. Dutta of IIT Delhi for checking who has found several queries in the said design.  Since M/s. BTS is now not continuing with the project, the design cannot be finalized at this juncture without their clarification.
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2. Now a day several companies might be interested in executing the work on BOT basis in interest of carbon credits without direct cost of MCD.  As such the work can be assigned for construction as well as operation & maintenance on BOT basis. 

In any case fresh tenders will have to be called as per status received form MCD.  

Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Ask latest status from MCD and put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta
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   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Setting up of Integrated Waste Complex at NDMC Plant Site, Sukhdev Vihar,Okhla  

Name of the agency: New Delhi Municipal Council. (M/s Timarpur-Okhla Waste Management Company Private Ltd).  
Particulars of the project: 

Setting up of integrated municipal waste complex at NDMC Plant Site.  Sukhdev Vihar, Okhla.  The capacity of the project would be 950 TPD beside 150 TPD green garbage.  The treatment / processing of the MSW would be based on DST-TIFAC technology of mixed MW to RDF/ Fluff preparation and bio gas generation from                         the organic waste.  The power generation would be 10MW. Cost of project is                                 Rs. 1742.62 million.  

Status of Consent: 

· Consent to establish under Air and Water Act has been issued on 03.07.07 and valid upto 09.05.08.

· Requested for extension of consent to establish for two year along with consent fee of Rs. 5200/- vide letter dated 01.07.08 after expiry of the consent.  No formal application submitted for extension of consent to establish under Air and Water Act.  

· The unit has submitted another letter on 17.07.08 with a request that the application was submitted earlier for extension of the consent to establish after the lapse of due date (i.e. expiry of consent to establish on 09.05.08), it is understood that a fine of Rs.2600/- is payable.  They have requested that this additional amount may be adjusted from DD No. 357265 dated 30.06.08 for Rs.5200/- for Timarpur project vide letter dated 01.07.08 wherein only Rs.2600/- is payable to DPCC.
· Copy of Share Transfer Agreement between IL&FS Infrastructure Development Corporation Limited, Jindal Urban Infrastructure Ltd & Timapur Okhla Waste Management Company Pvt. Ltd.  is also enclosed with letter dated 17.07.08.
Status of authorization under MSW Rules: 

Authorization under MSW Rules was issued on 09.03.07 and valid upto 08.03.09.

Decision of Consent Management Committee in its meeting dated 29.07.2008:
Ask the unit for its present status and also to indicate when the unit will be fully established. 

As Consent to Establish is already granted, fee deposited by the unit for extension of Consent to Establish be refunded.

Action taken/ Status after the meeting held on 29.07.08:

· Letter issued on 18.08.08 with copy to Account Officer, DPCC for refunding the fees. The fees has been refunded by DPCC.
· A reply dated 23.08.08 received mentioning that plot area marking, Soil testing, Route survey for HT cable diversion etc. completed and  tentative completion period for the project would be 20 months.

Decision of CMC (MSW) in its meeting dated 10.10.2008:

Take up in next CMC (MSW) in November 2008. 

· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

Progress report may be asked quarterly with overall CPM and PERT chart.

Action taken/ Status after the meeting held on 05.12.08:
Letter issued on 29.12.08. Alongwith reply dated 16.01.09 unit has submitted schedule common for Okhla and Timarpur sites. Accordingly time for RDF execution at this site and power plant execution are April, 2010 and May, 2010 respectively.

Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Submit monthly reports.
Chairman
  M. S.
        Member      
Prof. S.K Gupta
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  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Integrated Municipal Solid Waste Complex at Timarpur  

Name of the agency: Municipal Corporation of Delhi (M/s Timarpur-Okhla Waste Management Company Private Ltd).  
Particulars of the project: 

Setting up of integrated municipal waste complex at Timarpur, Delhi-09.  The capacity of the project would be 600 TPD beside 100 MGD liquid waste.  The treatment / processing of the MSW would be based on DST-TIFAC technology of mixed MW to RDF/ Fluff preparation and bio gas generation from the organic waste.  The power generation would be 3.75MW. Cost of the project is    Rs. 400 million.  

Status of Consent: 
· Consent to establish under Air and Water Act has been issued on 25.09.07 and valid upto 06.07.09.

· Requested for extension of consent to establish for two year along with consent fee of Rs. 5200/- vide letter dated 01.07.08 even having valid consent to establish.
·  The unit has submitted another letter on 17.07.08 with a request that they have applied for extension of the consent to establish prior to validity of earlier consent issued i.e. consent to establish valid upto 06.07.09.  Now they have request to extend consent to establish only for one year for which fee of Rs.2600/- is required.

· They have also requested to adjust additional amount of Rs.2600/- toward the penalty charges for renewal of consent to establish for their Okhla Project as the application was submitted to DPCC after the lapse of the due date.

Status of authorization under MSW Rules: 

Authorization under MSW Rules was issued on 09.03.07 and valid upto 08.03.09.

Decision of Consent Management Committee in its meeting dated 29.07.2008:
Ask the unit for its present status and also to indicate when the unit will be fully established. 

As Consent to Establish is already granted, fee deposited by the unit for extension of Consent to Establish be refunded.

Action taken/ Status after the meeting held on 29.07.08:
· Letter issued on 18.08.08 with copy to Account Officer, DPCC for refunding the fees. The fees has been refunded by DPCC.
· A reply dated 23.08.08 received mentioning that plot area marking completed, soil testing started on 18.08.08 etc. and tentative completion period for the project would be 12 months.

Decision of CMC (MSW) in its meeting dated 10.10.2008:

Monitor the progress of the project. Take up in next CMC (MSW). 
Action taken/ Status after the meeting held on 10.10.08:

Letter issued on 27.10.2008. The unit has submitted reply on 03.11.08 & 01.11.08 and informed that:-

· They have taken over the Timarpur Plot on 8th September, 2008.

· Soil Testing has already been completed.  Accordingly specifications for civil infrastructure works have been framed up and issued to various vendors for obtaining quotes.

· The RDF Plant Process and Layout has been finalized and enquiries floated to various parties.  They are likely to finalize the party by December, 2008.
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· Supply o RDF Plant equipment is likely to start by April, 2009 and they expect to start the erection in the same month at Timarpur.

· Commissioning of the RDF Plant at Timarpur is expected to be taken up by November, 2009 and completed by December, 2009.

· They anticipate regular operation after fine tuning in January, 2010.

· While on the subject, the two RDF Plants at Okhla are targeted for Commissioning in January ‘10 and February ‘10 respectively.

· The Power Plant is likely to be ready for Synchronization by start of April ’10 and after stabilization and trial runs, they are planning to declare commercial operation by the end of May, 2010.
· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

Progress report may be asked quarterly with overall CPM and PERT chart.

Action taken/ Status after the meeting held on 05.12.08:
Letter issued on 29.12.08. Alongwith reply dated 16.01.09 unit has submitted schedule common for Okhla and Timarpur sites. Accordingly time for RDF execution at this site is Feb, 2010.

Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Submit monthly reports.
Chairman
  M. S.
        Member      
Prof. S.K Gupta
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   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Delhi Food Processing Complex (Meat) at Ghazipur, Delhi

Name & Address: Municipal Corporation of Delhi, Delhi Food Processing Complex (Meat) at Ghazipur, Delhi 

Correspondence Address: MCD Department of Veterinary Services, Room No. 56, Town Hall, Delhi-06
Status of Consent: 

Applied for consent to establish under Air & Water Acts on 02-06-2005

Activity: Slaughter House (1.75 MLD)

Status: 

Applied for consent to establish under Air & Water Act on 02-06-05 EIA report not submitted alongwith the application.  The case was earlier dealt by EIA Cell and matter was sent to Ministry of Environment & Forest, since issues related to EIA notification and Hon’ble Supreme Court Orders are also involved in this case, letter was also issued on 30-08-07 by EIA Cell regarding seeking information about the Environment clearance by MOEF however reply to the said letter has not been received so far. As directed inspection was conducted by a team comprising of DPCC officials and Dr. T.K.Joshi, Head, CEOH on 24-08-07(Copy enclosed).  During the inspection the civil construction work as well as fixation and erection of machineries was going on.  The work of construction of ETP was also going on. In the vicinity the rendering plant is also coming up and an ETP was also seen.  The inspection of the facility could not be done since no responsible person at the site.  Details of the ETP submitted with the project report mentions about Physico Chemical Treatment.  Since waste water generated from both the section (i) Slaughter House (ii) Rendering Plant has mainly organic waste which is biodegradable, therefore Physico Chemical Treatment should be avoided since as per HW Rules it will be generating Hazardous Waste.  Besides above unit should also go for better sludge handling mechanism Letter was issued followed by the reminder letter as decided by the BMW Committee & Reply along with Report on ETP/ Rapid EIA Report received. MOEF Clearance yet to be received.

Decision Taken by the Committee on 04.10.07: 

Report of the inspection team was perused by the Committee. A letter may be issued to concerned officer in M.C.D. for furnishing detailed information on the construction of E.T.P. and its likely completion date and copy of letter to be sent to Sh. Ravi Das Engineer-in-Chief in M.C.D. 

Action Taken Report
w.r.t. meeting on 04.10.07:

Letter issued. Reply not received.

Decision Taken by the Committee on  15.11.07: 

Reminder Letter to be issued.

Action Taken Report w.r.t. meeting on 15.11.07:


Reminder letter issued, Reply along with Report on ETP/ Rapid EIA Report received. MOEF Clearance yet to be received.

Decision Taken by the Committee on 15.01.08: 

MS to Speak to MOEF & Expedite EIA clearance. To be taken up in the next meeting.
Decision taken in meeting held on 28.02.2008:

Fresh inspection is to be conducted. 

Action taken/ Status after the meeting held on 28.02.08:

Proposed Slaughter House has been inspected on 26.03.08. During the visit Dr. Om Prakash (Manager) and Sh. Alok Tiwari (AE) were also present from Municipal Corporation of Delhi. The following are the observations:

1. The erection and installation of plant & machinery was in progress. As informed that the work of the Slaughter House will be completed & handed over to MCD by 20.05.08, as assured by the contractor in the court.  
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2. Work of installation of ETP for the Slaughter House was under progress and civil & mechanical work is almost completed.  

3. The effluent treatment plant consisting of Physico-chemical, Anaerobic followed by Aerobic processes. 

4. Alum, Poly-Electrolyte, NaOH, HCl, & Sodium Hypo-Chloride will be used in treatment process and dosing tanks have been provided near the reaction tanks. Hence, the sludge generated from the ETP will be in hazardous nature in view of the inspection team. 

5. In the project report, the unit has mentioned that the dewatered sludge will be collected in tractors & disposed off suitably. During inspection it was found that the unit has not taken any steps for compliance of HWM Rules.

6. A sump is constructed in the Slaughter House premises, to collect the effluent and same will be pumped through pipe lines to the ETP, located about 300m away from the Slaughter House. 

7. As informed that the treated effluent will be discharged into the open drain leading to Hindon drain, however, in the later stage it is also proposed to use the treated effluent for gardening and other greening purpose, after closing of adjacent Gazipur Municipal Solid Waste Disposal site. 

8. A rendering plant is also installed near the Slaughter House for processing of dead animal to prepare fish food etc. The rendering plant was found non operational condition; however, as informed that this rendering plant was earlier operated for around 15 days for trial run. 

9. A separate ETP is installed for this rendering plant and found filled with waste water in septic condition. ETP was not in operation. 

10.  Bio gas will be generated from the anaerobic process of ETP and same will be burned in the complex. There is no provision for utilization of biogas.  

11.  As also informed that the application for Environmental Clearance for this Slaughter House & rendering plant is under consideration by Ministry of Environment & Forest. Environmental Clearance will be submitted to DPCC after obtaining it.  

Decision of Consent Management Committee in its meeting dated 12.05.2008:

(i) Inform the unit about point no. 5. The ETP will be based on physiochemical process therefore there will be generation of hazardous waste. Unit may be asked to apply for authorization under HWM Rules. (ii) Unit to submit Environmental Clearance as soon as they obtained. 

Action taken/ Status after the meeting held on 12.05.08:

I. Letter issued on 02.06.08.  Unit has neither submitted any reply nor applied for authorization under HWM Rules. 

II. A letter dated 09.06.08 was received from MOEF asking to initiate necessary action under EPA 1986 as the construction work is in progress before the issuance of EC.  Accordingly a letter was issued to Commissioner, MCD on 04.07.08 to get resolve the matter with MOEF.
Decision of Consent Management Committee in its meeting dated 29.07.2008:
MSW Cell will inspect the slaughter house, Gazipur along with expert Dr. Anil Saroha, Asstt. Prof., Department of Chemical Engineering, IIT, Delhi who will be paid an honorarium of RS. 2500 for this work. Inspection report may be submitted on file administratively by 30th Aug, 2008. 

Action taken/ Status after the meeting held on 29.07.08:
Unit was inspected along with Dr. Anil Saroha, Asstt. Prof., Department of Chemical Engineering, IIT, Delhi and status of the unit was appraised on file and as approved, a D.O. letter was issued to Commissioner, MCD on 19.09.08 for following specific points which require immediate attention:-
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1.  Efficient method of utilization of generated bio gas.

2.  Suitable method for disposal of sludge.

3.  Adequacy report of installed E.T.P.

4.  Date of start of operation of slaughter house in its full capacity, and stabilization of     operation of E.T.P. 

MCD was requested to clarify the above points with time bound action taken report and supporting documents.  

Decision of CMC (MSW) in its meeting dated 10.10.2008:

Issue reminder to MCD to file reply within this month. To be taken up in next CMC (MSW). 

Action taken/ Status after the meeting held on 10.10.08:

· Letter issued on 03.11.2008. Further, as approved by Chief Secretary, Delhi another letter was written to Commissioner, MCD by Chairman, DPCC on 21.11.2008 wherein MCD was asked to give a credible plan to shift the abattoir to its modern location to stop the polluting the River Yamuna.  Complete reply is awaited. 

· A reply dated 28.11.08 received from Additional Commissioner, MCD.  The reply is as under:-

1. Efficient Method for utilization of generated Bio-gas:- Earlier MCD was planning to install a Screw Press Machine to de-water the dung (Paunch Waste) to make it transportable.  As the Screw Press Machine is not a complete solution, it has been decided to establish a Bio-Methaneation Plant of 70 tone capacity per day which will generate the electricity and manure and is a permanent and is a permanent solution for disposal of dung in an eco-friendly manner.  IL&FS after conducting the study has suggested that a Bio-Menthaneation Plant in an area of 0.9 acre can handle 70 tone of paunch waste, which is adequately available at Ghazipur.

2. Suitable method for disposal of sludge:- As suggested by the IL&FS, the sludge to be yielded from Slaughter House will be pumped to the Bio-Menthaneation Plant after converting it into slurry with the help of slurry pumps where as rest of the liquid waste will be pumped to the ETP.

3. Adequacy report of Installed ETP:- At Ghazipur Slaughter House, 500 Buffaloes and 4500 Sheep & Goats will be slaughtered in one shift per day.  Keeping in view the effluent to be received from the Slaughter House with this slaughtering capacity, an ETP of 1750 KLD has been established which is of over capacity and can easily treat the effluent to be generated at Ghazipur.

4. Date of start of operation of Slaughter House to its full capacity and stabilization of operation of ETP:- There are three sections at Ghazipur Slaughter House where the animals will be slaughtered i.e. Halal, Jhatka, and Buffalo Section.  The MCD has decided to make the Ghazipur Slaughter House operational in a gradual manner and accordingly it has been decided that Jhatka Section of Idgah Slaughter House will be closed down in first phase.  After inspection of Ghazipur Slaughter House, a Committee constituted by the Hon’ble Supreme Court will submit a report to the Hon’ble Supreme Court regarding the completion of the works of Ghazipur Slaughter House Project.  Thereafter, the final date of operation of Ghazipur Slaughter House will be decided.  Till then, the working at Idgah Slaughter House will remain continue.
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·   Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

In the first para of Sh. Naresh Kumar letter, date of start and date of completion may be sought by MS. As regard to sludge generation, they must indicate how it will be treated till the bio methyl plant is established. Ask the unit to file the adequacy report.  The date of start of the Gazipur slaughter house is still not clear in the letter. Please provide the estimated date of start of the project as desired by CS. Accordingly, the closure time schedule of Idgah slaughter house is to be communicated to DPCC. Water testing may be done by DPCC lab and direction for immediate setting up of ETP in view of the very large effluent discharge.
Action taken/ Status after the meeting held on 05.12.08:

Letter issued on 30.12.08. Reply is awaited.

Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Put up status in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta
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   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Slaughter House at Idgah

The brief chronological status of Idgah Slaughter House is as under: 
	Date
	Event

	27.01.1995
	Hon’ble High Court ordered to close slaughter house on or before 31.12.95 and also curtailed the no. of slaughtering animals till its closure.   

	12.11.1998
	Letter of MCD regarding modernization of Slaughter House- request for issue of NOC (C/5). No application for NOC/Consent to operate.

	19.02.1996
	Order of Hon’ble Supreme Court mentioning “In the meantime, status-quo shall be maintained” (C/12-13).

	06.04.2000
	Inspection by DPCC officials (C/14). Following are the main observations:

1. No ETP installed.

2. Solid Waste are also stating in to sewer. 

3. As per MPD-2001 slaughter house is in ‘H’ category.  However, it is operating as per status quo order of Hon’ble Supreme Court order dated 19.02.1996 and 03.02.1997.   

	03.07.2000
	Based on the above said inspection notice U/s 33 (A) of the Water Act issued to the unit (C/22).

	03.07.2000
	Directions U/s 33 (A) of the Water Act issued to the unit (C/28) for installation of STPs etc.

	18.09.2000
	Hon’ble Supreme Court allowed one year time to MCD for modernization of slaughter house in its order (C/51). The order further directed that may application from the MCD to DDA for charge of land use should be disputed of by DDA on priority and DPCC should render all advice from time to time for modernization of IDGAH slaughter house. 

	03.01.2003
	Minutes of meeting regarding modernization of Ighah slaughter house under Chairmanship of Pr. Secretary (UD) (C/74).

	06.02.2001
	Letter to MCD informed that consent to establish issued by CPCB to the Slaughter House in 1990 has no expiry date and hence is still valid.

	22.02.2001
	DO letter of Commissioner MCD for issue the NOC for modernization of Idgah Slaughter House (C/34). However, no application for NOC/Consent to operate. 

	19.04.2001
	DO letter to Commissioner MCD, informing that consent to establish issued by CPCB to the Slaughter House in 1990 has no expiry date and hence is still valid (C/35). 

	13.06.2001
	Reply of MCD mentioning that MCD will take action for installation of ETP as per final order/ directions of Hon’ble Supreme Court (C/37).  

	09.10.2002
	Letter of CPCB with copy of supreme court order and stating that supreme court allowed one year time for Modernization (C/57). 
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	21.11.2002
	Minutes of the meeting regarding change of land use measuring 2.9 hectares from residential use to extensive industries at Idgah for Slaughter House (C/69).

	03.01.2003
	Minutes of meeting regarding Modernization of the slaughter house under the chairmanship of Pr. Secretary (UD) (C/73). 

	02..06.2003
	D.O. Letter to CPCB with proposal of an indicting guidelines for the modernization of the slaughter house (C/107) and requested to give suggestion/ comments show as to enable to communicate the same to MCD for further action.  The proposed indicative guidelines are as follows:-

1. Animals to be slaughter using modern techniques.

2. Flooring of the slaughter house must be impervious so as to avoid ground water and soil contamination.

3. Automation in respect of handling animals, body parts wherever possible needs to be done.

4. Adequate washing facilities in each section need to be provided so as to keep the section neat and clean.

5. The liquid wastes arising from Slaughtering, Cleaning, floor washing etc. need to be trapped and properly cannelized and to be treated in accordance with the stipulated standards under EPA, 1986 (copy enclosed).

6. The treated water should be reused in cooling towers; wash area etc. so as to recycle water to the maximum extends possible.

7. Solid Wastes need to be treated and reused.

8. Reprocessing of the blood, carcasses, waste meat or any other bye-products to be processed outside Delhi only as all these activities fall under ‘H’ categories which are being done in the local areas at present.

9. Any other restriction/guidelines issued by the Hon’ble Supreme Court/ High Court regarding the slaughtering etc.  

	24.06.2003
	Letter from CPCB with comments/suggestions (C/108-109).  CPCB suggested that proper pollution control measures to be installed for control of Water, Air, Solid Waste, Noise and Odour Pollution. 

	22.07.2003
	D.O. Letter to Commissioner MCD with an indicating guidelines and draft guideline from CPCB (C/113).

	12.05.2003
	Public Notice for change of land use (C/180). 

	14.07.2004
	Hon’ble Supreme Court ordered directed that MCD shall construct temporary slaughter house in Gazipur within six month for today thereafter immediately, slaughtering activities as well as trade in cattle will be shifted to Gazipur.  The modern slaughter house also be completed within two year in Gazipur (C/227).
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	13.08.2004
	Letter to MCD for obtaining information about disposal of solid waste generated at slaughter house (C/223).

	26.08.2004
	Letter from MCD with information about disposal of solid waste generated at slaughter house (C/240).

	20.09.2004
	Reminder Letter to MCD for obtaining information about disposal of solid waste generated at slaughter house as information received are not in proper format (C/249).

	02.11.2004
	Letter to CPCB provided information about disposal of solid waste generated at slaughter house (C/324).

	02.02.2005
	Letter from CPCB with published guidelines for solid waste management in slaughter houses (C/337).

	01.03.2005
	The Gazette notification of India for change of land use at Ghazipur (C/367). 


No information is available in the file regarding modernization made by MCD at Idgah Slaughter House.

· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

Decision as per case of Gazipur Slaughter House.

Action taken/ Status after the meeting held on 05.12.08:
Directions issued on 15.01.09. Reply is awaited.

Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Put up status in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Compost Plant of Municipal Corporation of Delhi at Okhla

Name of the agency: Municipal Corporation of Delhi, O/o the Engineer in Chief, Town Hall, Delhi-6

Particulars of the project: 

Revival of the Compost Plant of Municipal Corporation of Delhi at Okhla, Delhi (The compost plant at Okhla is existing plant of MCD which stopped operation in 1994 and MCD now has handed over this plant to IL & FS for revival of up gradation).   

Status of Consent: 

Consent to establish has been issued on 29.01.08.
The unit has applied for consent to operate on 21.01.09. 

Status of authorization under MSW Rules: 

Applied for authorization for setting up and operation of waste processing facility on 20/11/07 (C/1 to 67).

Details of the project: 

a. Processing technology is composting through open
air aerobic window composting method.

b. Quantity of waste to be processed is 200 TPD.

c. Investment on the project is Rs.6.2 crores.

d. Quantity of waste to be disposed per day is 40 TPD.

e. Plot Area is 29000 sq m and Built up area- 4000 sq m 

f. Sanctioned Power Load – 280 KW

g. Revival period the compost plant will be start on 1 March, 2008.

h. Water consumption for domestic is 2000LPD &  for processing  is  20,000 LPD

i. Quantity of domestic waste generated is 1500 LPD and leach ate to be recycled in composition process

j. 100 KVA DG Set proposed to be installed.

k. Concession Agreement between MCD and IL & FS is placed at (C/71 to 103).

Decision taken in meeting held on 09.01.08:

· Consent to Establish granted.

· As regard the authorization under MSW Rules, the letter will be sent to the other bodies as mentioned in MSW Rules for their views/NOC and for site clearance to the concerned land owning agency and the copy of these letters will be sent to the project proponent also.
Action taken/ Status after the meeting held on 09.01.08:

· Consent to establish has been issued on 29.01.08. 

· As decided letter was also issued on 29.01.08.  

Decision taken in meeting held on 28.02.2008:

No action at present. 

Status:
Comments have been received from Town & Country planning Organisation, UD, Govt. of India. They suggested 7 modifications in the project (C/126).

Decision of Consent Management Committee in its meeting dated 12.05.2008:

Comment received from Town & Country Planning Organization, UD, Govt of India be forwarded to IL&FS and a reminder should go to others. 

Action taken/ Status after the meeting held on 12.05.08:

· Comments received from Town & Country Planning Organization, UD forwarded to IL&FS on 03.06.08 and reminder has also been issued on 03.06.08
· A reply dated 26.06.08 received from IL&FS with regard to the comments received from UD.  Accordingly this project is revival and upgradation of the existing compost plant of MCD and not a new project.  The reply is also supported by greenbelt development details and layout plan.

· No reply/comments received so far from DDA, CGWA and Air Force. 
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Decision of Consent Management Committee in its meeting dated 29.07.2008:
EE & both AEEs will ensure that the complete status report with all inputs and will be put up in the next meeting. 
Action taken/ Status after the meeting held on 29.07.08:

Reminder has also been issued to DDA, CGWA and Air Force on 14.08.08. CGWA has replied on 03.09.08 and requested for detail project report for there perusal and necessary action. Similarly,  DDA has asked for the details on 16.09.08 of the project in the case of compost plant at Tikri khurd.  ILF&S has informed on 29.09.08 that they are in touch with CGWA and DDA for the clarification and comments by DPCC and it was also informed that they have provided required information about the project for their consideration and perusal. A letter was again issued on 06.10.08 to DDA, CGWA and Air force enclosing the detail project report. 
Decision of CMC (MSW) in its meeting dated 10.10.2008:

Issue reminder to the three agencies to file reply . To be taken up in next CMC (MSW). 
Action taken/ Status after the meeting held on 10.10.08:

Letter issued on 27.10.2008.  The ILF&S has submitted reply on 21.11.08 and informed that they have followed up with the said departments and latest status of  the project is as follows:-

1.  Commanding Officer, Air Force Station Base, Palam:-  They have been informed that since there is no Defense installation in the vicinity of the  said plant, Air Force is not concerned with this subject.  The letter, with enclosures like DPR and location map etc., for comments/NOC should therefore be forwarded to the following:- 

Regional Executive Director (AAI), Operational Offices, Rangpuri, New Delhi-110037.

The letter should be marked to the Kind Attention of General Manager (Northern Region).

2.  The Vice Chairman, DDA:- The DDA vide their letter reference no. F. 1(96) 04-08/MOM/Vol.V/578 dated 06.11.08 addressed to your office have clarified that DDA is not in the picture as there is no change in land use etc.

As regards MCD, they are attaching herewith the copy of the Concession Agreement signed with MCD on dated 01.05.07 authorizing our company to Upgrade, Operate and maintain the subject plant.

3.  The Director, CGWA:-  They had met Mr. A.K. Bhatia, Supdt. Hydrogeology and H.O.D., who has informed that the matter is under active consideration and hopefully by 10th of December, 2008, they shall forward their comments to your office.

We would now request you to kindly take appropriate action in respect of S. No. 1 above and invite their comments urgently so that they can get the consent to operate well before the expiry date of 25.01.2009 of the Consent to Establish given by your office.

·  Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

SEE, EE, AEE & Trainee to inspect and report. File to be submitted administratively with action taken report by 19.01.2009.

Action taken/ Status after the meeting held on 05.12.08:
· The unit has been inspected on 13.01.09 and submitted the file of the unit administratively as per decision in CMC (MSW) meeting held on 05.12.08.

· The unit has applied for consent to operate on 21.01.09. 

Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Put up administratively on file.

Chairman
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Compost Plant at Tikri Khurd/ Khampur

Name of the agency: M/s Spiral Services, New Sabzi Mandi, Azad Pur, Delhi
Particulars of the project: 

Up-gradation of the A.P.M.C. Compost Plant at Tikri Khurd/ Khampur, G.T. Karnal Road, Delhi-40 (Existing plant inaugurated by Delhi C.M. on 17.01.02)
Status of Consent: 

· Consent to establish has been issued on 29.01.08. 

· Applied for consent to operate on 04.03.08.

Status of authorization under MSW Rules: 

Applied for authorization for setting up and operation of waste processing facility on 20/11/07 (C/1-27 and C/30-34).

Details of the project: 

a. Processing technology is composting through open air aerobic window composting method.

b. Quantity of waste to be processed is 200 TPD.

c. Investment on the project is Rs.1.6 crores.

d. Quantity of waste to be disposed per day is 30 TPD.

e. Plot Area is 24000 sq m.

f. Built up area- 1000 sq m

g. Sanctioned Power Load – 5 KV

h. Proposed to be commissioned from March, 2008 (earlier unit exist since 17.01.02).

i. Water consumption for domestic is 1440 LPD &  for processing  is  5000 LPD

j. Quantity of domestic waste generated is 1000 LPD & having 2 septic tanks and leach ate to be recycled in composition process.

k. No DG Set proposed to be installed.

l. Agreement between APMC and Spiral Services is placed at (C-/3 to 11).

Decision taken in meeting held on 09.01.08:

· IL&FS has sent the letter by Fax wherein it is mentioned that IL&FS is working with M/s. Spiral Services in managing the compost facility at Tikkri. In the same letter they have also mentioned that they would provide the following to the existing compost plant i.e. facilitate expansion of plant, purchase and supply of equipment, finance and facilitate accrual of CDM benefit, provide technical assistance in operation of plant and off take composite produced in the plant. In view of this, consent to Establish granted.

· As regard the authorization under MSW Rules, the letter will be sent to the other bodies as mentioned in MSW Rules for their views/NOC and for site clearance to the concerned land owning agency and the copy of these letters will be sent to the project proponent also.
Action taken/ Status after the meeting held on 09.01.08:

· Consent to establish has been issued on 29.01.08. 

· As decided letter was also issued on 29.01.08.  

Decision taken in meeting held on 28.02.08:

No action at present.

Status:

· Applied for consent to operate under Orange category on 04.03.08. 

· Views/ Comments/ NOC were received only from Town and Country Planning Organization, Ministry of U.D. (C/44- 45) asked before issued of authorization under MSW, Rules. Views/ Comments/ NOC are still awaited from Air Force, DDA and Central Ground Water Board.
Decision of Consent Management Committee in its meeting dated 12.05.2008:

Comment received from Town & Country Planning Organization, UD, Govt of India be forwarded to M/s Spiral Services / IL&FS and a reminder should go to other. 
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Agenda No. 4

Decision taken in CMC on 23.01.2009 with respect to                                   11 CETPs operating in Delhi.

Various CETPs societies and officials from DJB & DSIIDC have attended the meeting on 23.01.09 wherein issues related to the CETPs were discussed in detail with the representatives of societies and officials from DJB & DSIIDC in the individual cases given below in the following table:-

	S. No.
	Name of CETP
	Discussion in CMC (MSW) meeting held on 23.01.09

	1
	Jhilmil CETP
	CETP Society informed that Jhilmil Industrial Area & Friends Colony Industrial Area have around 2,000 units and are connected to conveyance system.  About 400 units are in Shahadara Industrial Area which is under re-development in MPD-2021 and they are not connected to conveyance system.  The society has not provided details of water polluting units and units not connected with the conveyance system.

	2
	GTK Road CETP
	CETP Society informed that there are around 800 units out of which around 350 units are water polluting. All units have been connected to conveyance system. The inflow to the CETP is 2-3 MLD.

	3
	Lawrence Road CETP
	DSIIDC informed that there are about 500 units in the area.  As per DJB, all units are connected with the conveyance system. DJB will inspect & inform the name & address of the unit which are not connected with CETP conveyance system.

	4
	Badli CETP
	CETP Society informed that Phase-I & II has around 325-400 units. Out of which, there are 35 water polluting units. Badli Phase-III has no conveyance system which has around 100 units.

	5
	Mayapuri CETP
	CETP Society informed that there are around 2900 units. Out of which around 100 units are water polluting.  All units have installed ETP. CETP society has informed about choking of the sewer system near Kabari Market.

	6
	Mangolpuri CETP
	CETP Society informed that there are around 800 units out of which 6 units are water polluting.  All units have been connected to conveyance system. The inflow to the CETP is 1.4 MLD.

	7
	Wazirpur CETP
	CEPT Society informed that there is around 1875 units out of which around 137 units are water polluting. However, DPCC record has already had information above 250 water polluting units. CETP Society has raised the problem of hazardous waste disposal being generated by CETP.

	8
	Nangloi CETP
	CETP Society informed that there are around 610 units and all are connected to the conveyance system. DSIDC industrial area has around 10-12 water polluting units and all are also connected to conveyance system.


	9
	SMA CETP


	CETP Society informed that there are around 438 units and are connected to the conveyance system. SSI Industrial Area is not connected so far to the conveyance system. There are around 38 water polluting units in the area.

	10
	Okhla Industrial Area  CETP
	CETP Society informed that there are around 3300 units and are connected to the conveyance system. Around 150 water polluting units are there in Okhla Industrial Area. The CETP informed that there is a domestic waste of 2 MLD coming from Tehkhand village to their CETP.

	11
	Narela CETP
	All water polluting units should be linked with conveyance system.  DSIIDC informed that there are some units which are not connected to the conveyance system.


Accordingly, following decisions were taken in the meeting.

1. Issue Show Cause Notice to CETP Societies for the rectification of deficiencies found during inspection within 15 days.
2. DSIIDC will provide the separate list of industries within 07 days, which are connected / not connected with the conveyance system w.r.t. Narela Industrial Area as this area is developed and maintained by DSIIDC.
3. Show cause notices u/s 33(A) of the Water Act 1974 will be issued to all water polluting units of the area and the units which are not connected with the conveyance system as per the list provided by DSIIDC.
4. Representative of DSIIDC informed that they have received report from IIT, Delhi. DSIIDC will take further action for taking approval from                 Secretary, Delhi w.r.t. installation of CETP in Patparganj Indl. Area on the basis of report of IIT, Delhi.

5. All CETP Societies and DSIDC will send following information within                         7 days w.r.t. CETP under there jurisdiction:-

(i) To ensure that all units of the area should be connected with the conveyance system.
(ii) To provide the list of water polluting units.

(iii) To provide list of units which have not installed ETP or are not operating the installed ETP properly.
(iv) Inform and warn all industrial units of the respective area to get their effluent/ waste water connected with the conveyance system & all water polluting units should install and operate their ETPs regularly and efficiently.
6. The representative of DJB have been asked to check the choking of conveyance system and also get checked the outlet of each individual unit to be connected with the conveyance system  in the area within one week and also submit the list of industries which are not connected to the conveyance system.

7. All water polluting units should be issued notice u/s 33(A) of the Water Act, 1974 for installation and regular & effective operation of adequate ETP and shall submit confirmation in this regard through an affidavit that unit is connected technically/ practically with the conveyance system of the area which is leading to the CETP, all effluent generated from these units should be discharged only through the said conveyance system.
8. On the problem being faced for disposal of hazardous waste generated by CETP,  CETP Society were advised to sort out the problem through disposal of hazardous waste arrangements at TSDF sites presently operating in Kanpur, Udaipur and Faridabad till the development of TSDF site in Delhi.

9. A D.O. letter is to be issued to CEO, DJB to take necessary action within 15 days,   on the following lines, expeditiously:-

(i) To remove choking of conveyance system in all the industrial areas.
(ii) To provide connection of individual units with the conveyance system of the area.
(iii) To ensure that conveyance system of industrial areas and drainage system are not be interlinked intentionally or otherwise due to choking or overflow problems in any industrial area.
(iv) To provide conveyance system in phase-III in Badli Industrial Area.
(v) To provide conveyance system in Shahdara Industrial Area having about 400 units.
(vi) To look in the matter of discharge of domestic sewerage of Tehkhand area in conveyance system of Okhla Industrial Area leading to Okhla CETP.  President CETP Society Okhla have informed that about 2 MLD domestic discharges with high BOD load is coming from Tehkhand Village without any contribution for operation and maintenance of CETP Okhla by DJB.

(vii) Regarding Choking of conveyance system near Kabari Market, Mayapuri Industrial Area.  President CETP society has informed that even they are ready to pay the charges of cleaning of conveyance system, if so required by DJB.

(viii) To provide connection with the conveyance system of units from                          SSI Industrial Area and to take action for removal of blockage in the area.
Chairman
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Udyog Vihar (Bawana) Industrial Area CETP ( 35 MLD)

Consent status of CETP

· DSIDC applied for Consent to Establish on 05.08.02.

· Consent to Establish was granted on 20.01.2004 for a period of one year.

DSIIDC has not applied for extension of consent to establish or consent to operate. 

Present status of CETP not available.   

Decision of CMC (MSW) in its meeting dated 09.01.2008 :

Member Secretary, DPCC to write a letter to GM, DSIDC to expedite the work of CETP of the area and for compliance of provisions of the Air & Water Acts.

Action Taken Report

Letter issued on 28.01.08. No reply.

Decision of CMC (MSW) in its meeting dated 28.02.2008:

Reminder letter to be issued.

Action Taken Report

 Reminder letter issued on 25.03.2008 to the GM, DSIDC to expedite the work of CETP of the area and for compliance of provisions of the Air & Water Acts. No reply received so far.

Decision of CMC (MSW) in its meeting dated 12.05.2008:

No action. 

Decision of CMC (MSW) in its meeting dated 29.07.2008:

 Ask DSIIDC to file the latest status with regard to construction of CETP. 

Action taken Report

Letter issued on 18.08.08.  DSIIDC has submitted the reply on 21.08.08 and that the necessary action for applying Consent to Establish with DPCC has been taken and soon it shall be applied.  Further, it is added that the construction of CETP, at Bawana is expected to be  completed by December, 2008.

Decision of CMC (MSW) in its meeting dated 10.10.2008:

Regular monitoring on progress of construction of CETP to be continued.

Action Taken Report

As decided by CMC, letter issued to DSIIDC on 27.10.2008.
Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

Issue reminder letter.

Action Taken Report

As decided by CMC, letter issued to DSIIDC on 24.12.2008.  DSIIDC submitted has reply                on 21.01.09 and it is informed that the construction of CETP, Bawana is at advanced stage and it is expected that it will be completed by March, 09.

Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Monitor closely every month.
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Najafgarh Road Industrial area, CETP ( 9.6 MLD)
Consent status of CETP

· DSIDC has submitted a letter dated 03.08.2007 in respect of DO letter 17.07.2007, that the EPCA has already directed not to go for further construction in view of spare capacity in other functional CETPs. As regards settling the dispute with the contractor, DSIDC looking into it as per the terms of the contract separately.

· DSIDC applied for Consent to Establish on 03-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

Report was examined by Dr. B.K Guha Committee and recommended that this area should have separate CETP, since there is no surplus capacity in the CETP in the nearby vicinity.

Decision of CMC (MSW) in its meeting dated 19.10.2007:

Member Secretary, DPCC to study Dr. BK Guha Committee report and discuss with Prof. S.K. Gupta. Committee will be taken up this matter in next meeting.

Action Taken Report

Report of Dr. BK Guha Committee dated 03.08.2007 examined.

Decision of CMC (MSW) in its meeting dated 09.01.2008 :

Member Secretary, DPCC to write a letter to GM, DSIDC to expedite the work of CETP of the area along with B.K. Guha’s Committee report. 

Action Taken Report

Letter issued on 12.02.08. No reply.

Decision of CMC (MSW) in its meeting dated 28.02.2008:

Reminder letter be issued.

Action Taken Report

 Letter issued on 24.03.2008. DSIDC has submitted the reply on 29-4-2008 and stated that  EPCA has directed that the necessity of Najafgarh Road CETP should be examined with respect to the available capacity of the CETP in the neighborhood area. It is presumed that the DPCC has accepted the report of Guha Committee regarding essentiality of the CETP at Najafgarh Road. In the Minutes, which have been forwarded, the quantity and quality of the effluent to be available at the Najafgarh Road CETP for treatment has not been identified. Since it is an essential requirement , the information on this account may kindly be forwarded for taking further action. It is also pertinent to mention that the quantity and quality mentioned by NEERI in their report have been at variance with the actual site conditions and therefore, before moving further, this information is essential.  

Decision of CMC (MSW) in its meeting dated 12.05.2008, 29.07.08 & 10.10.08:

No action.

Decision of CMC (MSW) in its meeting dated 05.12.2008:

No action.

Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Monitor closely every month.
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Naraina Industrial Area, CETP ( 21.6 MLD)

Consent status of CETP

· DSIDC applied for Consent to Establish on 02-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

·  EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and it was appraised by the representative of DSIDC that CETP is under installation and it is at final stage of construction and after commissioning of the same may be handed over to CETP Society of the area. 

Inspection of CETP on 23.07.2007 and following were  observed:

· CETP was under construction.

· Most of the units of CETP mentioned in layout plan have been completed.

· With regards to civil work most of the work have been completed except road and drainage work.

· With regard to electrical work cabling & lighting work are yet to be done. Same is under progress.

· Pipe fitting under progress in chemical dosing system, sludge thickener & DMF/ACFs.

· Electrical panel was also found under installation.

· There are so many machinery are yet to be installed and also lots of works are pending as observed at site.

· The representative of the construction agency i.e. M/s. SPML told that due to non availability of funds the work is not being done fastly.

Decision of CMC (MSW) in its meeting dated 19.10.2007:

The CETP is reported under construction for a long time. MS may write to MD (DSIDC) to complete this work by 31.12.07 and handover to CETP society by 31.12.07.

Action Taken Report

Letter issues to DSIIDC. A letter dated 08.11.2007 has been recd from COI w.r.t. status of CETPs in Delhi wherein it was stated that   the CETP at Naraina is at final stage of construction, the same will be handed over to the CETP Society after commissioning & trial run.

Decision of CMC (MSW) in its meeting dated 09.01.2008 :

A reminder letter from Member Secretary, DPCC may be issued to GM, DSIIDC

Action Taken Report

Reminder letter issued on 07.02.08. No reply.

Decision of CMC (MSW) in its meeting dated 28.02.2008:

Reminder letter be issued.

Action Taken Report

 Reminder letter issued on 24.03.2008 wherein they were directed to complete the work and hand over the CETP to CETP society. . No reply is received.

Decision of CMC (MSW) in its meeting dated 12.05.2008, 29.07.08 & 10.10.08:

No action.

Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

No action.


Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Monitor closely every month.
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Okhla Industrial Estate CETP ( 1.2 MLD)
Consent status of CETP

· DSIDC applied for Consent to Establish on 06-07-02.

· Letter issued by DPCC on 17-02-04 seeking clarification w.r.t treatment capacity.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP.

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and recommended that an independent CETP may be installed for this industrial area.

Decision of CMC (MSW) in its meeting dated 19.10.2007:

Member Secretary, DPCC to study Dr. BK Guha Committee report and discuss with Prof. S.K. Gupta. Committee will be taken up this matter in next meeting.

Action Taken Report

Report of Dr. BK Guha Committee dated 03.08.2007 examined.

Decision of CMC (MSW) in its meeting dated 09.01.2008 :

Based on B.K. Guha’s Committee report, Member Secretary, DPCC may write to EPCA for reconsideration of its decision so that necessary action can be taken w.r.t the Okhla Industrial Estate CETP. Copy of the letter may be sent to MD, DSIDC. 

Action Taken Report

Letter issued on 12.02.08.

Decision of CMC (MSW) in its meeting dated 28.02.08, 12.05.08, 29.07.08 & 10.10.08:

No action.

Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

No action.


Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:
Record of proceeding of meeting with CETP member be placed here.
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Anand Parbat  CETP ( 24 MLD)

Consent status of CETP

· DSIDC applied for Consent to Establish on 05.08.02.

· EPCA, in its meeting 10-06-06, asked DPCC to examine the necessity of the CETP. 

· Committee has been constituted under the Chairmanship of Dr. B.K Guha.

· Work of estimation of quantity and quality of effluents generated in catchment area of all CETPs awarded to Shriram Institute.

· Report submitted by Shriram Institute.

· Report was examined by Dr. B.K Guha Committee and recommended that an independent CETP may be installed for this industrial area.

Decision of CMC (MSW) in its meeting dated 19.10.2007:

Member Secretary, DPCC to study Dr. BK Guha Committee report and discuss with Prof. S.K. Gupta. Committee will be taken up this matter in next meeting.

Action Taken Report

Report of Dr. BK Guha Committee dated 03.08.2007 examined.

Decision of CMC (MSW) in its meeting dated 09.01.2008 :

Based on B.K. Guha’s Committee report, Member Secretary, DPCC may write to EPCA for reconsideration of its decision so that necessary action can be taken on the Anand Parbat CETP. Copy of the letter may be sent to MD, DSIDC. 

Action Taken Report

Letter issued on 12.02.08.

Decision of CMC (MSW) in its meeting dated 28.02.2008:

Letter approved for EPCA in a different file, be issued.

Action Taken Report

 Letter issued on 13.03.2008 from the file of EPCA report & copy placed in file. 

Decision of CMC (MSW) in its meeting dated 17.04.2008:

“There appears to be no reason to form a Society when there is no CETP in APIA. Taking this stand, we must return all the petition and applications received from CETP Society in APIA to Commissioner of Industries to windup all such Societies. The logic of such Society without CETP is totally unclear and only leads to unnecessary confusion and alleged misuse of funds of members of the Society.”
Action Taken Report

 Letter issued to the commissioner of Industries on 06.05.2008.

Decision of CMC (MSW) in its meeting dated 12.05.2008, 29.07.08 & 10.10.08:

No action.

Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

No action.


Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Record of proceeding of meeting with CETP member be placed here.
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Dr. Sen Nursing home Nallah STP  (2.2 MGD)

Consent Status 

Consent valid up to 25-02-08.  Applied for renewal of consent on 13.05.2008.

Decision taken  

Issue SCN for deficiencies observed during the inspection.
Action taken report

Plant was inspected on 04.12.06.

SCN issued on 02.01.2007 for the deficiencies observed during the inspection.

No reply has been received. 

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 19.10.2007:

Member Secretary, DPCC to inspect.

Action taken report

STP was inspected on  05.01.2007 and some deficiencies were observed during inspection.
Decision of CMC (MSW) meeting dated 09.01.2008:

Inspection done on 05.01.2007. Issue notice for rectification of deficiencies within 30 days time, failing which Bank Guarantee of Rs. 2 lakh will be imposed. 

Action taken report

SCN issued on 12.2.2008. Reply awaited.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 17.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 22.01.2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

Case to be taken up in April CMC along with the reply of the unit. 

Action Taken Report

No reply received from the unit in response to SCN issued on 12.02.2008 in pursuance of decision taken on 09.01.2008.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.20008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 11.03.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 12.05.2008:

Ask him to apply for renewal of consent under Air & Water Act and authorization under HWM Rules. 

Action Taken Report

Applied for renewal of consent under Air & Water Act on 13.05.2008. Not applied for authorization under HWM Rules.

EE, DJB has returned our letter dated 02.06.2008 in original with remarks that this office has already applied for renewal of consent under Air & Water Act. Unit has not give any reply regarding application for Authorization under HWM Rules, as sought vide letter dated 02.06.08.

 As per DPCC Analysis report, dated 03.06.2008 (sampling done on 08.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 30.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 11.07.2008 (sampling done on 12.06.2008), all parameters are within the prescribed standard.
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Dr. Sen Nursing home Nallah STP  (2.2 MGD)

Decision of CMC (MSW) meeting dated 29.07.2008:

Issue reminder letter for Authorization under HWM Rules. EE & both AEEs will ensure that the complete status report with all inputs. 

Action Taken Report

Letter issued on 20.08.2008. EE, DJB has submitted reply on 11.09.2008 along with copy of test report of sewage sludge sample from PCRI lab at BHEL, Ranipur, Haridwar and requested to waive off the STP to apply for authorization under HWM Rules as the obtained valve of Arsenic, Lead, Mercury etc do not fall within hazardous range. 

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 30.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 12.08.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 10.10.2008:

Issue letter quoting the provisions of  HWM Rules and ask  the unit to file application under HWM Rules.

Action Taken Report

As decided by CMC, letter issued on 10.11.08.  No reply received so far.

As per DPCC Analysis report, dated 13.10.08 (sampling done on 16..09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 24.11.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.

Present Consent Status 

Consent valid up to 25-02-08.  Applied for renewal of consent on 13.05.2008.

Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 16.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Delhi Gate Nallah STP, (2.2 MGD)

Consent Status 

Consent to operate issued on 15.2.2007 & valid upto 11.10.09.

Decision taken  

Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days and also to maintain the log book properly

Action taken report

Consent Issued. As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 19.10.2007:

No action. 

Action taken report

-
Decision of CMC (MSW) meeting dated 09.01.2008:

No action.
Action taken report

No action.
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 17.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 22.01.2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

No action. 

Action Taken Report

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.20008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 11.03.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 12.05.2008:

No action. 

Action Taken Report

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 08.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 30.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 11.07.2008 (sampling done on 12.06.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.07.2008:

No action. 

Action Taken Report

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 14.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 14.08.2008), all parameters are within the prescribed standard.
Contd..2..
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Delhi Gate Nallah STP, (2.2 MGD)

Decision of CMC (MSW) meeting dated 10.10.2008:

No action.

Action Taken Report

As per DPCC Analysis report, dated 13.10.08 (sampling done on 16.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11..2008 (sampling done on 24.11.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

No Action

Consent Status 

Consent to operate issued on 15.2.2007 & valid upto 11.10.09.


Action Taken Report

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 17.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

No action.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

KONDLI STP , Ph-I (10MGD)

Consent Status 

Applied for consent to operate on 19.04.06. Consent issued on 20.08.2008 & valid upto 18.04.2009.

Decision taken on 16.01.2007  

Issue SCN giving last opportunity to remove the deficiencies observed during inspection
Action taken report

SCN issued on 15-02-07. Reply received on 23-02-07. The following submissions have been made:-

· Power back up system, with flow meters, is being provided in due course of time.

· All aerators and PST are in working condition now. 

· Presently, treated effluent is being used for horticulture purpose within the premises of plant. Further reuse of treated effluent is under consideration with DDA.

· Work order has already been placed for renovation of digester and gas holders. 

· Plant has submitted required information as per consent application along with an affidavit.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 19.10.2007:

Consent to operate will be granted once the deficiencies noted in SCN are finally implemented and confirmed to DPCC.
Action taken report

Letter issued on 06.11.2007. Reply recd on 07.12.07. The following submissions have been made:-

The flow meter installed at inlet & outlet are working properly. Case of providing power backup to the flow meter is under process.

All aerators &PST are in working order.

Treated effluent is being used for horticulture within premises, DDA laid pipes to take 2.6 lac Gallon per day, proposed to supply 8 MLD to IL&FS for proposed Gazipur MSW complex. Requested for grant of consent.
Decision of CMC (MSW) meeting dated 09.01.2008:

The unit has complied with the deficiencies but not filed an affidavit. STP may be inspected and case may be put up in next CMC.
Action taken report

Inspected on 20-2-2008. The observation are as follows : 

· Flow meter at inlet and outlet of STP found installed and operational, work of providing of UPS as power backup going on.

· all aerators found functional however one aerator was found closed as standby.

· All the digesters (three) and gas holder(one) of phase-1 are under refurbishment and work to be awarded shortly as informed. 

· As reported DDA has laid their network for reuse of approximate 2.6 Gallon per Day for horticultures purposes, pump house has been installed by DDA. 

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 31.12.2007), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), except BOD (35 mg/l) other parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

Ask the unit to file an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

Letter issued on 24.03.2008. Unit has submitted reply on 29.04.08 (without affidavit) and stated that flow meters with power & back up installed at inlet and outlet are working properly, all aerators & PST are in working order, for renovation of digester & gas holders tender is under process for award the work to the lowest tenderer, DDA has laid their network for horticulture and 8 MLD will be supplied to M/s IL&FS for proposed MSW complex at Gazipur. 

Contd..2..
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KONDLI STP , Ph-I (10MGD)

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008),  parameters BOD (32 mg/l) is exceeding the prescribed standard (30 mg/l).
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 19.03.2008), STP found non operational during monitoring.
Decision of CMC (MSW) meeting dated 12.05.2008:

The unit may be asked to explain why the STP was non operational and how is the waste water getting disposed off  as observed during inspection by DPCC Laboratory on 19.03.2008, for conducting monitoring. STP to file reply by 30.06.2008. 

Action Taken Report

Applied for consent to operate on 19.04.06.

Unit has submitted reply on 02.07.08 that plant could not be operated at the time of monitoring on 19.03.2008, due to power failure. Submitted an affidavit also along with reply regarding rectification of deficiencies
As per DPCC Analysis report, dated 03.06.2008 (sampling done on 11.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 23.05.2008), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 11.07.2008 (sampling done on 24.06.2008), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 29.07.2008:

Consent to operate granted. 

Action Taken Report

Consent order issued on 20.08.2008.

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 02.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 06.08.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 10.10.2008:

No action.

Action Taken Report

As per DPCC Analysis report, dated 13.10.08 (sampling done on 04.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 07.10.2008), BOD (34 mg/l) is exceeding the prescribed standard of 30 mg/l.
Decision of CMC (MSW) meeting dated 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.

Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

Contd..3..
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KONDLI STP , Ph-I (10MGD)

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 12.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

KONDLI STP, Ph-II  (25 MGD)

Consent Status 

Applied for consent to operate on 19.04.06. Consent issued on 20.08.2008 & valid upto 18.04.2009.

Decision taken on 16.01.2007  

Issue SCN giving last opportunity to remove the deficiencies observed during inspection.
Action taken report

SCN issued on 15-02-07. Reply received on 23-02-07. The following submissions have been made:-

· Power back up system, with flow meters, is being provided in due course of time.

· All aerators are in working condition now. 

· Work order has been placed for renovation of five sludge digesters and 2 gas holders.

· Presently, treated effluent is being used for horticulture purpose within the premises of plant. Further reuse of treated effluent is under consideration with DDA.

· Work order has already been placed for renovation of digester and gas holders. 

· Plant has submitted required information as per consent application along with an affidavit.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 19.10.2007:

Consent to operate will be granted once the deficiencies noted in SCN are finally implemented and confirm to DPCC.
Action taken report

Letter issued on 06.11.2007. Reply recd on 07.12.07. The following submissions have been made:-

The flow meter installed at inlet & outlet are working properly. Case of providing power backup to the flow meter is under process. All aerators &PST are in working order. Treated effluent is being used for horticulture within premises, DDA laid pipes to take 2.6 lac Gallon per day, proposed to supply 8 MLD to IL&FS for proposed Gazipur MSW complex. Requested for grant of consent.
Decision of CMC (MSW) meeting dated 09.01.2008:

The unit has complied with the deficiencies but not filed an affidavit. STP may be inspected and case may be put up in next CMC.
Action taken report

Inspected on 20-2-2008. The observation are as follows :

Flow meter at inlet and outlet of STP found installed and operational, work of providing of UPS as power backup going on.

All aerators found functional however one aerator was under maintenance.

All the digesters (five) and gas holder(two) of phase-II are under refurbishment and work to be awarded shortly as informed

As reported DDA has laid their network for reuse of approximate 2.6 Gallon/day for horticultures purposes, pump house has been installed by DDA. 

Work of renovation of sludge drying beds was going on and will be completed within 2 months.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 31.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

Ask the unit to file an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Contd..2..
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KONDLI STP , Ph-II (10MGD)

Action Taken Report

Letter issued on 24.03.2008. Unit has submitted reply on 29.04.08 (without affidavit) and stated that flow meters with power & back up installed at inlet and outlet are working properly, all aerators & PST are in working order, for renovation of digester & gas holders tender is awarded and likely to be completed by September, 2008, DDA has laid their network for horticulture and 8 MLD will be supplied to M/s IL&FS for proposed MSW complex at Gazipur. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 19.03.2008), STP found non operational during monitoring.
Decision of CMC (MSW) meeting dated 12.05.2008:

The unit may be asked to explain why the STP was non operational and how is the waste water getting disposed off  as observed during inspection by DPCC Laboratory on 19.03.2008, for conducting monitoring. STP to file reply by 30.06.2008.

Action Taken Report

Applied for consent to operate on 19.04.06.

Unit has submitted reply on 02.07.08 that plant could not be operated at the time of                   monitoring on 19.03.2008, due to power failure. Submitted an affidavit also along with reply regarding rectification of deficiencies
As per DPCC Analysis report, dated 03.06.2008 (sampling done on 11.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 23.05.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 11.07.2008 (sampling done on 24.06.2008), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 29.07.2008:

Consent to operate granted. 

Action Taken Report

Consent order issued on 20.08.2008.

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 02.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 06.08.2008), all parameters are within the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

No action.

Present Consent Status 

Consent to operate valid upto 18.04.2009.

Action Taken Report

As per DPCC Analysis report, dated 13.10.08 (sampling done on 04.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 07.10.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

No action.

Contd..3..
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KONDLI STP , Ph-II (10MGD)

Action Taken Report

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 12.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

No action.
Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

KONDLI STP, Ph-III , (10 MGD)
Consent Status 

Consent issued on22.09.05 and valid up to 02-12-07. Applied for renewal of Consent on 16.11.2007. Consent issued on 20.08.2008 & valid upto 02.12.2010.

Decision taken  

Issue SCN to the plant with a copy to CE, DJB
Action taken report

SCN issued on 13-03-07.

Reply received on 03-04-07. The following submissions have been made:-

Power back up system, with flow meters, is being provided. 

All aerators are in working condition now. Report is being submitted month wise. 

Sludge analysis is being carried out in the lab of DJB at STP Kondli and same is being forwarded to Director (T & QC) DJB. However, a copy of report from July 06 to Feb 07 is enclosed herewith. 

Record is being maintained at Laboratory under the supervision of ACWQA Kondli plant.  

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 19.10.2007:

Consent to operate will be granted once the deficiencies noted in SCN are finally implemented and confirm to DPCC.
Action taken report

Letter issued on 06.11.2007. Reply recd on 07.12.07. The following submissions have been made:-

The flow meter installed at inlet & outlet are working properly. Case of providing power backup to the flow meter is under process.

All aerators &PST are in working order.

Treated effluent is being used for horticulture within premises, 

DDA laid pipes to take 2.6 lac Gallon per day, proposed to supply 8 MLD to IL&FS for proposed Gazipur MSW complex. Requested for grant of consent.
Decision of CMC (MSW) meeting dated 09.01.2008:

The unit has complied with the deficiencies but not filed an affidavit. STP may be inspected and case may be put up in next CMC.

Action taken report

Flow meter at inlet and outlet of STP found installed and operational, work of providing of UPS as power backup going on.

All aerators found functional, Digesters (three) and gas holder(2) of phase III found functional. 

Bio-gas generated is burnt at site. As informed, a generator is purposed to install in near future at Phase-IV STP (45 MGD) to generate electricity by bio-gas for operation of said phase-IV STP.

As informed the work of phase-IV STP will be awarded shortly and schedule time for construction is 2 years. 

DDA has laid their network for reuse of approximate 2.6 Gallon per Day for horticultures purposes and pump house has been installed by DDA. 

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 31.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), except TSS (54 mg/l) other parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

Letter to be issued to the unit for submitting an affidavit as to why the parameters are not meeting the prescribed limit and also to file an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

Letter issued on 24.03.2008. Unit has submitted reply on 29.04.08 (without affidavit) and stated that flow meters with power & back up installed at inlet and outlet are working 

Contd..2..
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KONDLI STP , Ph-III (10MGD)

properly, all aerators & PST are in working order, the digesters and gas holders are working properly, DDA has laid their network for horticulture and 8 MLD will be supplied to M/s IL&FS for proposed MSW complex at Gazipur. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 19.03.2008), STP found non operational during monitoring.
Decision of CMC (MSW) meeting dated 12.05.2008:

The unit may be asked to explain why the STP was non operational and how is the waste water getting disposed off  as observed during inspection by DPCC Laboratory on 19.03.2008, for conducting monitoring. STP to file reply by 30.06.2008. 

Action Taken Report

Applied for renewal of Consent on 16.11.2007.

Unit has submitted reply on 02.07.08 that plant could not be operated at the time of monitoring on 19.03.2008, due to power failure. Submitted an affidavit along with reply, regarding rectification of deficiencies. 
 As per DPCC Analysis report, dated 03.06.2008 (sampling done on 11.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 23.05.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 11.07.2008 (sampling done on 24.06.2008), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 29.07.2008:

Consent to operate granted. 

Action Taken Report

Consent order issued on 20.08.2008.

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 02.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 06.08.2008), all parameters are within the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

No action.

Present Consent Status 

Consent to operate valid upto 02.12.2010.

Action Taken Report

As per DPCC Analysis report, dated 13.10.08 (sampling done on 04.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 07.10.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

No action.

Contd..3..
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KONDLI STP , Ph-III (10MGD)

Action Taken Report

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 12.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:


No action.
Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Nehru Vihar, Oxidation Pond STP (13.5 MGD)

Consent Status 
Consent issued on21.09.05 and  valid up to 28.11.07. Applied for renewal of consent on 25.10.2007.

Decision taken  

-
Action taken report

· Plant was inspected on 15.11.06.

· SCN issued on 26.12.2007 as number of deficiencies were observed during the above said inspection.

· Plant has not submitted any reply. 

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 19.10.2007:

SEE  to inspect.
Action taken report

Inspected on 03.01.2008.  Applied for renewal of consent on 25.10.2007.
Decision of CMC (MSW) meeting dated 09.01.2008:

The unit was inspected on 03.01.2008 by SEE & deficiencies were noted. Issue letter to DJB that if the STP will correct the deficiencies within 30 days, application for consent for renewal will be considered accordingly.
Action taken report

Letter issued on 12-2-2008. No Reply received.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 17.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

Reminder letter to be issued to the unit for submitting an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

 Letter issued on 25.03.2008.

Unit has submitted reply on 03.04.08 (without affidavit) and submitted that approach road to the outlet point has been cleared and are being maintained properly, photographs of the site enclosed, after the de-silting of oxidation pond no. 9 the DJB has provided the bio-remediation treatment of the sewage water at the inlet channel of the oxidation pond and de-silting of the oxidation ponds is not felt necessary at this stage. However, the result of the final effluent of the outlet of the oxidation pond are within the prescribed limit and requested to grant the consent.  

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard.
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Nehru Vihar, Oxidation Pond STP (13.5 MGD)

As per DPCC Analysis report, dated 09.04.2008 (sampling done on 17.03.2008), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 12.05.2008:

The de-silting of oxidation pond should be done in a phased manner for better treatment. A time bound program is to be submitted in this regard within period of one month. 

Action Taken Report

Applied for renewal of consent on 25.10.2007.

Unit has submitted time bound program in its reply on 27.06.08 that the Pond No. 5 shall be desilted in Current financial year as soon as got allocation of the budget.

The remaining pond 10 & 2 shall be desilted in next financial year as soon as got allocation of the budget. Presently the remaining oxidation ponds have sufficient space/depth to accumulate the solid waste and desilting could be carried out  as & when required. 

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 09.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 15.05.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 11.07.2008 (sampling done on 20.06.2008), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 29.07.2008:

Inform the unit that as soon as they complete the work of de-silting, Consent to operate (renewal) will be granted. 

Action Taken Report

Letter issued on 20.08.08.  However, no response has been received so far. 

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 16.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 11.08.2008), all parameters are within the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

Ask the unit to file report regarding compliance of desilting. Consent application to be taken up  in next CMC.

Present Consent Status 
Consent issued on21.09.05 and  valid up to 28.11.07. Applied for renewal of consent on 25.10.2007.

Action Taken Report

As decided by CMC, letter issued on 10.11.08.  Executive Engineer, DJB has submitted a letter on 15.10.08 and 26.11.08 with request for the consent and informing that the tender has been invited and due on 17.10.08 for the following works and same shall be executed within given time bound programme. 

1. Desilting and cleaning of Oxidation Pond no. 2, 5 & 10 at Nehru Vihar.

2. Construction, restoration of damaged road and CC path up to outlet channel at Oxidation Pond Nehru Vihar. 

As per DPCC Analysis report, dated 13.10.08 (sampling done on 11.09.2008), all parameters are within the prescribed standard.
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Nehru Vihar, Oxidation Pond STP (13.5 MGD)

As per DPCC Analysis report, dated 10.11.2008 (sampling done on 22.10.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

No action.

Action Taken Report

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 24.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:


No action.
Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Keshopur STP (60 MGD (40+20)

Consent Status 

Consent issued on 21.09.05 & expired on 24-09-07 for 60 MGD. 

Applied for renewal of consent on 7-1-2008.

Decision taken  

-

Action taken report

· Plant inspected by DPCC officials on 5.12.2006.

· SCN issued on 02.1.2007 as number of deficiencies     were observed.

· Plant has not submitted any reply.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

· However, no consent application for the STP of 12 MGD capacity. DPCC lab reported that said STP was found abundant during sampling in Sept 2007. 

Decision of CMC (MSW) meeting dated 19.10.2007:

Ask for renewal of consent. Unit may also be asked to rectify the deficiencies as communicated vide SCN dated 2.1.07. STP may give time of one month to do so.
Action taken report

Letter issued on 07.11.2007.  Submitted application for renewal of consent by post, (ID No. 24675 dated 07.01.2007) & as decided, letter for deficiencies issued on 08.01.08. No comments about the deficiencies mentioned in the letter.

Decision of CMC (MSW) meeting dated 09.01.2008:

Letter was issued on 07.11.07 for correction of deficiencies. No reply received. If the unit does not file an affidavit within 30 days, Bank Guarantee of Rs. One Lakh under Water Act will be imposed & further action will be taken.
Action taken report
Letter issued on 7-2-2008. Reply awaited.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 01.01.2008), all parameters are within the prescribed standard for phase-I & Phase-II. Phase-III STP (12 MGD) found non operational during operational.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 23.01.2008), all parameters are within the prescribed standard for phase-I. For Phase-II, TSS964mg/l) & BOD ( 40 mg/l) are exceeding the prescribed norms. Phase-III STP (12 MGD) found non operational during operational.
Decision of CMC (MSW) meeting dated 29.02.2008:

Letter to be issued to the unit for submitting an affidavit as to why the parameters are not meeting the prescribed limit and also to file an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

Letter issued on 24.03.2008. No reply has been received from the unit. 

A letter received from National River Conservation Directorate, MOEF, Govt of India dated 25.04.2008 regarding construction and augmentation of treatment capacity (72 MGD) of STP at Keshopur under YAP-II in Delhi. DJB has submitted a DPR for treatment of sewage in order to meet standards of 20 mg/l and 30 mg/l for BOD and SS respectively.  However, there is inadequate provision for disinfection of Faecal Coliform. NRCD has requested that details of standards and specific guideline issued by DPCC to DJB with regard to improve the water quality of Yamuna may be intimated to the NRCD so that they can consider their proposal. 
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Keshopur STP (60MGD (40+20)

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard for phase-I & Phase-II. Phase-III STP (12 MGD) found non operational during operational.
As per DPCC Analysis report, dated 09.04.2008  (sampling done on 18.03.2008), all parameters are within the prescribed standard for phase-I & Phase-II. Phase-III STP (12 MGD) found non operational during operational.
Decision of CMC (MSW) meeting dated 12.05.2008:

The unit may be asked to explain why the STP Phase-III (12 MGD) was non operational and how is the waste water getting disposed off  as observed during inspection by DPCC Laboratory on 18.03.2008 for conducting monitoring. STP to file reply by 30.06.2008. 

An appropriate reply for MOEF will be drafted by SEE for this STP and put up on file for approval before issue. 

Action Taken Report

Applied for renewal of consent on 7-1-2008.

As decided by CMC, reply has been sent to MOEF on 13.06.2008.

No reply has been recd from the unit in response to our letter dated 03.06.08. 

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 23.04.2008), all parameters are within the prescribed standard for phase-I, In Phase-II BOD (38 mg/l) is exceeding the prescribed norms. Phase-III STP (12 MGD) found non operational during operational.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 28.05.2008), all parameters are within the prescribed standard for phase-I, In Phase-II BOD (34 mg/l) is exceeding the prescribed norms. Phase-III STP (12 MGD) found non operational during operational.
As per DPCC Analysis report, dated 11.07.2008 (sampling done on 18.06.2008), all parameters are within the prescribed standard. Phase-III STP (12 MGD) found non operational during operational.
Decision of CMC (MSW) meeting dated 29.07.2008:

Issue letter to direct the unit to comply with the norms and file BG of Rs. 1 Lakh. 

Action Taken Report

Letter issued on 20.08.08.  EE, DJB has submitted reply on 25.09.08 as under: 

12 MGD plant was constructed in 1958.  The work order of Demolition, design, construction, commissioning & operation/ maintenance of 12 MGD STP (Phase-III).  Rehabilitation of two existing modules of 20 MGD STP (Phase-II) and 40 MGD STP (Part-I) at Keshopur under YAP-II and the work is in progress.  

As far as parameter of BOD is concerned in the analysis report dated 03.06.08 to 04.07.08, in this regard it is to submit that parameter may change at a particular moment on account of frequent electric supply failure/ persistence of low voltage in the system during peak summer and statement of power failure at WSTP Keshopur is also enclosed herewith for you kind perusal which it self is explanatory.  

They have requested to waive off the Bank Guarantee since DJB is a Department under Delhi Govt. 
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Keshopur STP (60MGD (40+20)

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 07.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 22.08.2008), all parameters are within the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

Issue reminder letter to file Bank Guarantee within one month. To be taken up in next CMC.

Present Consent Status 

Consent expired on 24-09-07. Applied for renewal of consent on 7-1-2008.

Action Taken Report

As decided by CMC, letter issued on 10.11.08.  No reply received so far.
As per DPCC Analysis report, dated 13.10.08 (sampling done on 22.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 21.10.2008), it was found that no flow due to pumping station cleaning. 
Decision of CMC (MSW) meeting dated 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.

Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 10.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta
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   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Mehrauli  STP (5 MGD)

Consent Status 

Consent issued on 20.03.2007 & valid upto 15.12.09.

Decision taken  

Issue consent to operate subject to the following consent conditions as well as comments:

1. Install mechanical sludge dewatering system.

2. Ensure proper storage of dry sludge.                

3. Examination of the issue related to low capacity utilization and quick resolution of the problem in consultation with related agencies.                                  

Comments:-

 a. DPCC would appreciate if DJB takes steps to generate gas form the STP.                                                                                                   
b. DJB would make all efforts to reuse the treated effluents in the nearby parks and farm houses.                                              

Action taken report

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 19.10.2007:

Mehrauli STP has not replied to the consent conditions imposed on 20.3.07. STP may be asked to reply within one month positively. 

Action taken report

Letter issued on 06.11.2007. Reply received on 28.12.2007 and submitted the action taken report w.r.t. compliance of consent conditions.  
Decision of CMC (MSW) meeting dated 09.01.2008:

The matter of low intake quantity of sewage at STPs will be taken up in next CMC (MSWM) Meeting with the DJB & MCD.
Action taken report

Meeting notice issued to invites DJB and MCD Officials.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 24.01.2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

Letter to be Member (Drainage) with a copy to Sh. V. K. Jain, SE (E&M), DJB who have  attend the meeting) by Member Secretary, DPCC for seeking reasons of low intake quantity of sewage & under utilization of STP capacity.   

Action Taken Report

 Letter issued on 31.03.2008. No reply received so far.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 24.03.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 12.05.2008:

MS to issue reminder to Member (Drainage), DJB on last decision of CMC dated 29.02.2008 for seeking reasons of low intake quantity of sewage & under utilization of STP capacity.

Action Taken Report

SE, DJB has submitted reply on 07.07.08 in response to letter issued on 03.06.2008 and stated that the under utilization of mehrauli STP is due to less sewage received from the connected area. However further efforts are being made to receive more sewage in this plant.
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Mehrauli  STP (5 MGD)

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 21.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 30.05.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 11.07.2008 (sampling done on 18.06.2008), BOD-32 mg/l is exceeding the prescribed standard.
Decision of CMC (MSW) meeting dated 29.07.2008:

Issue letter to direct the unit to comply with the norms.

Action Taken Report

Letter issued on 20.08.08.  A Copy of analysis report of DJB Laboratory for the month of August, 2008 received from DJB and parameters are found meeting the norms.

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 17.07.2008),  parameters BOD (32 mg/l)are exceeding the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 27.08.2008), parameters BOD (36 mg/l)are exceeding the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

Issue reminder letter to comply with the norms.

Consent Status 

Consent valid upto 15.12.2009.

Action Taken Report

As decided by CMC,  letter issued on 27.10.08.  No reply received so far.

As per DPCC Analysis report, dated 13.10.08 (sampling done on 05.09.2008), BOD                  (33 mg/l) is exceeding the prescribe standards (30 mg/l).
As per DPCC Analysis report, dated 10.11..2008 (sampling done on 08.10.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.

Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 11.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE
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   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Yamuna Vihar Phase –I STP (10 MGD)

Consent Status 

Consent issued on 28.2.2007 & valid upto 16.11.07. Applied for renewal of consent on 25.10.2007, issued on 20.08.2008 & valid upto 16.11.2010..  
Decision taken  

Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days.
Action taken report

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 19.10.2007:

STP has not replied to consent conditions imposed on 28.02.07. STP may be asked to reply within one month positively. 

Action taken report

Letter issued on 06.11.2007. Reply received on 28.12.2007 and submitted the action taken report w.r.t. compliance of consent conditions. Applied for renewal of consent on 25.10.2007.  
Decision of CMC (MSW) meeting dated 09.01.2008:

SEE to inspect and to submit report in the next CMC (MSW) Meeting.
Action taken report

Inspected on 19-2-2008. The observation are as follows: 

All aerators found in operation. 

Ultrasonic flow meters installed at inlet and outlet of STP. As informed magnetic flow meter van not be provided being open channel discharge.

Bio-gas generated in plant is burnt at site, however as informed DJB has plant to install generators(3 nos. x 1000 KVA) for generation of electricity from bio-gas of phase-I&II and same will be installed in next two months. 

All 12 SDBs were found filled with Sludge as reported STP is facing problem w.r.t lifting of sludge/manure. 

Regarding reuse of treated effluent, an effluent pump house is under installation near the STP.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 31.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

Letter to be issued to the unit for submitting an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

 Letter issued on 25.03.2008. No reply received.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 27.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 19.03.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 12.05.2008:

No action. 
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Yamuna Vihar Phase –I STP (10 MGD)

Action Taken Report

Applied for renewal of consent on 25.10.2007.  
As per DPCC Analysis report, dated 03.06.2008 (sampling done on 09.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 29.05.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 11.07.2008 (sampling done on 24.06.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.07.2008:

Consent to operate (renewal) granted. 

Action Taken Report

Consent order issued on 20.08.2008.

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 02.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 04.08.2008), all parameters are within the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

No action.

Action Taken Report

As per DPCC Analysis report, dated 13.10.08 (sampling done on 05.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 24.10.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.12.2008 (sampling done on 11.11.2008), no flow was found during the monitoring.
Decision of CMC (MSW) meeting dated 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.

Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 12.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta
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   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Yamuna Vihar Phase –II STP  (10 MGD)

Consent Status 

Consent issued on 28.2.2007 & valid upto 28.12.09.

Decision taken  

Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days.
Action taken report

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), plant is not meeting the prescribed standard.

Decision of CMC (MSW) meeting dated 19.10.2007:

The unit has not replied to consent conditions imposed on 28.2.07. The unit is also not meeting with the prescribed standards. SCN may be issued u/s 33 A of Water Act for remedial action within one month. 

Action taken report

Letter issued on 07.11.2007. Reply received on 28.12.2007 and submitted the action taken report w.r.t. compliance of consent conditions.  
Decision of CMC (MSW) meeting dated 09.01.2008:

SEE to inspect and to submit report in the next CMC (MSW) Meeting.
Action taken report

Inspected on 19-2-2008. The observation are as follows : 

Ultrasonic flow meters installed at inlet and outlet of STP, commissioning is expected within a week. 

All aerators found operational. 

A new fine screen installed after primary screen section. 

Bio-gas generated in plant is burnt at site, however as informed DJB has plant to install generators(3 nos. x 1000 KVA) for generation of electricity from bio-gas of phase-I&II and same will be installed in next two months. 

SDBs were found filled with Sludge as reported STP is facing problem w.r.t lifting of sludge/manure. 

Regarding reuse of treated effluent, an effluent pump house is under installation near the STP.

Acoustic enclosures installed with the DG sets of 7.5 KVA and 160 KVA.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 31.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

Letter to be issued to the unit for submitting an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

Letter issued on 24.03.2008. No reply received so far. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 27.02.2008), parameters BOD (34 mg/l) is exceeding the prescribed standard (30 mg/l).
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 19.03.2008), parameters BOD (33 mg/l) is exceeding the prescribed standard (30 mg/l).
Decision of CMC (MSW) meeting dated 12.05.2008:

Ask the unit to file explanation why BOD is exceeding the standard in the month of March & April, 2008 by 30.06.2008. Call on July, 2008.

Action Taken Report

No reply received in response to letter issued on 03.06.2008.

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 09.04.2008), BOD (33 mg/l) is exceeding the prescribed standard .
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 29.05.2008), BOD (34 mg/l) is exceeding the prescribed standard .
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Yamuna Vihar Phase –II STP (10 MGD)

As per DPCC Analysis report, dated 11.07.2008 (sampling done on 24.06.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.07.2008:

Issue reminder for compliance of norms and ask the unit to submit Bank Guarantee of Rs. 1 Lakh. 

Action Taken Report

Letter issued on 20.08.2008. EE, DJB has submitted the reply on 27.08.2008 and stated that the testing of various parameters are being conducted at DJB laboratory and the results of April, May, June, July & August 2008 are meeting the prescribed standards (the average BOD are 15, 11, 12, 15 mg/l) and requested to waive off the Bank Guarantee. 

 As per DPCC Analysis report, dated 12.08.2008 (sampling done on 02.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 04.08.2008), all parameters are within the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

Wait for Sept. & October 2008 report. To be taken up in next CMC.

Action Taken Report

As per DPCC Analysis report, dated 13.10.08 (sampling done on 05.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 24.10.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.12.2008 (sampling done on 11.11.2008), parameter        TSS (56 mg/l)  was found  exceeding the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.

Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  EE, DJB has submitted reply on 21.01.09 and submitted that the sample of STP Ph-II was collected jointly with DPCC on 11.11.08 & the same was also analyzed is our DJB laboratory.  The results found are meeting within the prescribed standards, which is 27 mg/l in respect of TSS.  Testing of various parameters are being conducted at our Delhi Jal Board laboratory on regular basis.  The reports for the BOD & TSS contents in the final effluent for the moth of Nov, Dec, 2008 & Jan, 2009 (up to 16.01.09) and copies enclosed.  The daily results achieved are meeting within the prescribed standards.  The average TSS contents are           29 mg/l, 25 mg/l, 21 mg/l & average BOD contents are 19 mg/l, 16 mg/l, 15 mg/l for the moth of Nov, Dec, 2008 & Jan, 2009 (up to 16.01.09) respectively.  

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 12.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta
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   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Rithala STP– Ph-I, (40 MGD)

Consent Status 

Previous Consent valid upto 04.05.06. Applied on 29.06.2006 for renewal of consent.
Decision taken  

Issue SCN giving last opportunity to remove deficiencies observed during inspection.

Action taken report

SCN issued on 15.02.07.Reply received on 09.03.2007 & following submissions have been made:-
Necessary action initiated for rectification of flow meter. Repair of 3 aerators is underway.
Secondary settling tanks have been operational after rectification. Gas holders are under repair. 5 MGD of treated effluent is being given to DDA for horticulture purpose. In addition to some quantity being lifted by DDA through tankers. Gas collection improved. 1200 m3 gas is being generated per day and sent to Phase – II for power generation.
As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 19.10.2007:

Unit was given last opportunity to correct deficiencies. A reply received on 9.3.07 indicates that some remedial action has been taken. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 

Action taken report

Letter issued on 07.11.2007. Reply received on 26.12.2007 and submitted affidavit to confirm correction of deficiencies. Further requested for exemption of Bank Guarantee as all defects/ deficiencies attended.  
Decision of CMC (MSW) meeting dated 09.01.2008:

MS, DPCC  to inspect  and submit the report in next CMC (MSW) Meeting.
Action taken report

   Inspected on 21-2-2008. The observation are as follows :

Ultrasonic flow meters found operational. 

18 Aerators (out of 24) found operational, as informed aerators are operated on rotational basis as per requirement. 

Gas generated in phase-I is transferred to phase-II for operation of generators. 

One sludge digester found under maintenance. 

Approximate 1200 cubic meter gas is generated per day. 

Average intake effluent intake in jan,’2008 was 17.1 MGD.

One gas holder found not in use and as informed it is to be reconstructed /refurnished. Treated effluent (5MGD) is used by DDA for horticulture. It is purposed that 25 MGD treated effluents will be supplied to Proposed Pragati Power Projects, Bawana and 2 MGD to NDPL.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007) except TSS (62 mg/l), other parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 29.01.2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

Letter to the Member (Drainage) for seeking reasons of low intake quantity of sewage & under utilization of STP capacity. Letter to be issued to the unit for submitting an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

 Letters issued on 26.03.2008. 

Reply received on 31.03.2008 stating that DJB has rectified all its deficiencies. DJB has requested that exemption may be granted to submit Bank Guarantee as DJB is running the STP for public service purpose and have no profit motive unlike other private installation where these norms are generally applicable.  DJB has already submitted an affidavit regarding rectification of deficiencies. 
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Rithala STP– Ph-I, (40 MGD)

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 28.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 17.03.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 12.05.2008:

No action. 

Action Taken Report

Applied on 29.06.2006 for renewal of consent.
Unit has submitted copy of earlier submitted affidavit regarding rectification of deficiencies and requested for renewal of consent.

Unit has submitted another letter on 15.07.08 & informed that the deficiencies pointed have been completely rectified and affidavit to this effect has already been furnished.

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 15.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 STP was found non operational during visit on 16.05.2008. 

As per DPCC Analysis report, dated 11.07.2008 (sampling done on 09.06.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.07.2008:

Put up in next CMC in Sep, 2008.

Action Taken Report

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 16.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 18.08.2008), all parameters are within the prescribed standard
A D. O. letter issued to VC, DDA on 23.09.2008 to explore the possibility of reuse of treated water of Rithala STP for the Japanese Park at Rohini.

EE, DJB has submitted a letter on 11.09.2008, informing that in order to sort out the problem of sludge disposal, a remedy has been sought by installing new Thermal Oxidation Plant at Rithala using Thermylis technology in which the dry sludge will be generated into another inert material by thermal oxidation process. This process will be carried out in furnace and will help in 87% reduction (by weight). This process will also produce electric power by cogeneration using waste heat from plant. There will be almost Zero air pollution and the exhaust flue gases from thermal oxidation plant shall meet the local air pollution norms. There are provisions already made in this plant design for air 

pollution control system using venture scrubber. Requested for prescribed norms/ guidelines in this regard so that same could be followed before allowing the executive agency to start the construction of the above plant.

Decision of CMC (MSW) meeting dated 10.10.2008:

Member Secretary, DPCC may issue reminder to Member Engineer, DDA for our earlier letter dated 23.09.2008. To be taken up in next CMC.

Consent Status 

Applied for renewal of consent on 29.06.2006.
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REUTILISATION OF TREATED EFFLUENT OF CETPs

Confederation of Delhi Industries and CETP Societies submitted has representation appreciating the gesture of DPCC and the Principle Secretary, UD, Govt. of Delhi regarding the re-use of treated water emanating from CETPs in Delhi.  Confederation  give their opinion for the possible area the re-use as under:- 

1. Watering of non-agriculture/ non consumable species of trees, shrubs planted on the road side by MCD, PWD and also the ridge areas monitored by Delhi Government.

2. Civil Construction work (mostly undertaken by MCD/DDA).

3. Road construction work (undertaken by MCD/PWD).

Pr. Secretary, (UD) had taken a meeting on this issue on 09.01.2008 with DSIDC as well as user agencies namely MCD, DDA, I&FCD, Delhi Fire Service.  DPCC was not called for the said meeting. 

As decided letter along with copy of analysis reports of all CETPs for three months were issued on 05.06.08 to the user agencies for to submitted that the demand for utilization of treated effluent from CETPs w.r.t. the following points:-

(i) Purpose of use – like maintaining the parks, fire fighting.

(ii) Quantity that can be utilized from nearby CETPs.

(iii) Time frame of utilization.

DSIIDC was also ask to give comments regarding suitability for use of treated effluent both in terms of quantity and quality and also for seeking minutes of meeting taken by Pr. Secretary, (UD) on 09.01.08.

No response has been received so far from the user agencies and DSIDC.

Decision of CMC (MSW) taken in its meeting dated 29.07.2008:

Issue reminder to all these agencies regarding use of the treated effluent. 

ACTION TAKEN REPORT

Reminder letters were issued on 25.08.2008 to all the agencies. Response received in this regard is compiled in a tabular form and enclosed as “Annexure-I” 

A representation has been received 21.08.2008 from Shri Ravi Meattle, 26, Prithvi Raj Road, New Delhi regarding use of treated water from CETPs in Delhi and suggested as under :-

In Australia, Singapore and other water scarce countries, the water is treated and recycled for use, you cannot construct using water ground water, but in Delhi, ground water is used and the treated water is dumped back in the polluted river, thus treatment of water becomes redundant.
The authorities or the societies running the plant should construct overhead storage tanks and separate pipelines laid in these areas so that this water is used for washing, cleaning, construction, irrigation and toilets.  The water can be colored blue to differentiate like done in kerosene.  All the Industries should be made to use this water.  This can save a huge quantity of potable water, which could be utilized solely for drinking purposes.
In this way we can save 191.4 million liters/day, which is phenomenal but wasted.  With the Commonwealth Games coming up enormous of Construction will be required, the need of water will be substantial.  Instead of using ground water, is should be made mandatory to use recycled water.
Contd..2..
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Even the recycled water from the discharging units could be recycled again and again thus optimizing and fully utilizing our scarce resources.

The authorities should charge for this water and give incentives to the public to utilize this water at a concessional tariff.  With this procedure, we will save water, which authorities supply for drinking, which is mis-utilised now. Government authorities will also earn revenues.  

Decision of CMC(MSW) taken in its meeting dated 10.10.2008:

Issue appropriate reminder to all the societies and agencies except Okhla CETP Society for reutilization of treated effluent of CETPs. 

ACTION TAKEN REPORT

As decided by CMC, reminder letters were issued to all CETP Societies & other agencies on 10.11.2008. Reply has been received from DSIIDC only & they have states that DPCC may consider the recommendations of Guha Committee. As such DSIIDC have no data in this respect and not in position to offer any comments on this issue for 9 CETPs. Further, as per Guha committee report probable use of treated effluent from CETP Lawrence Road & Narela given  in the report are as follows depending upon the quality of treated effluent

a). Use in acid pickling unit for the 1st & 2nd stage rinse wash of metal sheets.

b). Use in service station for car wash.

c). Use for land irrigation in parks and gardens in nearby area for horticulture.

d). Use in thermal power plants for process water (boiler fed water after further treatment) and for cooling/ condenser water. 
Decision of CMC (MSW) its meeting dated 05.12.2008:

The matter be included in the Cabinet Note.

Action Taken Report

As decided by CMC (MSW) draft Cabinet Note has been submitted administratively on file. 
Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta
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EE
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   DPCC
  DPCC      Env. Deptt.

Member (Acd. Inst)      
(MSW) 
MSWM Cell

Agenda No. 8

Study of CETPs in Delhi

Decision of CMC (MSW) taken in its meeting on 12.05.2008:

Dr. A. K. Neema, IIT may kindly be requested to file his report on CETPs by 30.06.2008 positively. Dr. Neema may be asked to inspect those CETPs also which were stopped by EPCA orders so that latest update is received on each of these CETPs. For this additional work one month additional time is granted to file supplementary report. 

Action Taken Report

As decided letter issued to Dr. Nema. Dr. Nema has submitted draft report on 09.07.2008 and has been put-up in concerned file. 
Decision of CMC (MSW) taken in its meeting on 29.07.2008:

Matter is already under process in the concerned file.

Action Taken Report

As decided letter was issued to Dr. Neema on 25.08.08 requesting to give complete/ final report covering all points of scope of work as specified in the work order and also inspect the CETPs.  However, no report is received in this regard so far. 
Copy of the report submitted by Sh. Ram regarding “Assessment of Quantity and Quality of effluent generated in catchment area of CETPs meant for 21 industrial areas in NCT of Delhi” including revised report of Lawarance Road Industrial Area were also send to                 Dr. Neema on 01.09.08 so that the input of this report may be shared in the study conducted by him.  

Decision of CMC (MSW) taken in its meeting dated 10.10.2008:

MS to talk to Dr A. K. Neema to sort out the matter. 

ACTION TAKEN REPORT
The report “Technical evaluation of the design, utilization and conveyance system of CETPs” has been received form Dr. Neema,  I.I.T. on 25.11.08.  As discussed, report is being examined and will be put up on file administratively. 

Decision of CMC (MSW) taken in its meeting dated 05.12.2008:

File be submitted administratively.

Action Taken Report

As decided by CMC (MSW), matter submitted on file and as decided on file, the report may be put up in CMC (MSW) meeting to be held on 23.01.09.
The report on technical evaluation of the design, utilization & conveyance system of CETPs is resubmitted by Prof. A.K. Neema, IIT Delhi. The report is still lacking w.r.t. scope of work of the project. Therefore, Prof. Neema may be again conveyed to complete the scope of work of the project. The report as silent observation on each CETP separately which may be  communicated to the concerned CETP for  improvement.  The 
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Study of CETPs in Delhi

report cover the 11 operational CETPs and still lacking with the study to be conducted in the rest CETP under construction. The comparison of the scope of work and the report is as under: 

	S.No.
	Issue as per the scope of work order 
	Whether incorporated in the report

	a.
	Study whether 11 CETPs have been over-designed and the present capacity utilization of each CETP.
	Present capacity utilization of all 11 operational CETPs incorporated & study  regarding Okhla & Mayapuri CETPs is given.

	b.
	Ways and means for full utilization of unutilized capacity of CETPs, through the effluent waste of the industrial areas where there is no CETP.
	Incorporated under point 6.1 of the report and given two options regarding full utilization of capacity of CETPs.

	c.
	Study of conveyance system of industrial areas leading to CETPs and to suggest the addition/alteration in the conveyance system so that all effluent generated from the industrial areas is connected to the conveyance system.
	Not covered.

	d.
	Study how to generate energy efficiency and earn carbon credits.
	Not covered.

	e.
	Study the payment of Cess under Water  (Prevention and Control of Pollution) Cess Act, 1977 from the members of concerned CETP Society.
	Not covered.

	f.
	Study the relationship between CETP Society and other Industrial Associations of the concerned Industrial Area.
	Incorporated under point 6.3 & 7 of the report.

	g.
	Study whether CETPs can be run by professionals for improving their performance and making them effective.
	Incorporated under point 5 of the report.

	h.
	Study the feasibility of reuse of treated water from all 10 CETPs.
	Incorporated under point 6.2 of the report. 

	i.
	The amendments if any required in the CETP Act, 2000, for better management and control, on the operation of CETPs.
	Not covered.


The key observations of the study w.r.t. all 11 CETPs are covered in chapter 5 at page 43-46 of the report. The report also stress the need for full utilization of the capacity of the CETPs  in the chapter 6 at page 47 by adding more effluent  from nearby industrial areas where the CETP are not available presently. However, there is need to check the
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Study of CETPs in Delhi

compatibility with the existing treatment process at the CETPs and availability of capacity in terms of waste water quantity as well as amount of sludge likely to be generated. The report also emphasizes the reuse of treated effluent from the CETPs with a tertiary treatment device like membrane filtration with all operational CETPs. 


The major recommendations have been given in chapter 7 at page 50 of the report which is reproduced as below:

I. The CETPs are facing problems in operation and maintenance. Most of the problems are due to the (i) poor input quality from the member industries and other sources, (ii) proper operation and maintenance, and (iii) the deviation of input wastewater quantity and characteristics from the design values.

II. CETPs operating agencies should carry out performance review and process optimization for improved operation and maintenance of CETP. Examples of similar exercise are Mayapuri and Okhla Industrial Area CETPs.

III. Optimization of neutralizing/coagulating chemicals is very important for deriving maximum benefits from primary treatment units based on physico-chemical treatment, minimizing sludge production and reducing pollutants’ load on subsequent treatment units. Jar tests should be conducted on daily basis to decide type of coagulant and their dozing.

IV. High TDS in the raw influent reaching CETPs and, as a result, in treated effluent of CETPs is a major cause of concern. Attempt should be made for reduction in release of TDS contributing chemicals from problem industries by adopting cleaner production technologies and recovery and recycling of chemicals from the waste streams.


V. At the CETP Lawrence road a suitable biological treatment unit shall be planned to reduce the BOD load.

VI. At CETP Narela, the operation of treatment units based on biological treatment (Activated Sludge Process) is sensitive and requires understanding of important controlling parameters. Use of Solid Retention Time (SRT), the ratio of solids in the system and solids wasted per day, as controlling parameter is recommended because it is most simple and treatment efficiency, sludge production, oxygen requirements and nutrients requirements are dependent on SRT.
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Study of CETPs in Delhi
VII. Sludge management (including disposal) is an essential part of CETP projects, which should have been addressed along with the CETP design. In the absence to secured landfill site(s), all the CETPs are storing the sludge within their premises. Apart from the severe space constraints there exist a risk of exposure to the CETP personnel and neighboring population through various pathways. A permanent solution through suitable treatment and management options shall be examined.

VIII. It should be mandatory for the member units to reveal the information regarding the types of raw materials, its quantity, by-products, production process and the final product. Any industry using hazardous chemicals should be asked to minimize the use and take corrective measures to finally phase out such chemicals. These should not be diluted in the larger volumes to aggravate the problem.

IX. The member industries should be encouraged reduce hydraulic and pollutant loads in discharges to the CETPs, facilitate CETPs’ operation, and help improve CETPs’ compliance with environmental requirements. Recycling/reusing of effluents from CETPs to member industries shall be evaluated through pilot-scale testing and compared with the originally-conceived scheme of discharging to the surface water. If the studies show that the recycling/reuse option is feasible and more cost-effective than the originally conceived options, then hydraulic and pollutant loads in CETPs’ effluents will be curtailed or eliminated.

X. Reusing the treated water from the CETPs for the industrial uses in the same industrial estate which is responsible for its generation. This will help in improvement of the performance of CETPs and result is significant load reduction on the environmental resources.

Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

File be submitted administratively.

Chairman
  M. S.
        Member      
Prof. S.K Gupta
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  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Agenda No. 9

Inviting proposal for establishment of Common Effluent Treatment Plants
A letter dated 15.04.2008 has been received from the Joint Secretary, Ministry of Env. & Forest, Govt. of India inviting proposal for establishment of Common Effluent Treatment Plants along with necessary documents after coordinating with State Environment Department, so that proposal  may be considered for senction of Central subsidy during the financial year 2008-09, for which funds have been provided. 

A letter dated 16.08.2007 on the same matter has also been received from MoEF (copy enclosed). As decided, reply was sent to the Jt. Secretary, MoEF on 11.10.07  (copy enclosed) informing that out of 15 proposed CETPs, at present 10 CETPs are in operation in different industrial areas of Delhi. DSIIDC was the agency for construction of all the 10 CETPS installed so far. Industries Department, Govt of Delhi is the nodel agency for the implementation of CETP Act. Hence DSIIDC may be asked to submit the proposal of setting up of CETP as per the scheme of the MoEF, Govt. of India. 

Decision of CMC (MSW) taken in its meeting on 12.05.2008:

There are 10 industrial areas which are still do not have CETP. The letter can also be forwarded to the DSIDC for writing to MOEF. Accordingly draft to JS, MOEF may be put up. 

Action Taken Report

As decided, letter issued to Joint Secretary, MOEF, Govt of India & MD, DSIIDC. 

Decision of CMC (MSW) taken in its meeting on 29.07.2008:

Follow up with DSIDC and Industries department.

Action Taken Report

Letters were issued to Commissioner Industries, MD DSIIDC on 25.08.08.  Reply dated 07.10.08 received from DSIIDC informing that the matter is being examined by DSIIDC for the various parameters which are required for having a feasibility report on the subject.  We will inform you soon in this regard.

The matter was discussed by the Member Secretary, DPCC with the Commissioner (Industries) on 29.07.08 and he has told that he shall take up the matter.  However, no further reply has been received so far.   
Decision of CMC (MSW)taken in its meeting dated 10.10.2008:

MS to issue reminder letter to MD, DSIIDC.

ACTION TAKEN REPORT

Letter issued to MD & DSIIDC on 31.10.08.  Chief Engineer (E), DSIIDC has submitted the reply dated 21.11.08 and stated that for the preparation of the proposal for establishment of CETPs following inputs are required.

1. Names of the industrial area where CETPs are to be established.

2. List of the industries situated in each of the industrial area and the product being manufactured by them.

3. Quantum & Quality of effluent of each of the industrial estate.

4. The drainage map & the lay out maps of industrial areas.
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DSIIDC has further requested that Rs.1.00 Crore may also please be allocated to DSIIDC initially so that the process of engagement of consultant could be initiated by this department for the preparation of proposal for establishment of CETPs.  The expenditure on above proposal shall be informed once the consultant is engaged. 

Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

Letter may be sent to DSIIDC & Industries Department.

Action Taken Report

As decided by CMC (MSW), letters issued to DSIIDC & Industries Department on 14.01.2009. 

Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Reminder letters be sent to DSIIDC & Industries Department.

Chairman
  M. S.
        Member      
Prof. S.K Gupta
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   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Agenda No. 10 

Compliance of EPCA & CPCB directions 

A letter dated 17.10.08 has been received from EPCA from 23.10.08 regarding sending of periodical monitoring reports of CETPs to Commissioner Industries and EPCA.  Chairman EPCA has requested that the following actions are ensured by DPCC:-

1. To continue periodic and proactive monitoring of the performance of CETPs and work with the CETP Societies to ensure compliance with inlet and effluent discharge standards.

2. To initiate immediate action against industries that are continuously and grossly violating CETP inlet standards especially against the acidic effluent discharging industries connected to Wazirpur CETP.

3. To identify the industries not connected to conveyance systems leading to the CETPs and take appropriate action in a time bound manner, and to point out the deficiencies in the conveyance system, if any to the Delhi Jal Board to rectify the defects expeditiously so that all waste water generated in industrial areas shall be conveyed and treated in the respective CETPs.

4. To submit status report on development of the Treatment, Storage and/or Disposal Facility (TSDF) site for hazardous waste.

Regarding Point No. 1. DPCC is already doing monthly monitoring and quarterly inspection of all the operational CETPs and accordingly action is taken against the defaulting CETP after examine the individual case in the Consent Management Committee (MSWM).

As regard Point No. 2, 3 & 4, the matter pertains to Consent Management Cell and as decided a separate note with copy of the EPCA letter has been send to CMC on 31.10.08 for taking necessary action.
 A letter dated 17.11.08 received from CPCB in response to the letter issued by DPCC on 31.11.08 regarding compliance of CPCB direction u/s 18 (1)(b) of the Water, Act 1974 dated 02.09.08.  Now, CPCB has asked to take necessary action regarding the areas of concern demanding immediate action include ensuring connection of entire effluent from industrial area to the respective CETP ensuring compliance of inlet quality standards by member industries and creation of facility for safe disposal of hazardous. CPCB further asked to ensure the compliance of directions of EPCA dated 17.11.08 
Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

Member Secretary, DPCC direct all CMCs and Enquiry Counter for compliance of directions of EPCA dated 17.10.2008 and CPCB directions u/s 18(1) (b) of Water Act dated 02.09.08. Accordingly, reply be sent to CPCB and EPCA. 
Action Taken Report

As decided by CMC (MSW), MS, DPCC has issued direction note on 26.12.2008 to EEs of Consent Management Cell and Enquiry Counter for compliance of directions. Reminder was also issued on 07.01.2009 for seeking action taken report so that reply will be sent to CPCB & EPCA accordingly. The consent application of individual units which contains the information as to whether the said unit is discharging its effluent in “drain/ public sewer/ open land etc., are being dealt by Consent Management Cell  
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Part reply has been received from EEs (CMC) on 20 & 22.01.09 that CMC officials are not inspecting any of the area(s) since long and so doesn’t have any data w,r,t. connection of individual industries to conveyance system leading to CETP. Only SIT is carrying out the inspections. No information has been provided with regard to point no 2 & 3 of the CPCB directions and also as mentioned in the note issued by MS, DPCC, as decided in the meeting of CMC (MSW).  
Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

The issue with regard to CPCB direction dated 02.09.08 u/s 18(1) (b) of Water Act regarding not to permit expansion/establishment of the industries in the area where the associated CETPs are not complying with the required standards and where such CETPs do not have adequate hydraulic capacities be discussed in CMC orange on 28.01.09.Accordingly a reply to be sent to the CPCB.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE
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   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Agenda No. 11
An article entitled, “Chemical laboratories releasing abundant chemicals into the Sewers”.

Ms. Kusum Lata Bharadwaj, 8/168, Arya Nagar, Kanpur has submitted an article on the above matter and the brief is as under:- 

The chemical laboratories of Intermediate Degree and Post Graduate Colleges, Universities and Research Institutes are regularly discharging chemicals into their drains which are connected with the sewer line.  The chemicals are used by the students during qualitative systematic analysis, volumetric analysis and research work etc.  The above mentioned chemicals and others will undoubtedly, also flow into the sewage of the septic tanks and other tanks used for sewage treatment.   

The end products of sewage treatment are sludge and clean water.  These are free from disease causing organisms, but unfortunately, the chemicals released from the chemical laboratories will also certainly be present in them.  Sludge and clean-water are, thus, poisonous. 

Application of Sludge and clean –water to fields under cultivation will contaminate the soils by numerous chemicals.  In order to overcome these difficulties steps of prevention be taken.  

· All Institutional heads should be asked, by the Government, not to discharge their chemicals into the drains connected with the Sewer line. 

· The use of soaps, detergents and VIM powder for bathing, cleaning and washing; use of acids for cleaning the toilets; use of phenols for disinfecting the toilets, and use of dettol and other disinfecting and cleaning reagents, can, however, not be brought to an end.  They will persist in the Sludge and clean-water which will, still, not be fit to be used for Agricultural purposes.

· The clean water (STP treated Water) can be evaporated and the sludge be used for generating Bio-gas.  After generating Bio-gas the remnant sludge can be dried and burned.  The ashes can be submerged in the rivers. 

As per the article the most vital actions which have to be taken are:-

1. Chemical laboratories should have their own treatment plants to collect chemicals released by them.

2. The sludge contaminated by chemicals or domestic toxic reagents should, also, not be added to fields under cultivation.  Such sludge will be fatal for the plants.

3. Sludge, free from chemicals, should be used for generating Bio-gas.  The remnant sludge, after production of Bio-gas, should be dried and burned and the ashes be submerged in rivers.

Decision of Consent Management Committee (MSW) its meeting dated 05.12.08:

The list of all relevant chemical laboratories may be prepared within 15 days and letter be issued to them for submitting the effluent analysis report at outlet of the premises within next 15 days. The matter be discussed in next CMC(MSW) on 19.01.2009. Based on the decision taken today, CM office may be informed accordingly. Ms. Kusum Lata Bhardwaj, Kanpur may be invited to next CMC (MSW) and DPCC will give her to and fro train fare, Rs. 2000 for per sitting in the meetings of CMC (MSW) and for stay at Gymkhana Club.

Action Taken Report

As decided by CMC (MSW), letters issued to 27 laboratories on 05.01.2009 for seeking the effluent analysis report at outlet of the premises within next 15 days (list enclosed). C.M. office has also been appraised in this regard.
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Reply has been received from 2 laboratories. M/s FICCI Research & Analysis Centre, Dwarka has stated that the analysis time taken by the DPCC pproved lab is 3 to 4 weeks & it is expected that report will be available in middle of February for submission in DPCC. M/s ITL Labs Pvt. Ltd, Mangolpuri Indl Area has stated that they are one of the active member of CETP Society of the area & effluent outlet of the premises is directly connected with the said CETP. 

In response to our letter dated 30.12.2008, Ms. Kusum Lata Bhardwaj, Kanpur has replied that she will not be able to come due to some health problems and do not travel to far off distances where she can not get the desired home made edibles. Any infaction caused by restaurant made edibles will also become troublesome and are other health hazards also. She also shows her inability to attend the meeting of CMC (MSW) on 23.01.2009 when contacted over phone.

Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Put up status report in next CMC (MSW) meeting.
Chairman
  M. S.
        Member      
Prof. S.K Gupta
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  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Agenda No. 11
Re: In-situ treatment of waste water in the Najafgarh drain and Supplementary Drain.

A letter has been received from Foundation for Greentech Environmental Systems suggesting an unconventional treatment system along the length of the two major drains in the city i.e. Najafgarh drain and supplementary drain and requested to allow to make a representation in this regard. 
Because of the long length and a well defined large perimeter, both these drains in particular, and some others in general, can be considered as long plug flow type treatment reactors.  This approach offers a unique opportunity to develop the large drains as in-situ treatment reactors wherein the waste water can be lifted in short stretches, recycled and spread on the perimeter.  A system of reed beds and wetland can be created on the perimeter which will help in rapid up take of dissolved organic matter.  By this innovative system, one can reduce a fair degree of BOD load in the waste water before it reaches the river.  A schematic of the suggested scheme is presented in the following exhibit.

Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

A letter be sent to CEO, DJB through Chairman, DPCC to examine the matter.

Chairman
  M. S.
        Member      
Prof. S.K Gupta
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  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Agenda No. 12

Sub:- Implementation of MSW Rules.

A letter D.O. No. B-19011/1/PCP/2008/6260 dated 03.09.08 on the above cited subject was received from on the Chairman, Central Pollution Control Board.  Accordingly, following directions was issued to local bodies i.e. Municipal Corporation of Delhi, New Delhi Municipal Council  and Delhi Cantonment Board on 27.11.08 (C/149-154):-

1. Shall submit a time bound action plan for compliance with MSW Rules and attach such a plan with Authorization form, and forward to DPCC before 30.10.08 and DPCC on receipt of such plan, will grant authorization stipulating an implementation schedule. 

2. Shall undertake Quantification and Characterization of waste in Delhi and submit to DPCC, which will in turn, send a consolidated report to CPCB before 31.12.08.

The action taken report with Ambient Air Monitoring Reports of July, 2008 for three landfill sites in Delhi, Water Quality Analysis Report of July, 2008 for three landfill sites in Delhi and Analysis Report of ground water of July, 2008 at 38 locations in Delhi was sent to the Chairman, Central Pollution Control Board vide D.O letter dated 27.11.08 (C/167). 

As no reply has been received from any of the local body w.r.t. above said directions, the reminder letters for the above said directions were issued on 22.01.09 to all three local bodies.

This is for information and perusal to the committee.  

Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

No action. 
Chairman
  M. S.
        Member      
Prof. S.K Gupta
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Member (Acd. Inst)      
(MSW) 
MSWM Cell

Agenda No : 13 

Sub:- Award of work by CPCB for identification of common landfill sites for Management of Municipal Solid Waste in National Capital Region (NCR). 

A letter F.No. B-19012/1/PCP/2008/9223/9896 dated 19.01.09 addressed to Shri. T.P. Singh, Director, Bhaskaracharya Institute for Space Application and Geo-Informatics, Department of Science and Technology, Govt. of Gujarat Near Ch-0 Circle, Indulal Yagnik Marg, Gandhinagar-382007 was received from Addl. Director, Central Pollution Control Board on the above cited subject.   Accordingly, based on the proposal of Director, Bhaskaracharya Institute for Space Application and Geo-Informatics, on identification of sites for regional landfill facilities for Management of Municipal Solid Waste in the National Capital Region (NCR) vide letter no. BISAG/CPCB/2008/2237 dated 13.10.08 CPCB is directed to convey the sanction of CPCB for execution of the study on “Identification of common/ regional landfill sites using remote sensing and GIS techniques in the National Capital Region (NCR) covering 16 towns/ cities for Management of Municipal Solid Waste at a total cost of Rs. 35.0 lakh.  The payment schedule, and other terms and conditions are mentioned below:- 

Payment Schedule:-

1. 50% of the total cost will be released on the acceptance of the terms and conditions of the sanction.
2. 40% of the total cost will be released on the receipt of the Utilization Certificate (UC) of the first installment along with progress repot.
3. Final installment (10% of the cost) on completion of the study and submission of the final report.
Time Frame:- Nine months (9) from the date of release of first installment.

General Terms and Conditions:-

1. This sanction is for conducting study for identification of common landfill sites in National Capital Region.

2. The fund released will be exclusively used for the study.

3. The work has to be executed in close co-ordination with CPCB and as per the Municipal Solid Waste (Management and Handling) Rules, 2000.

4. All the information collected, generated, maps prepared will belong to CPCB and may be submitted to CPCB at the completion of the study.  It should not be used without CPCB’s permission.

5. On receipt of the acceptance of this sanction order, an amount of Rs. 17.5 lakhs (Rupees seventeen lakh fifty thousand only) will be released to Bhaskaracharya Institute for Space Application and Geo-Informatics (BISAG), Department of Science and Technology, Govt. of Gujarat as 1st installment.  The balance amount of Rs. 17.5 lakhs will be released in two installments as specified in above payment schedule.  

This is for information and perusal to the committee.  

Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Send a copy of the letter to MCD Commissioner.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.

Member (Acd. Inst)      
(MSW) 
MSWM Cell

Agenda for 13TH  CMC (MSW Cell) meeting to be held on 23.01.2009.

13th meeting of the Committee constituted for deciding the consent under the Air and Water Acts, for CETPs, STPs, WTPs & Power Plants cases, Special Reference cases and follow up action on the pending issues of the Local Area Environment Committee, is scheduled to be held on 23.01.2009.
Agenda 1- Follow up action on the pending issues of the Local Area Environment Committee:

a) Matter regarding effluent generated in Patparganj Industrial Area.

b) Matter regarding conveyance system of WIA.
c) Removal of encroachment by DDA in WIA.

d) Construction of Road in WIA by MCD.’

e) Matter regarding illegal hazardous waste dumping sites.  

f) Matter regarding TSDF site at Ghumenhera.

g) Matter regarding gas supply to WIA.

h) Matter regarding E-waste.
Agenda 2- Cases of power plants w.r.t 7 power plants. 

Agenda 3- Cases of Municipal Solid Waste Management Project and Slaughter House- 9 units
Agenda 4 - Cases of CETPs – w.r.t 16 CETPs. 

Agenda 5 - Cases of STPs – w.r.t. 28 STPs. 

Agenda 6 - Cases of Water Treatment Plants –  w.r.t  six (6) plants.

Agenda 7-  Reutilization of treated effluent from CETPs.
Agenda 8 – Study of CETPs in Delhi.

Agenda 9 - Inviting proposal for establishment of CETPs in Delhi.

Agenda 10- Compliance of EPCA directions.

Agenda 11- An Article entitled “Chemical laboratories releasing abundant chemicals into the sewers” -reg.
Agenda 12- 
 Implementation of MSW Rules.
Agenda 13- 
Award of work for identification of common landfill sites for management of MSW in NCR.

Agenda 14- Any other item with the permission of Chairman.
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Rithala STP– Ph-I, (40 MGD)

Action Taken Report

As decided by CMC, letter issued to the Member Engineer, DDA on 03.11.08 .  No reply received in this regard. However, Ex. Engineer,  DJB has submitted a letter informing that the deficiencies pointed out have been rectified and affidavit to this effect has all ready been furnished in your office an requested for renewal of consent.  

As per DPCC Analysis report, dated 13.10.08 (sampling done on 18.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 31.10.2008), BOD (33 mg/l) is exceeding the prescribed standard (30 mg/l).
Decision of CMC (MSW) meeting dated 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.

Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 17.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
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   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Rithala  STP– Ph-II, ( 40 MGD)

Consent Status 

Previous Consent valid upto 21.01.06. Applied for renewal of consent on 20.01.2006. 

Decision taken  

Issue SCN giving last opportunity to remove the deficiencies observed during inspection

Action taken report

SCN issued on dated 15-02-07. Reply received on 22-03-07. The following submissions have been made:-

The defective flow meter at treated effluent channel made operational. Both sludge thickeners are in working condition now. Sludge de-watering unit is operated only during monsoon season. Matter wrt reuse of treated effluent is under planning stage. Electricity is being generated as per    raw sewage availability. As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 19.10.2007:

Unit was given last opportunity to correct deficiencies. A reply received on 22.03.07 indicates that some remedial action has been taken. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 

Action taken report

Letter issued on 07.11.2007. Reply received on 26.12.2007 and submitted affidavit to confirm correction of deficiencies. Further requested for exemption of Bank Guarantee as all defects/ deficiencies attended.  
Decision of CMC (MSW) meeting dated 09.01.2008:

MS, DPCC  to inspect  and submit the report in next CMC (MSW) Meeting.
Action taken report

Inspected on 21-2-2008. The observation are as follows :

Ultrasonic flow meters operational. 

Primary Settling Tanks and Final Settling tanks found operational. 

One aeration tank out of four found not in use and as informed tank is under cleaning and not in use from last six months. 

Three generators (each 890KWH) installed for generation of electricity from bio-gas and found operational.

Total power requirement per day for phase-II is approx. 34000 KWH/ day (for 40 MGD effluents) and average power generation from bio-gas was 14000 KWH/ day. As informed actual requirement for power is 20,000 to 25,000 KWH/ day as per the average intake.  

Approximate 8000 cubic meter gas is generated per day. 

Average intake effluent intake in Jan, 2008 was 23.64 MGD. 

Treated effluent (5MGD) is used by DDA for horticulture. It is purposed that 25 MGD treated effluents will be supplied to Proposed Pragati Power Projects, Bawana and 2 MGD to NDPL.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 29.01.2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

Letter to be Member (Drainage) for seeking reasons of low intake quantity of sewage & under utilization of STP capacity. Letter to be issued to the unit for submitting an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

Letters issued on 26.03.2008. 

Reply received on 31.03.2008 stating that DJB has rectified all its deficiencies. DJB has requested that exemption may be granted to submit Bank Guarantee as DJB is running the STP for public service purpose and have no profit motive unlike other private installation
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Rithala STP– Ph-II(40 MGD)

where these norms are generally applicable.  DJB has already submitted an affidavit regarding rectification of deficiencies. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 28.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 17.03.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 12.05.2008:

No action. 

Action Taken Report

Applied for renewal of consent on 20.01.2006.

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 15.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 STP was found non operational during visit on 16.05.2008. 

As per DPCC Analysis report, dated 11.07.2008 (sampling done on 09.06.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.07.2008:

Put up in next CMC in Sep, 2008.

Action Taken Report

EE, DJB has submitted a letter on 28.09.08 that this office has completed the formalities and requested for renewal of consent. 

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 16.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 18.08.2008), all parameters are within the prescribed standard
A D. O. letter issued to VC, DDA to explore the possibility of reuse of treated water of Rithala STP for the Japanese Park at Rohini.

Decision of CMC (MSW) meeting dated 10.10.2008:

Member Secretary, DPCC may issue reminder to Member Engineer, DDA for our earlier letter dated 23.09.2008. To be taken up in next CMC.

Consent Status 

Applied for renewal of consent on 20.01.2006. 

Action Taken Report

As decided by CMC, letter issued to the Member Engineer, DDA on 03.11.08.  No reply received in this regard.

As per DPCC Analysis report, dated 13.10.08 (sampling done on 18.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 31.10.2008), all parameters are within the prescribed standard.
Contd..3..

..3.

Rithala STP– Ph-II(40 MGD)

Decision of CMC (MSW) meeting dated 05.12.2008:

No Action.

Action Taken Report

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 17.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

No action.
Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE
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   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Pappankalan STP ( 20 MGD)

Consent Status 

Applied for renewal of consent on 10.12.2004. Consent issued on 25.08.2008 & valid upto 06.01.2011. 

Decision taken  

Issue SCN to SE, a copy to Chief Engineer giving last opportunity to rectify the deficiencies

Action taken report

SCN issued on 15.02.07. No reply received. 

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 19.10.2007:

While the unit is applied for consent he has not corrected deficiencies. Unit was given last opportunity to correct deficiencies. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 

Action taken report

Letter issued on 07.11.2007. Reply received on 26.12.2007 and submitted affidavit to confirm correction of deficiencies. Further requested for exemption of Bank Guarantee being a Govt. deptt. Under GNCTD. Submitted application for renewal of consent by post, (ID No. 24674 dated 07.01.2007) & as decided, letter for deficiencies issued on 08.01.08.
Decision of CMC (MSW) meeting dated 09.01.2008:

EE to inspect and report submit in next CMC (MSW) Meeting.
Action taken report

Aerators 22 nos  found in operation and 2 are under maintenance. 

Ultrasonic flow meter found operational. 

Sewage intake is low (14-15MGD) compared to installed capacity, as reported by Sh. Katakwal, EE DJB, this is due to the no population in the catchment area i.e. Dwarka. Presently they are taking sewage from Najafgarh drain also. 

All the digester found under use, however biogas generated is burned in the plant through burners as the provision of supply of  biogas is not provided so far due to less occupancy in the nearby vicinity of  STP. 

Acoustic enclosure provided with the DG set of 125KVA. 

As reported, DDA has constructed for reservoirs for reuse of treated effluent.     

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 23.01.2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

To ensure the maximum capacity utilization of the installed STP near Najafgarh nallah, STPs may be identified and accordingly letter may be written to CEO, Delhi Jal Board for taking the required quantity of water from Najafgarh Drain. 

Letter to Member (Drainage) for seeking affidavit for the reasons of low intake quantity of sewage & under utilization of STP capacity after inspection of the STP personally. Case to be taken up in April CMC.

Action Taken Report

Letters issued on 26.03.2008. 

Unit has submitted its reply along with an affidavit on 15.04.2008 stating that the reason for low intake quantity of sewage and under utilization of 20 MGD STP after inspection along with Member (Draining) are as under :-

(i) The encatchment area of this 20 MGD STP is not fully developed, as and when area is fully developed, the capacity of STP would full be utilized.

(ii) Presently, they are lifting approx. 10 MGD sewage water from Palam Drain / Nalah for this STP and treating about 16 MGD sewage at this STP.
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Pappankalan STP ( 20 MGD)

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.2008), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 09.04.2008 (sampling done on 26.03.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 12.05.2008:

No action. 

Action Taken Report

Applied for renewal of consent on 10.12.2004. 

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 21.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 19.05.2008), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 11.07.2008 (sampling done on 10.06.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.07.2008:

Consent to Operate (renewal) granted after the unit submit requisite fee for renewal of consent. 

Action Taken Report

Requisite fee submitted. Consent to operate (renewal) issued on 28.08.2008.

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 07.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 25.08.2008), all parameters are within the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

No action.

Action Taken Report

As per DPCC Analysis report, dated 13.10.08 (sampling done on 17.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 23.10.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

No Action.

Action Taken Report

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 17.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

No action.
Chairman
  M. S.
        Member      
Prof. S.K Gupta
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   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Najafgarh STP, ( 5 MGD
Consent Status 

Applied for consent to operate on 29.11.2004. 

Decision taken  

Issue SCN to SE, a copy to Chief Engineer giving last opportunity to rectify the deficiencies.

Action taken report

SCN issued on 15.02.07. No reply received.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 19.10.2007:

While the unit is applied for consent he has not corrected deficiencies. Unit was given last opportunity to correct deficiencies. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 

Action taken report

Letter issued on 07.11.2007. Submitted affidavit on 09.01.2008 to confirm correction of deficiencies. Deposited fee on 08.01.08 for conducting effluent analysis by DPCC lab.

Submitted application for renewal of consent by post, (ID No. 24673 dated 07.01.2007) & as decided, letter for deficiencies issued on 08.01.08.
Decision of CMC (MSW) meeting dated 09.01.2008:

EE to inspect and report submit in next CMC (MSW) Meeting.
Action taken report

All 16 aerators found operational. 

Average sewage in take is 1.5MGD to 2.0MGD. 

As reported Sewer lines are yet to be installed in catchment area of STP and presently they are taking sewage from Najafgarh and Dhrampura Drain. 

One DG Set found installed in dismantled conditions and of no use. 

Only single power supply line provided and power failure is approx. 100-125hr/ month, as per logbook. 

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 23.01.2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

To ensure the maximum capacity utilization of the installed STP near Najafgarh nallah, STPs may be identified and accordingly letter may be written to CEO, Delhi Jal Board for taking the required quantity of water from Najafgarh Drain. 

Letter to Member (Drainage) for seeking affidavit for the reasons of low intake quantity of sewage & under utilization of STP capacity after inspection of the STP personally. Case to be taken up in April CMC.

Action Taken Report

Letters issued on 26.03.2008. No reply received so far.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 26.03.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 12.05.2008:

Ask the unit to file reply sought by CMC on 29.02.2008.

Action Taken Report

Applied for consent to operate on 29.11.2004. 

Unit has submitted an affidavit on 03.07.2008 stating that the catchment area of this 5 MGD Najafgarh STP is not fully developed by Sewerage facility. As & when area is  fully developed the capacity of STP would fully be utilized. At present approx. 2.5 to 3 MGD 
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average sewage is being treated. The same will be increased very shortly by lifting sewage water from Dharampura drain falling into Najafgarh drain because surrounding agricultural land has been taken over by DJB for construction of Water Treatment Plant at Najafgarh. The farmers were using Dharampura drain sewage water in recent past.

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 21.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 19.05.2008), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 11.07.2008 (sampling done on 10.06.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.07.2008:

Consent to Operate (renewal) granted after the unit submit requisite fee for renewal of consent. 

Action Taken Report

Requisite fee submitted. Consent to operate (renewal) issued.

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 07.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 25.08.2008), all parameters are within the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

No action.

Action Taken Report

As per DPCC Analysis report, dated 13.10.08 (sampling done on 17.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 23.10.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

No Action.

Action Taken Report

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 17.12.2008), parameters TSS-66 mg/l & BOD-34 mg/l are exceeding the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta
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Member (Acd. Inst)      
(MSW) 
MSWM Cell

Nilothi STP (40 MGD)

Consent Status 

Consent expired in 02-12-06. Applied for renewal of consent on 26-11-2007.

Decision taken  

-

Action taken report

Plant was inspected on 17.11.2006.

SCN was issued on 26.12.06, as numbers of deficiencies were observed.

Plant has not submitted consent application for renewal of consent.

As per inspection by DPCC laboratory dated 19.09.2007 it reveals that the plant was non operational during the monitoring. 

Decision of CMC (MSW) meeting dated 19.10.2007:

The unit was issued SCN on 17.11.2006 and the reply received indicates that some deficiencies have been corrected. SEE to inspect and submit a report on file for necessary action.  The unit may ask to apply for renewal of consent immediately.
Action taken report

Letter issued on 07.11.2007. no reply received. Inspected on 04.01.2007 and some deficiencies were observed during inspection. Not applied for renewal of consent.
Decision of CMC (MSW) meeting dated 09.01.2008:

Inspection was done by SEE on 04.01.2007 and the points were noted which may be communicated to the STP to follow up the points.  
Action taken report

Letter issued on 7-2-2008. No reply received.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 21.11.2007), Except TSS (64 mg/l) & BOD (34 mg/l) others parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 24.01.2007), Except BOD (33 mg/l) others parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

To ensure the maximum capacity utilization of the installed STP near Najafgarh nallah, STPs may be identified and accordingly letter may be written to CEO, Delhi Jal Board for taking the required quantity of water from Najafgarh Drain. 

Reminder letter to be issued to the unit to apply for consent, for submitting an affidavit as to why the parameters are not meeting the prescribed limit and also to file an affidavit w.r.t. rectification of deficiencies. Case to be taken up in April CMC.

Action Taken Report

Letters issued on 26.03.2008. No reply received so far.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 28.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 18.03.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 12.05.2008:

Ask the unit to file reply sought by CMC on 29.02.2008.

Action Taken Report

Applied for renewal of consent on 26-11-2007. No reply has been received so far in response ot our letter dated 05.06.2008.

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 07.04.2008), BOD (32 mg/l) is exceeding the prescribed standard.
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As per DPCC Analysis report, dated 04.07.2008 (sampling done on 28.05.2008), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 11.07.2008 (sampling done on 10.06.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.07.2008:

Issue reminder for compliance of norms and ask the unit to submit Bank Guarantee of Rs. 1 Lakh. 

 Action Taken Report

Letter issued on 20.08.2008. EE, DJB has submitted the reply on 23.09.2008 that presently only 18-20 MGD sewage is being treated at this plant due to non availability of sewage at the feeding pumping stations. Regarding BOD, as per DJB laboratory analysis reports the results of this plant are within the prescribed parameters.  The BOD results in DPCC may change at a particular moment on account of frequent electric failure/low voltage or non availability of sewage during odd hrs. Regarding Bank Guarantee it is submitted that DJB is a govt. deptt under Delhi Govt. hence it is requested to waive off the BG.

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 07.07.2008), parameters BOD (37 mg/l) & TSS (62 mg/l) are exceeding the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 22.08.2008), all parameters are within the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

Issue reminder letter to file Bank  Guarantee within one month. To be taken up in next CMC.

Consent Status 

Applied for renewal of consent on 26-11-2007.

Action Taken Report

As decided by CMC, letter issued on 31.10.08.  No reply received so far.

As per DPCC Analysis report, dated 13.10.08 (sampling done on 22.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 21.10.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

No Action.

Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 10.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

No action.
Chairman
  M. S.
        Member      
Prof. S.K Gupta
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Rohini STP (15 MGD)

Consent Status 

Applied for consent to operate on 01-05-07. 

Decision taken  

CE, DJB was asked to apply for consent, who agreed to do the needful.
Action taken report

As per DPCC laboratory report, during the last several occasions, plant found non operational. Hence, no monitoring report available with DPCC. However plant has submitted analysis report of its own. Treated effluent quality is as per norms laid down.
As per inspection by DPCC laboratory dated 21.09.2007 it reveals that the plant was non operational during the monitoring. 

Decision of CMC (MSW) meeting dated 19.10.2007:

SEE to inspect and report on file.
Action taken report

Inspected on 04.01.2007.

Decision of CMC (MSW) meeting dated 09.01.2008:

Inspection was done by SEE on 04.01.2007 and the points were noted which may be communicated to the STP to follow up the points.  
Action taken report

Letter was issued on 12-2-2008. No reply received.

As per DPCC Analysis report, dated 11.01.2008 STP was found non operational during inspection on 21.09.2007.
As per DPCC Analysis report, dated 25.02.2008 STP was found non operational during inspection on 29.01.2007.
Decision of CMC (MSW) meeting dated 29.02.2008:

Sh. Aditya Narayan Singh, Scientist, Deptt of Env., will inspect the STP & submit report on file. Based on that, decision will be taken to write letter to Member (Drainage), DJB. Case to be taken up in April CMC.

Action taken report

Inspected by Sh. A. N. Singh.

As per DPCC Analysis report, dated 18.03.2008 (visited on 28.02.2008), STP was found non operational during inspection on 21.09.2007.
As per DPCC Analysis report, dated 09.04.2008 (visited on 17.03.2008), STP was found non operational during inspection on 21.09.2007.
Decision of CMC (MSW) meeting dated 12.05.2008:

The STP is not getting adequate water as per the installed capacity. As per the inspection report it was found that there is lack of coordination between DJB and DDA for getting adequate water at STP. Issue letter to both DJB and DDA that they make best possible efforts to ensure that the capacity of the STP plant is better utilized in pubic interest. Call Ex. Engineer of Rohini Zone from DJB & DDA in next CMC (MSW) meeting. 

Action Taken Report

Letters issued on 03.06.2008. Ex Engineer, DDA has submitted reply that there is no sewage pumping station under the jurisdiction of his office & hence no action is required.

As per DPCC Analysis report, dated 03.06.2008 STP was found non operational during inspection on 15.04.2008.
 As per DPCC Analysis report, dated 04.07.2008 STP, was found non operational during inspection on 16.05.2008.

 As per DPCC Analysis report, dated 11.07.2008, no flow was found at the inlet & outlet of STP at the time of visit for monitoring on 09.06.2008.


Contd..2..

..2..

Rohini STP (15 MGD)

Decision of CMC (MSW) meeting dated 29.07.2008:

Chairman, DPCC may write to VC, DDA and CEO, DJB to ensure that the Rohini STP becomes fully functional through appropriate coordination between DDA and DJB. Since, habitation in sector 20 to 25 of Rohini is substantially large and there is no reason for under-utilization of STP about 6 % of its capacity and this needs immediate co-ordination between them for full utilization of Rohini STP. Copy may also be sent to Pr. Secretary, UD, GNCTD to arrange a meeting on his level to sort out the issue. This letter must go out in next week. 

Action Taken Report

Letters were issued to CEO, DJB and Vice Chairman, DDA on 11.08.08.  Copy were also send to Principal Secretary, UD for arranging a meeting to sought out the issued.

Decision of CMC (MSW) meeting dated 10.10.2008:

Member Secretary, DPCC may issue a reminder letter to Addl. CEO,DJB and Engineer Member, DDA. To be taken up in next CMC.

Consent Status 

Applied for consent to operate on 01-05-2007. 

Action Taken Report

As decided by CMC, letters issued to DJB & DDA on 03.11.08.  No reply received so far.

As per DPCC Analysis report, dated 13.10.08 (sampling done on 18.09.2008), no flow was found during the monitoring.
As per DPCC Analysis report, dated 10.11.08 (sampling done on 31.10.2008), no flow was found during the monitoring.
As per DPCC Analysis report, dated 04.12.2008 (sampling done on 21.11.2008), no flow was found during the monitoring.
Decision of CMC (MSW) meeting dated 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.

Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 17.12.2008), no flow was found during the monitoring.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Coronation Pillar STP (40 MGD)

Consent Status 

Consent to operate issued on 28.2.2007 valid upto 12.03.2009.

Decision taken  

Issue consent, subject to the condition that the lacunae observed during the inspection will be removed with in 45 days and also to maintain the log book properly.

Action taken report

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 19.10.2007:

No action. 

Action taken report

-
Decision of CMC (MSW) meeting dated 09.01.2008:

No action. 

Action taken report

No action

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 17.12.2007), all parameters are within the prescribed standard. Phase-III (10 MGD) found non operational during sampling.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 25.01.2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

Letter to be Member (Drainage) for seeking affidavit for the reasons of low intake quantity of sewage & under utilization of STP capacity (only 10 MGD). 

Action Taken Report

Letter issued on 25.03.2008. 

Unit has submitted its reply along with an affidavit on 11.04.08 & informed that the commo0n area SPS of NSTP are Jahangirpuri, Nehru Vihar, Adarsh Nagar, Model Town, R.U. Nagar. Out of these trunk sewers i.e. UTS & NTS and Jahangirpuri Trunk Sewers are settled resulting into less flow of sewage. The rehabilitation of UTS/WTS is in progress which may increase sewer flow. Also the tenders on rehabilitation of Jahangirpuri Trunk Sewer have been called for which work will be awarded in near future. However, all the sewage coming to the STP is fully treated without by-passing any sewage. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard for Phase-I, II,III and old clarifier.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 18.03.2008), all parameters are within the prescribed standard for Phase-I, II,III. BOD (32 mg/l) is exceeding the prescribed norms for old clarifier.
Decision of CMC (MSW) meeting dated 12.05.2008:

Let the unit file reply by 30.06.2008, why the BOD is exceeding the prescribed norms in the monitoring conducted by DPCC Laboratory on 18.03.2008.

Action Taken Report

Submitted 06.06.08 this is in reference the said subject, it is to inform that all out efforts are made to treat sewage and achieving BOD/SS as 30 mg/lt /50 mg/lt.  and submitted report of sampling done in DJB Laboratory along with DPCC on 
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Coronation Pillar STP (40 MGD)

18.03.08,  the result shows BOD as18 mg/lt. where BOD indicated by DPCC as 32 mg/lt. which are contradictory.  There seems to be mixing/change of sample.  The result of effluent i.e. BOD/SS from old S.T.P are very well within prescribed limits of DPCC.

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 09.04.2008), all parameters are within the prescribed standard for Phase-I, II, III & Old Clarifier.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 15.05.2008), all parameters are within the prescribed standard for Phase-I, II, III & Old Clarifier.

As per DPCC Analysis report, dated 11.07.2008 (sampling done on 20.06.2008), all parameters are within the prescribed standard for Phase-I, II, III & Old Clarifier.
Decision of CMC (MSW) meeting dated 29.07.2008:

Put up in next CMC in Sep, 2008.

Action Taken Report

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 07.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 11.08.2008), all parameters are within the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

No action.

Consent Status 

Consent to operate is valid upto 12.03.2009.

Action Taken Report

As per DPCC Analysis report, dated 13.10.08 (sampling done on 11.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 22.10.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

 No Action.

Action Taken Report

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 24.12.2008), all parameters are within the prescribed standard for phase-I (20 MGD) & Phase-II (10 MGD) plants. However for Old Clarifier (10 MGD) plant TSS-52 mg/l & BOD-36 mg/l are exceeding the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Vasant Kunj STP (5.2 MGD)

Consent Status 

Consent issued on 22.09.05 & valid up to 11-12-07.Applied for renewal on 29-1-2008.

Decision taken  

-

Action taken report

Plant was inspected on 14.11.06.

SCN issued on 26.12.2007 as number of deficiencies were observed during the above said inspection.

Plant has not submitted any reply. 

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 19.10.2007:

Unit was given last opportunity to correct deficiencies. Unit may be reminded to correct all deficiencies by 31.12.07 and also to submit an affidavit and BG of Rs. One lakh  (valid for period of six months) by 31.12.07. 

Action taken report

Letter issued on 06.11.2007. No reply received.
Decision of CMC (MSW) meeting dated 09.01.2008:

EE to inspect and put up in next CMC (MSW) meeting.
Action taken report

Inspected on 22-1-2008 and observations are as under: 

Flow meter installed for 2.2. MGD plant found operational, however flow meter of 3 MGD found non-operational condition. 

4 aerators (out of 8) for 2.2 MGD and 4 aerators (out of 10) found out of order.

Logbook maintained for operation of pumps etc.

Treated effluent discharge in drain leading to Sanjay Ban as reported.

Representative of DJB not shown the records wrt removal of sludge/ manure from the plant.

Applied for renewal of consent on 29.01.2008.

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 28.12.2007), all parameters are within the prescribed standard for phase-I (2.2 MGD) plant. However for phase-II (3.0 MGD) plant TSS (65 mg/l) & BOD (34 mg/l) are exceeding the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 24.01.2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

Issue notice for non operation of flow meter & aerators, to file an affidavit w.r.t. correction of deficiencies within one month & reason for non submission of Bank Guarantee. Case to be taken up in April CMC.

Action Taken Report

 Letter issued on 25.03.2008. Reply received on 24.04.2008 without affidavit. 
As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (visited on 18.03.2008), STP was found non operational.
Decision of CMC (MSW) meeting dated 12.05.2008:

The unit may be asked to explain why the STP was non operational and how is the waste water getting disposed off  as observed during inspection by DPCC Laboratory on 18.03.2008, for conducting monitoring. STP to file reply by 30.06.2008. 
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Vasant Kunj STP (5.2 MGD)

Action Taken Report

Letter issued on 02.06.08, however, no reply has been received so far.     

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 21.04.2008), BOD (33 mg/l) is exceeding the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 13.05.2008), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 11.07.2008 (sampling done on 13.06.2008), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 29.07.2008:

Ask the unit to file an affidavit with reply of letter issued on 02.06.2008. 

Action Taken Report

Letter issued on 20.08.08. DJB has submitted by replies on 05.09.08 and stated that on  18.03.08, it was heavy rainfall at Vasant Kunj, therefore the concerned foreman of STP closed the gates so that storm water could not enter the plant and it should take the route to storm water drains only.  Meanwhile he informed the concerned PWD people who opened the storm water drains and all the rain water followed that route.  Then the foreman opened the gate and plant was normal.  As it was first rain of the season, therefore the system was not so much well operative. However it is certified that there is no by-pass arrangement available as such at STP Vasant Kunj.  If one of the gates is closed also, the water will automatically go to other STP at Vasant Kunj only.  (As there are two STPs i.e. 2.2 MGD and 3 MGD). 

A complaint has been received from RWA Vasant Kunj regarding the foul smell  and as decided on file, show cause notice was issued on 15.09.08.  EE, DJB as submitted reply on 16.09.08 that STP was visited by SE (SDW) IV on 09.09.08 and there was no foul smell at the whole plant.  The plant is situated adjacent to the Central School Building and if there is any smell, the school authorities immediately inform to the higher authorities.  The RWA houses which are complaining about the foul smell are situated at a distance from the plant.  A gravity duct carrying the sewage water passes through these houses and it gives the foul smell occasionally whenever its manhole covering gets disturbed.  The above was apprised to Sh.  D.S. Yadav telephonically by our SE (SDW)IV when he visited the plant.  He was very much convinced. They have further stated that the plant is running satisfactorily and its effluent standards are within the permissible designed parameters. 

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 17.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 19.08.2008), all parameters are within the prescribed standard

Decision of CMC (MSW) meeting dated 10.10.2008:

Member Secretary, DPCC may issue reminder to Addl. CEO, DJB. To be taken up in next CMC.
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Vasant Kunj STP (5.2 MGD)

Action Taken Report

As decided by CMC, letter issued on 03.11.08.  Reply received on 20.11.2008 along with the affidavit  of Ex. Engineer, DJB.   

As per DPCC Analysis report, dated 13.10.08 (sampling done on 05.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 31.10.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.12.2008 (sampling done on 07.11.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

No Action.

Action Taken Report

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 11.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

No action.
Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Narela STP (10 MGD)

Consent Status 

Previous Consent valid upto 14.01.2005. Applied for renewal of consent on 14.01.2005 and issued on 7-11-2007 and valid up to 13-1-2008. Applied for renewal of consent on 3-1-2008.
Decision taken  

Issue SCN giving last opportunity to remove the deficiencies observed during inspection.
Action taken report

SCN issued on 20-03-2007. Reply received on 18-05-07 The following submissions have been made:-

Flow meter at inlet & outlet of STP are in working condition.                            

Treated effluent is being used for irrigation at the plant and possibility is being explored for its use by DDA or other Civil Agency.

Possibility is being explored for installing mechanical sludge dewatering system at the plant.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 19.10.2007:

Renewal of the consent granted with clear condition that the plant shall operate properly and efficiently.
Action taken report

Consent issued on 07.11.2007.
Decision of CMC (MSW) meeting dated 09.01.2008:

No action.
Action taken report

No action. Applied for renewal of consent on 3-1-2008.
As per DPCC Analysis report, dated 11.01.2008 (sampling done on 17.12.2007) except BOD (33 mg/l), other parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 24.01.2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

Letter to be Member (Drainage) for seeking affidavit for the reasons of low intake quantity of sewage & under utilization of STP capacity (only 10 MGD). 

Action Taken Report

Letter issued on 26.03.2008. 

Unit has submitted its reply along with an affidavit on 11.04.08 & informed that the supply of clear water in the area is less due to non commissioning of Bawana Water Treatment Plant. Moreover, there is less habitat in the area further decreasing sewage in the catchment area. Nearby villages sewer is also un-trapped due to non availability of sewage systems. However, all the sewage coming to STP is full treated without by-passing any sewage. It is not proposed to lay sewer system in nearby villages. Also laying of sewerage system in nearby colonies is in progress. All about efforts may increase intake flow  to the STP  and will improve utilization capacity of STP.

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 22.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 25.03.2008), all parameters are within the prescribed standard.
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Narela STP (10 MGD)

Decision of CMC (MSW) meeting dated 12.05.2008:

No action. 

Action Taken Report

Applied for renewal of consent on 3-1-2008.
As per DPCC Analysis report, dated 03.06.2008 (sampling done on 22.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 15.05.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 11.07.2008 (sampling done on 16.06.2008), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 29.07.2008:

Consent to Operate (renewal) granted.

Action Taken Report

Consent to operate (Renewal) issued on 20.08.2008.

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 09.07.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 11.08.2008), all parameters are within the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

No action.

Action Taken Report

As per DPCC Analysis report, dated 13.10.08 (sampling done on 11.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 22.10.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

No action.

Action Taken Report

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 24.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

No action.
Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE
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   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

OKHLA STP , [Phase- I, II, III & IV, (12+30+37+45), Total 124 MGD) ]

Consent Status 

Consent to operate was granted by CPCB on 23.01.1987 (valid upto 31.12.88), 

Applied on 03.04.1998 issued by DPCC on 14.06.99 (valid upto 31.05.2000), 

Applied on 10.05.2000 issued by DPCC on 18.04.2001 (valid upto 17.04.2002).

Applied on 08.10.2002 issued by DPCC on 20.01.2004 (valid upto 17.04.2005).

Applied for renewal on 10.03.2005 for Phase I, II, III & IV Plant (124 MGD) and yet to be decided. 

Applied for renewal on 10.03.2008 for phase-I (12 MGD) plant (ID No. 25118).

Applied for renewal on 10.03.2008 for phase-II (30 MGD) plant (ID No. 25120).
Applied for renewal on 10.03.2008 for phase-III (37 MGD) plant (ID No. 25117).
Applied for renewal on 10.03.2008 for phase-IV (45 MGD) plant (ID No. 25119).
Decision taken  

Issue SCN giving last opportunity to remove the deficiencies observed during inspection
Action taken report

SCN issued on 15.2.2007. Reply received on 26-03-07. The following submissions have been made:-

· Magnetic flow meter is not feasible. Ultrasonic flow meter also did not work due to deposition of sludge /plastic floating material on probes of the meter.

· Wrt renovation of sludge drying beds, necessary action is being taken by construction division.

· The issue, of trapping of effluents flowing in the two drains passing through the plant, has not been addressed in the reply.

· The supply of effluents for irrigation after primary treatment suspended. The matter is under examination.

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 19.10.2007:

Unit has applied for renewal of consent but has not corrected all the deficiencies pointed out vide SCN issued on 15.2.07. Unit may be reminded to correct all deficiencies and only then consent will be granted.
Action taken report

Letter issued on 07.11.2007. No reply received.
Decision of CMC (MSW) meeting dated 09.01.2008:

SEE to inspect and put up in next CMC (MSW) meeting.
Action taken report
Inspected on 19-2-2008. 

No flow meters were installed with any of the four STPs. Aerators found operational. 

Bio-gas generated in STPs supplied to south Delhi area i.e. Lajpat Nagat, New friends colony, sukhdev Vihar etc. 

Effluents from different pump houses which is to STPs, no open drain carrying raw effluents seen in the premises. 

As enquired storm water drain(Harkesh Nagar Drain) is passing through STP, the said drain being storm water drain is not connected with STP. The drain leading to Madanpur Khadar is closed, being area is acquired by DDA. 

No bypass observed.  All the four STPs are connected to a common channels within the premises before discharge. 

As Informed about 10-15 MGD treated effluents is used for horticultures by CPWD. About 5MGD treated effluent to the also used by Jaitpur village for agriculture purposes. 

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 18.12.2007) all  parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 22.01.2007), all parameters are within the prescribed standard.
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OKHLA STP , [Phase- I, II, III & IV, (12+30+37+45), Total 124 MGD) ]

Decision of CMC (MSW) meeting dated 29.02.2008:

Letter for installation of flow meter and TOC analyzer.

Sh. Aditya Narayan Singh will study the file & decision will be taken accordingly.  

Action Taken Report

 Letter issued on 03.04.2008. As decided on file, note of Sh. A. N. Singh is to be putup in next CMC. 

Now DJB has submitted separate application (4 applications) for renewal of consent for each phase of STP. 

Applied for renewal on 10.03.2008 for phase-I (12 MGD) plant (ID No. 25118).

Applied for renewal on 10.03.2008 for phase-II (30 MGD) plant (ID No. 25120).
Applied for renewal on 10.03.2008 for phase-III (37 MGD) plant (ID No. 25117).
Applied for renewal on 10.03.2008 for phase-IV (45 MGD) plant (ID No. 25119).
As per DPCC Analysis report, dated 18.03.2008 (sampling done on 03.03.2008), all parameters are within the prescribed standard. for Phase I, II, II & IV STPs.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 20.03.2008), all parameters are within the prescribed standard for Phase I, II, II & IV STPs.
Decision of CMC (MSW) meeting dated 12.05.2008:

Consent is renewed for all the four applications. 

Action Taken Report

Consent issued on 03.06.08 to all four phases of Okhla STP. 

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 08.04.2008), all parameters are within the prescribed standard for Phase-I, II, III & IV.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 06.05.2008), all parameters are within the prescribed standard for Phase-I, II, III & IV.
As per DPCC Analysis report, dated 11.07.2008 (sampling done on 13.06.2008), all parameters are within the prescribed standard for Phase-I, II, III & IV.

As per DPCC Analysis report, dated 11.07.2008 (sampling done on 12.06.2008), all parameters are within the prescribed standard for Phase-I, II, III & IV.

Decision of CMC (MSW) meeting dated 29.07.2008:

No action. 

Action Taken Report

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 02.07.2008), all parameters are within the prescribed standard for Phase-I, II, III & IV.

As per DPCC Analysis report, dated 10.09.2008 (sampling done on 19.08.2008), all parameters are within the prescribed standard for Phase-I, II, III & IV
Decision of CMC (MSW) meeting dated 10.10.2008:

No action.

Consent Status 

Consent is renewed for all the four phses on 03.06.2008 & valid upto 09.03.2011. 

Action Taken Report

As per DPCC Analysis report, dated 13.10.08 (sampling done on 08.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 15.10.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.12.2008 (sampling done on 06.11.2008), parameters TSS-54 mg/l, BOD-34 mg/l & Phosphate-5.4 mg/l were found exceeding the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.
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OKHLA STP , [Phase- I, II, III & IV, (12+30+37+45), Total 124 MGD) ]
Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 11.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE
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   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Okhla STP, (16 MGD)

Consent Status 

Consent is renewed on 29.05.2008 & valid upto 16.12.2010. 

Decision taken  

_
Action taken report

Plant was inspected on 06.12.06. SCN dated 02.1.2007 was issued as number of deficiencies were observed. Plant  submitted reply with the following submissions:-

· Magnetic flow meter is not feasible in such type of STP’s. Ultrasonic flow meter also did not work due to deposition of sludge /plastic floating material on probes of the meter.

· Fourteen to sixteen aerators at a time are sufficient for generating effluent of desired quantity .However, all digesters and aerators have been made operational.

·  Presently, part of treated effluent is being used for horticulture purpose from this unit. 

As per DPCC Analysis report, dated 10.10.2007 (Sampling done in Sept. 2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 19.10.2007:

Unit has applied for renewal of consent but has not correct all the deficiencies pointed out vide SCN issued on 02.01.2007 

Unit may be reminded to correct all deficiencies and only then consent will be granted.

Action taken report

Letter issued on 06.11.2007. No reply received.
Decision of CMC (MSW) meeting dated 09.01.2008:

SEE to inspect and put up in next CMC (MSW) meeting.
Action taken report

Inspected on 19-2-2008. 

Ultrasonic flow meters installed at inlet and outlet of STP found of functional. 

Aerators found operational and sludge digesters are in use.

TOC analyzer installed at outlet of STP however found non-operational condition as informed TOC analyzer is not in use for last few moths due to non-availability of its chemicals and non-maintenance by supplier of TOC analyzer. 

Bio-gas generated in STPs supplied to south Delhi area i.e. Lajpat Nagat, New friends colony, sukhdev Vihar etc. 

This STP is connected with other four STPs to a common channels within the premises before discharge. 

As Informed about 10-15 MGD treated effluents is used for horticultures by CPWD. About 5MGD treated effluent to the also used by Jaitpur village for agriculture purposes. 

Applied for renewal of consent on 17.12.07

As per DPCC Analysis report, dated 11.01.2008 (sampling done on 18.12.2007) all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 25.02.2008 (sampling done on 22.01.2007), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.02.2008:

Letter for non functioning of TOC analyzer.

Sh. Aditya Narayan Singh will study the file & decision will be taken accordingly.  

Action Taken Report

 Letter issued on 01.04.2008. Submitted reply on 21.04.08 in response to our letter dated 01.04.08, informing that TOC Analyzer is in working order and copies of reports are enclosed.  

Contd..2..

..2..

Okhla STP, (16 MGD)

As decided on file, note of Sh. A. N. Singh is to be putup in next CMC. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 03.03.2008), all parameters are within the prescribed standard for Phase V STPs.

As per DPCC Analysis report, dated 09.04.2008 (sampling done on 20.03.2008), all parameters are within the prescribed standard for Phase V STPs.

Decision of CMC (MSW) meeting dated 12.05.2008:

Consent is renewed. 

Action Taken Report

Consent issued 29.05.08.

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 08.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 06.05.2008), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 11.07.2008 (sampling done on 12.06.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.07.2008:

No action. 

Action Taken Report

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 02.07.2008), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 10.09.2008 (sampling done on 19.08.2008), all parameters are within the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

No action.

Action Taken Report

As per DPCC Analysis report, dated 13.10.08 (sampling done on 08.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11..2008 (sampling done on 15.10.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

No action.

Action Taken Report

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 11.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

No action.
Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

STP at C-DOT Campus, Chattarpur, Mehrauli, New Delhi-30. ((125 KLD)

Consent Status 

Consent to operate expired on 12.4.2007.

 Applied for renewal of consent on 11.03.2008 vide ID No. 25144. 

Decision taken  

-

Action taken report

A letter was issued on 26.06.2007, to  submit the consent application, but no reply/consent application received.

Decision of CMC (MSW) meeting dated 19.10.2007:

Unit may be asked to apply for renewal of consent. 

SEE to inspect. 

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Inspected on 04.01.2007. Sewage of office complex is being treated in STP. Most of the treated effluent is being used for horticulture purposes in complex. Flow meter at inlet not installed. Chlorination not done as feeding pump is out of order. Requested for one month time for submission of desired details.(i.e. consent application)
Decision of CMC (MSW) meeting dated 09.01.2008:

A letter for deficiencies be sent to unit and put up in next CMC (MSW) meeting.
Action taken report

Letter issued on 12.02.08. Reply received on 28.02.08.

Analysis report not received from DPCC laboratory so far.

Decision of CMC (MSW) meeting dated 29.02.2008:

Issue letter to apply for renewal of consent & to submit affidavit w.r.t. correction of deficiencies with in one month.

SSO(Water) to ensure that she will do the monthly monitoring of all CETPs & STPs and submit the test report before the CMC(MSW) meeting.

Action Taken Report

 Letter issued on 26.03.2008. Unit has submitted reply on 24.04.208. Applied for renewal of consent on 11.03.2008 vide ID No. 25144. 

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 26.02.2008), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 09.04.2008 (sampling done on 28.03.2008), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 12.05.2008:

Consent is renewed. 

Action Taken Report

Consent issued on 03.06.08.

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 21.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 30.05.2008), all parameters are within the prescribed standard.


Contd..2..
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STP at C-DOT Campus

As per DPCC Analysis report, dated 11.07.2008 (sampling done on 13.06.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.07.2008:

No action. 

Action Taken Report

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 17.07.2008), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 10.09.2008 (sampling done on 27.08.2008), all parameters are within the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

No action.

Consent Status:

Consent issued on 03.06.2008 & valid upto 10.03.2010.

Action Taken Report

As per DPCC Analysis report, dated 13.10.08 (sampling done on 05.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 08.10.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

No action.

Action Taken Report

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 12.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

No action.
Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Bakkarwala STP, (3 MGD)
Consent Status 

Consent issued on 12.02.08 and valid up to 20.05.2010.
Decision taken  

Copy of the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-07 to instruct the officials concerned to apply for the renewal of consent.

Action taken report

Copies of the letters/SCN issued on 01-11-06, 29-11-06 handed over during CMC meeting held on 21-02-07.  Previous Consent valid upto 12.06.06. 

Plant has submitted consent application for renewal of consent on 21-05-07 with self analysis report.

Decision of CMC (MSW) meeting dated 19.10.2007:

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Inspected on 04.01.2008.
Decision of CMC (MSW) meeting dated 09.01.2008:

Consent granted.
Action taken report

Consent issued on 12.02.08.

Analysis report not received from DPCC laboratory so far.

Decision of CMC (MSW) meeting dated 29.02.2008:

SSO(Water) to ensure that she will do the monthly monitoring of all CETPs & STPs and submit the test report before the CMC(MSW) meeting.

Action Taken Report

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 28.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 31.03.2008), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 12.05.2008:

No action. 

Action Taken Report

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 07.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 28.05.2008), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 11.07.2008 (sampling done on 18.06.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.07.2008:

No action. 

Action Taken Report

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 24.07.2008), all parameters are within the prescribed standard.

Contd..2..

..2..

Bakkarwala STP, (3 MGD)
As per DPCC Analysis report, dated 10.09.2008 (sampling done on 22.08.2008), all parameters are within the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

No action.

Consent Status 

Consent issued on 12.02.08 and valid up to 20.05.2010.
Action Taken Report

As per DPCC Analysis report, dated 13.10.08 (sampling done on 22.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 17.10.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

No action.

Action Taken Report

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 31.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

No action.
Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Molar Band STP (3 MGD)
Consent Status 

Consent issued on 12.02.08 and valid up to 20.05.2010.
Decision taken  

Copy of the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-2007 to instruct the officials concerned to apply for the renewal of consent.
Action taken report

Copies of the letters / SCN issued on 01-11-2006 & 29-11-06 handed over during CMC meeting held on 21-02-2007.  Previous Consent valid upto 12.06.06. 

Plant has submitted consent application for renewal of consent on 21-05-2007 with self analysis report.

Decision of CMC (MSW) meeting dated 19.10.2007:

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Inspected on 04.01.2008.
Decision of CMC (MSW) meeting dated 09.01.2008:

Consent granted.
Action taken report

Consent issued on 12.02.08.

Analysis report not received from DPCC laboratory so far.

Decision of CMC (MSW) meeting dated 29.02.2008:

SSO(Water) to ensure that she will do the monthly monitoring of all CETPs & STPs and submit the test report before the CMC(MSW) meeting.

Action Taken Report

As per DPCC Analysis report, dated 18.03.2008 (sampling done on 19.02.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 09.04.2008 (sampling done on 28.03.2008), all parameters are within the prescribed standard.

Decision of CMC (MSW) meeting dated 12.05.2008:

No action. 

Action Taken Report

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 08.04.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 26.05.2008), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 11.07.2008 (sampling done on 12.06.2008), all parameters are within the prescribed standard.
Decision of CMC (MSW) meeting dated 29.07.2008:

No action. 

Action Taken Report

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 02.07.2008), all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 10.09.2008 (sampling done on 20.08.2008), all parameters are within the prescribed standard
Decision of CMC (MSW) meeting dated 10.10.2008:

No action.

Consent Status 

Consent issued on 12.02.08 and valid up to 20.05.2010.
Contd..2..
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Molar Band STP (3 MGD)
Action Taken Report

As per DPCC Analysis report, dated 13.10.08 (sampling done on 05.09.2008), all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 15.10.2008), BOD (35 mg/l) and TSS (53 mg/l) are exceeding the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.

Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 11.12.2008), all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

 Holambi Kalan STP, (2 MGD)
Consent Status 

Consent issued on 14.05.04 & valid upto 08.10.06.Not applied for renewal of consent.

Decision taken  

Copy o f the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-07 to instruct the officials concerned to apply for the renewal of consent.
Action taken report

Copies of the letters/SCN issued on 01-11-2006 & 29-11-2006 handed over during CMC meeting held on 21-02-07. Consent issued on 14.05.04 & valid upto 08.10.06.

Decision of CMC (MSW) meeting dated 19.10.2007:

Unit may be asked to apply for renewal of consent. 

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Letter issued on 07.11.2007. No reply received . 

Not applied for renewal of consent.
Decision of CMC (MSW) meeting dated 09.01.2008:

Issue reminder letter.
Action taken report

Letter issued on 12.02.08. No reply received.

Analysis report not received from DPCC laboratory so far.

Decision of CMC (MSW) meeting dated 29.02.2008:

Issue final reminder letter to concerned EE with the copy to Addl. Commissioner (MCD) to applying for renewal of consent. 

SSO(Water) to ensure that she will do the monthly monitoring of all CETPs & STPs and submit the test report before the CMC(MSW) meeting.

Action Taken Report

 Letter issued on 25.03.2008. Ex. Engineer (S) DDI, MCD has submitted reply on 04.04.08, informing that the STPs at Tikri Khurd and Holambi are non-operational due to some administrative reasons and he is  making all his efforts to make it operational and to hand over these STPs to DJB. Further, requested for three months time for this process.

As per DPCC Analysis report dated 18.03.2008, STP was non operational.
As per DPCC Analysis report, dated 09.04.2008 STP was non operational.

Decision of CMC (MSW) meeting dated 12.05.2008:

To take up with DJB in July, 2008 and ask the unit to apply for renewal of consent. 

Action Taken Report

Letter issued on 03.06.2008. Not applied for consent under Air & Water Act.

Meeting notice issued to DJB & MCD to attend the meeting schedule to be held on 21.07.08.

Executive Engineer, MCD has submitted to letter along with the copy of minutes held on 02.05.08 in the Chamber of Additional Commissioner (S&JJ) with DJB Officers and a copy of the DO letter dated 16.05.08, written by Additional Commissioner (S&JJ) to CEO, Delhi Jal Board regarding handling over of STPs at Molar Bund, Bakkarwala, Tikri Khurd and Holambi.

As per DPCC Analysis report, dated 03.06.2008 STP was non operational.

As per DPCC Analysis report, dated 04.07.2008 STP was non operational.

As per DPCC Analysis report, dated 11.07.2008 STP was non operational.

Contd..2..
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Holambi Kalan STP, (2 MGD)

Decision of CMC (MSW) meeting dated 29.07.2008:

The two STPs of Holambi Kalan & Tikri Khurd, which belongs to MCD, are intended to be handed over to DJB provided they are immediately made operational or the deficiency charges are immediately given by MCD to DJB. 

In public interest, Member Secretary, DPCC may write to Member (Drainage), DJB and Addl. Commissioner (Engineering), MCD requesting them to sort out the matter quickly since no sewage is treated in the area due to non operational status of these two STPs and action taken report may be submitted within a month. 


Action Taken Report

Letters issued on 05.08.2008.

Copy of letter dated 19.09.2008 received from EE, DJB addressed to EE, MCD vide which they have requested for reply of their earlier letter dated 25.08.2008 informing that the DJB has no objection in taking over the plant subject to either the STPs are made operational or deposition of deficiency charges by MCD. 

EE, MCD has submitted a letter on 12.09.2008 informing that as the deficiencies calculated also includes the operation & maintenance charges of one year so the matter is to be sorted out at the level of higher authorities of both the departments and efforts are being made for early settlement.

Decision of CMC (MSW) meeting dated 10.10.2008:

Member Secretary, DPCC may issue a reminder letter with its copy to Commissioner, MCD & CEO, DJB.

Action Taken Report

As decided by CMC, letter issued to MCD & DJB on 05.11.08.  

Executive Engineer, DJB has submitted copy of the letter dated 22.10.08 & 05.11.08 addressed to MCD mentioning that at present STP is non functional and it is no use to take over the above plant in absence of decision of deficiency charges.  Thus you are once again requested to either make both plant operational before handing over or pay deficiency charges so that STPs be made operational.

Executive Engineer, DBJ has submitted a copy of the letter dated 13.10.08 addressed to DJB mentioning that the note for fixing a meeting with Principal Secretary (UD) has been sent for deciding the deficiencies as the Department is unable to make the STPs functional due to non-availability of funds. He further requested that the STPs may kindly be taken over subject to the deficiencies as it has already been done in case of the STP at Molarbund which was taking over by DJB subject to finalization of DJB on 12.05.08.

As per DPCC Analysis report, dated 13.10.08  & 10.11.08 STP was non operational.

Decision of CMC (MSW) meeting dated 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.

Contd..3..
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Holambi Kalan STP, (2 MGD)

Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

Ex. Engineer, DJB has submitted a copy of letter dated 29.12.08 addressed to MCD stating that it is no use to take over the plant in absence of decision of deficiency charges thus either make plant operational before handing over or pay deficiency charges so that STP be made operational.

As per DPCC Analysis report, dated 04.12.08  & 09.01.09 STP was non operational.

Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Tikri Khurd STP (2 MGD)
Consent Status 

Consent expired on 12.06.06. Not applied for renewal.

Decision taken  

Copy o f the letter issued to the plant handed over to Jt. Director, DMES, MCD in the meeting held on 21-02-07 to instruct the officials concerned to apply for the renewal of consent.

Action taken report

Copies of the letters/SCN issued on 01-11-2006 & 29-11-06 handed over during CMC meeting held on 21-02-07. Previous Consent valid upto 12.06.06. Letter issued on 29.11.06 for seeking consent application for renewal. No application for renewal of consent received.

Decision of CMC (MSW) meeting dated 19.10.2007:

Unit may be ask for apply to renewal of consent. 

SEE to inspect. MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Visited on 03.01.2008. Premises of STP found locked. As per information gathered from nearby residents, STP is non operational & locked from last 8-10 months.
Decision of CMC (MSW) meeting dated 09.01.2008:

MS may write to Dy. Commissioner, MCD Narela Zone asking for reasons of closing and details about when STP will restart. Copy to Slum & JJ Deptt, MCD
Action taken report

Letter issued on 12.02.08. No reply received.

Decision of CMC (MSW) meeting dated 29.02.2008:

Letter to Sh. Naresh Kumar, Addl. Commissioner (MCD) through Chairman, DPCC giving details of previous letters.

Action taken report

Letter issued on 25.03.2008. Ex. Engineer (S) DDI, MCD has submitted reply on 04.04.08, informing that the STPs at Tikri Khurd and Holambi are non-operational due to some administrative reasons and he is  making all his efforts to make it operational and to hand over these STPs to DJB. Further, requested for three months time for this process.

As per DPCC Analysis report dated 18.03.2008, STP was non operational.
As per DPCC Analysis report, dated 09.04.2008 STP was non operational.

Decision of CMC (MSW) meeting dated 12.05.2008:

To take up with DJB in July, 2008 and ask the unit to apply for renewal of consent. 

Action Taken Report

Letter issued on 03.06.2008. Not applied for consent under Air & Water Act.

Meeting notice issued to DJB & MCD to attend the meeting schedule to be held on 21.07.08.  

Executive Engineer, MCD has submitted to letter along with the copy of minutes held on 02.05.08 in the Chamber of Additional Commissioner (S&JJ) with DJB Officers and a copy of the DO letter dated 16.05.08, written by Additional Commissioner (S&JJ) to CEO, Delhi Jal Board regarding handling over of STPs at Molar Bund, Bakkarwala, Tikri Khurd and Holambi.

As per DPCC Analysis report, dated 03.06.2008 STP was non operational.

As per DPCC Analysis report, dated 04.07.2008 STP was non operational.

As per DPCC Analysis report, dated 11.07.2008 STP was non operational.

Contd..2..
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Tikri Khurd STP (2 MGD)
Decision of CMC (MSW) meeting dated 29.07.2008:

The two STPs of Holambi Kalan & Tikri Khurd, which belongs to MCD, are intended to be handed over to DJB provided they are immediately made operational or the deficiency charges are immediately given by MCD to DJB. 

In public interest, Member Secretary, DPCC may write to Member (Drainage), DJB and Addl. Commissioner (Engineering), MCD requesting them to sort out the matter quickly since no sewage is treated in the area due to non operational status of these two STPs and action taken report may be submitted within a month. 


Action Taken Report

Letters issued on 05.08.2008.

Copy of letter dated 19.09.2008 received from EE, DJB addressed to EE, MCD vide which they have requested for reply of their earlier letter dated 25.08.2008 informing that the DJB has no objection in taking over the plant subject to either the STPs are made operational or deposition of deficiency charges by MCD. 

EE, MCD has submitted a letter on 12.09.2008 informing that as the deficiencies calculated also includes the operation & maintenance charges of one year so the matter is to be sorted out at the level of higher authorities of both the departments and efforts are being made for early settlement.

Decision of CMC (MSW) meeting dated 10.10.2008:

Member Secretary, DPCC may issue a reminder letter with its copy to Commissioner, MCD & CEO, DJB.

Consent Status 

Consent expired on 12.06.06. Not applied for renewal.

Action Taken Report

As decided by CMC, letter issued to MCD & DJB on 05.11.08.  

Executive Engineer, DJB has submitted copy of the letter dated 22.10.08 & 05.11.08 addressed to MCD mentioning that at present STP is non functional and it is no use to take over the above plant in absence of decision of deficiency charges.  Thus you are once again requested to either make both plant operational before handing over or pay deficiency charges so that STPs be made operational.

Executive Engineer, DBJ has submitted a copy of the letter dated 13.10.08 addressed to DJB mentioning that the note for fixing a meeting with Principal Secretary (UD) has been sent for deciding the deficiencies as the Department is unable to make the STPs functional due to non-availability of funds. He further requested that the STPs may kindly be taken over subject to the deficiencies as it has already been done in case of the STP at Molarbund which was taking over by DJB subject to finalization of DJB on 12.05.08.

As per DPCC Analysis report, dated 13.10.08  & 10.11.08 STP was non operational.

Decision of CMC (MSW) meeting dated 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.

Contd..3..
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Tikri Khurd STP (2 MGD)
Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

Ex. Engineer, DJB has submitted a copy of letter dated 29.12.08 addressed to MCD stating that it is no use to take over the plant in absence of decision of deficiency charges thus either make plant operational before handing over or pay deficiency charges so that STP be made operational.

As per DPCC Analysis report, dated 09.01.2009 STP was non operational.

Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Ghitorni STP,  (5 MGD)
Consent Status 

Not applied for consent.

Decision taken  

CE, DJB was asked to apply for consent, who agreed to do the needful.
Action taken report

No application for consent received.

As per DJB, plant will be commissioned by Dec. 2007. 

Decision of CMC (MSW) meeting dated 19.10.2007:

Unit may be ask for apply to renewal of consent. 

SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs..
Action taken report

Visited on 08.01.2008. Premises of STP found completely dry & non operational. As per information gathered from nearby residents & security person of STP, it  is non operational from last many years. A letter recd from DJB informing that Gitorni STP is yet to be commissioned by DJB after the raw sewage is made available by DDA at the plant. Consent will be submitted to DPCC after operation of plant.

Decision of CMC (MSW) meeting dated 09.01.2008:

MS to write Member (drainage), DJB to give reason for not operating the STP for a long time even the sewage is generated from the surrounding area.
Action taken report

Letter issued on 12.02.08. No reply received.

Decision of CMC (MSW) meeting dated 29.02.2008:

Issue reminder letter to Member (Drainage) by Member Secretary, DPCC.  

Action Taken Report

 Letter issued on 26.03.2008. A letter received oj 26.03.08 from S.E., DJB informing that this STP is not working due to non availability of raw sewage for which the network is to be laid by DDA and requested that matter may be taken up with DDA for laying of network, so that this STP is made functional.

Decision of CMC (MSW) meeting dated 12.05.2008:

The STP is not getting adequate water as per the installed capacity. As per the inspection report it was found that there is lack of coordination between DJB and DDA for getting adequate water at STP. Issue letter to both DJB and DDA that they make best possible efforts to ensure that the capacity of the STP plant is better utilized in pubic interest. 

Call the Ex. Engineer of South Zone from DJB & DDA in next CMC (MSW) meeting. 

Action Taken Report

Letter issued on 02.06.08 , however no reply has been received so far.

Meeting notice issued to DJB & DDA  to attend the meeting schedule to be held on 21.07.08.  

Decision of CMC (MSW) meeting dated 29.07.2008:

Chairman, DPCC may write to VC, DDA and CEO, DJB to ensure that the Ghitorni STP becomes fully functional through appropriate coordination between DDA and DJB. Since, habitation in Rangpuri & other catchment areas is substantially large and there is no reason for un-utilization of STP and this needs immediate co-ordination between them for effective operation & utilization of Ghitorni STP. Copy may also be sent to Pr. Secretary, UD, GNCTD to arrange a meeting on his level to sort out the issue. This letter must go out in next week. 

Contd..2..
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Ghitorni STP,  (5 MGD)
Action Taken Report

Letters were issued to CEO, DJB and Vice Chairman, DDA on 11.08.08.  Copy  were also send to Principal Secretary, UD for arranging a meeting to sought out the issued.

Decision of CMC (MSW) meeting dated 10.10.2008:

Member Secretary, DPCC may issue a reminder letter to Addl. CEO,DJB and Engineer Member, DDA. To be taken up in next CMC.

Consent Status 

Not applied for consent.

Action Taken Report

As decided by CMC, letter issued to DDA & DJB 05.11.08.  No reply received so far.

Decision of CMC (MSW) meeting dated 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.

Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

As per DPCC Analysis report, dated 09.01.2009 STP was non operational.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

STP at National Bureau of Plant Genetic Resources ICAR, Pusa Campus, (80 KLD)
Consent Status 

Consent expired on 07.06.07. Not applied for renewal of consent.

Decision taken  

-
Action taken report

Consent to operate expired on 07.06.2007, and not applied for renewal of consent.

A letter was issued on 26.06.2007 to submit the consent application, but no reply/consent application received.

Decision of CMC (MSW) meeting dated 19.10.2007:

Unit may be ask for apply to renewal of consent.


SEE to inspect.

MS to direct lab officials of DPCC to do lab test of all CETPs, STPs including Mini STPs.
Action taken report

Inspected on 03.01.2008. During inspection it was found that sewage of institute received at STP is directly goes to the final sump though screen. Sewage was not passed through other units of STP. From the final sump, sewage is pumped out in the near by outlet drain for discharge. No dry/wet sludge observed at site.

Neither applied for renewal of consent nor submitted reply of letter.

Decision of CMC (MSW) meeting dated 09.01.2008:

MS to write Director General,  PUSA regarding non operation of STP and that the effluent be discharge only after proper treatment.
Action taken report

Letter issued on 12.02.08. Reply awaited.

Analysis report not received from DPCC laboratory so far.

Decision of CMC (MSW) meeting dated 29.02.2008:

Letter to Joint Secretary, ICAR with copy to Director General, PUSA through    Chairman, DPCC.

SSO(Water) to ensure that she will do the monthly monitoring of all CETPs & STPs and submit the test report before the CMC(MSW) meeting.

Action taken report

Letter issued on 04.04.2008. As desired by Chairman, matter was discussed with Dir. General of PUSA by Member Secretary, DPCC and asked to apply for renewal of CTO and Compliance report before 12.5.08 .  He told that STP is looked after by CPWD but he will instruct them  for compliance.    

As per DPCC Analysis report dated 18.03.2008, STP was non operational.
As per DPCC Analysis report, dated 09.04.2008 STP was non operational.

Decision of CMC (MSW) meeting dated 12.05.2008:

Ask the unit to give reasons for non operation of STP by 30.06.2008 positively. 

Action Taken Report

Letter issued on 02.06.08, however no reply has been received so far.

As per DPCC Analysis report, dated 03.06.2008 (sampling done on 16.04.2008), BOD-120, COD-372, TSS-176 mg/l) are exceeding the prescribed standard.

Contd..2..
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STP at National Bureau of Plant Genetic Resources ICAR, Pusa Campus
As per DPCC Analysis report, dated 04.07.2008 (sampling done on 28.05.2008), ), BOD-46, TSS-124 mg/l) are exceeding the prescribed standard.
As per DPCC Analysis report, dated 11.07.2008 stp was found non operational at the time of visit for monitoring on 27.06.2008.
Decision of CMC (MSW) meeting dated 29.07.2008:

Issue reminder for letter dated 02.06.2008, to comply the norms and also ask the BG of Rs. 1 Lakh. 

Action Taken Report

Letter issued on 20.08.08.  Director NBPGR has submitted a reply on 29.09.08 that they have approached the concerned authorities regarding the adequacy report of ETP and Test Report of Sewage Treatment Plant (STP), as and when it is received, we will submit the same along with all the relevant documents and admissible fee.  

Further, they have requested for exemption of Bank Guarantee since NBPGR is an institute of Indian Council of Agricultural Research (ICAR) an autonomous organization under Deptt.  of Agriculture Research & Education (DARE), Min. of Agriculture. 

The STP plant is being maintained by CPWD and the concern of DPCC has been intimated to CPWD and to ensure that the situation does not arise again they have instructed to Dr. Sidheshwar Prasad, Senior Scientist & Chairman, Electrical Works Committee, NBPGR, to monitor the functioning of CPWD at the STP.         

As per DPCC Analysis report, dated 12.08.2008 (sampling done on 18.07.2008),  parameters BOD (90 mg/l),TSS (62 mg/l) & COD (260 mg/l) are exceeding the prescribed standard.

As per DPCC Analysis report, dated 10.09.2008 (sampling done on 28.08.2008), No flow during the monitoring.
Decision of CMC (MSW) meeting dated 10.10.2008:

Issue reminder letter to file Bank Guarantee and compliance of the norms. To be taken up in next CMC.

Consent Status 

Consent expired on 07.06.07. Not applied for renewal of consent.

Action Taken Report

As decided by CMC, issued on 03.11.08.  No reply received so far.

As per DPCC Analysis report, dated 13.10.08 (sampling done on 18.09.2008), no flow was found during the monitoring.
As per DPCC Analysis report, dated 10.11.2008 (sampling done on 31.10.2008), BOD (52 mg/l) & TSS (136 mg/l) are exceeding letter the prescribed standard.
Decision of CMC (MSW) meeting dated 05.12.2008:

Issue final  reminder letter.

Contd..3..
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STP at National Bureau of Plant Genetic Resources ICAR, Pusa Campus
Action Taken Report

As decided by CMC, final reminder letter was issued on 05.01.2009.  A letter has been received from Director NBPGR on 21.01.09 and stating that we have to again submit that the ETP/STP of our Residential Complex, Harbhajan Enclave is being maintained by the CPWD (Electrical Division).  Which is a Govt. of India establishment.  I have to also say that at the time of commissioning of the said ETP/STP no guarantee was demanded by the DPCC.  Now, after 5 years the DPCC is demanding and compelling to submit the Bank Guarantee of Rs. 1.00 lakh.  Since, we have been exempted in the beginning for submitting such Bank Guarantee, the NBPGR being the Govt. of India organization, may kindly exempted for the said guarantee of Rs. 1.00 lakh.
A letter has been received from Director NBPGR on 22.12.2008 in response to our letter dated 20.08.08 & 03.12.2008, stating as under:

we have been approaching the concerned authorities regarding the Adequacy report of ETP and Test Report for STP.  Due to some inconvenience we have not been submitted the reports.  As and when it is received, we will submit the same along with all the relevant documents and admissible fee as per your norms.

We have already requested that exemption may kindly be granted regarding Bank Guarantee of Rs. 1 Lakh.  Since NBPGR is an institute of ICAR an autonomous organization under Deptt. of Agriculture Research & Education (DARE), Min. of Agriculture.  The STP plant is being maintained by CPWD and the concern of DPCC has been intimated to CPWD.  To ensure that the situation does not arise again, I have instructed to Dr. Sidheshwar Prasad, Senior Scientist & Chairman, Electrical Works Committee, NBPGR, to monitor the functioning of CPWD at the STP.  

As per DPCC Analysis report, dated 09.01.2009 (sampling done on 16.12.2008), parameters BOD-52 mg/l, TSS- 136 mg/l & Phosphate-20.6 mg/l are exceeding the prescribed standard.
Decision of Consent Management Committee (MSW) in its meeting dated 23.01.2009:

Another reminder letter to be issued for not meeting the standards.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Haiderpur  Water Treatment Plant
Consent status:

Applied for consent to operate on 13.02.2008 & consent to Establish on 20.11.2008.

Decision of Committee taken on 19.10.2007

Unit may be ask for apply for consent to operate.  MS to direct lab officials of DPCC to do regular monthly lab testing for drinking water standards.
Action Taken Report

Letter for seeking consent to operate under Air & water Acts issued on 07.11.2007. No reply received so far.

As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of CMC (MSW) taken on 09.01.2008 :

Reminder letter may be issued.

Action taken report

Letter issued on 12.02.2008. Applied for consent to operate on 13.02.2008.

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of CMC (MSW) taken on 29.02.2008:

Member Secretary, DPCC to inspect & report in April CMC(MSW). 

Action taken report

Plant was inspected on 08-05-2008 by Member Secretary.

Decision of CMC (MSW) taken on 12.05.2008:

Ask the unit to apply for consent to Establish under Air & Water Act for both its old & new units. 

Action Taken Report

SE, DJB has submitted a letter on 07.07.08 that they have already applied on 19.12.07 for 200 MGD with consent fee of Rs. 109200/- i.e. with effect from 1993.  This include                        3 years for consent fee, 1 year for establishment fee and (17 years w.e.f. 1993 to 2009). The already submitted from is for establishment also so this may please be accepted for establishment for consent. Details of 16 MGD plant also submitted along with the reply.   

Decision of CMC (MSW) taken on 29.07. 2008:

Issue reminder letter for application for Consent to Establish. 

Action Taken Report

Letter issued to on 18.08.08 to the Superintendent Engineer, (WW-II), DJB . The unit has not submitted the application for consent to establish under Air and Water Act so far.  

As per DPCC analysis report dated 08-08-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

As per DPCC analysis report dated 10-09-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of CMC (MSW) taken on 10.10.2008:

Member Secretary, DPCC to issue reminder letter to the Member (Water) to apply for Consent to Establish.
Contd..2..
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Haiderpur  Water Treatment Plant

Action Taken Report

As decided by CMC, letter issued on 31.10.08.  
Applied for consent to operate on 13.02.2008 & Consent to Establish on 20.11.2008.

As per DPCC Analysis report, dated 13.10.08, all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 04.12.08, all parameters are within the prescribed standard.
Decision of CMC (MSW) taken on 05.12.2008:

No action.

Action Taken Report

As per DPCC Analysis report, dated 09.01.2009, parameters Ca (76 mg/l) found exceeding the prescribed limit of 75 mg/l.
Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Nangloi Water Treatment Plant
Consent status:

Not applied for consent under Air & Water Acts. 

Decision of Committee taken on 19.10.2007

Unit may be ask for apply for consent to operate.  MS to direct lab officials of DPCC to do regular monthly lab testing for drinking water standards.
Action Taken Report

Letter for seeking consent to operate under Air & water Acts issued on 07.11.2007. No reply received so far.

As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of CMC (MSW) taken on 09.01.2008 :

Reminder letter may be issued.

Action taken report

Letter issued on 12.02.2008. No reply received.

Decision of CMC (MSW) taken on 29.02.2008:

Issue  reminder letter for reply. 

Action Taken Report

Letter issued on 27.03.2008. Received application for consent to operate through Post on 29-4-2008 which is not complete(less consent fee, trade effluent generated but no treatment method mentioned), Demand Draft is yet to be detatched.

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of CMC (MSW) taken on 12.05.2008:

Ask the unit to apply for consent to Establish under Air & Water Act at Enquiry Counter of DPCC and application for Consent to operate to be returned back to the unit in original with fee draft. 

Action Taken Report

Letter issued on 03.06.08.  However, no reply/application for consent to establish has been received so far.

Decision of CMC (MSW) taken on 29.07. 2008:

Issue reminder letter to Member (Water), DJB for application for Consent to Establish. 

Action Taken Report

Letter issued to Member (Water), DJB on 20.08.08 with copy to Executive Engineer, DJB . The unit has submitted the application for consent to establish under Air and Water Act on 10.10.2008.  

As per DPCC analysis report dated 08-08-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

As per DPCC analysis report dated 10-09-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of CMC (MSW) taken on 10.10.2008:

Consent to Establish granted.

Action Taken Report

As decided by CMC, consent to establish issued on 03.11.08.  

As per DPCC Analysis report, dated 13.10.08, all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.12.08, all parameters are within the prescribed standard.
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Nangloi Water Treatment Plant
Decision of CMC (MSW) taken on 05.12.2008:

 No action

Action Taken Report

As per DPCC Analysis report, dated 09.01.2009, parameters Ca (76 mg/l) found exceeding the prescribed limit of 75 mg/l at outlet no. 1.
Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.
Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell
Wazirabad Water Treatment Plant

Consent status:

Not applied for consent under Air & Water Acts. 

Decision of Committee taken on 19.10.2007

Committee has also decided that other two units i.e Wazirabad Water Works & Chandrawal Water Works be also asked to apply for consent to operate under Air & Water Acts.

Action Taken Report

Letter for seeking consent to operate under Air & water Acts issued on 07.11.2007. No reply received so far.

As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of CMC (MSW) taken on 09.01.2008 :

Reminder letter may be issued.

Action taken report

Letter issued on 12.02.2008. No reply received.

Decision of CMC (MSW) taken on 29.02.2008:

Issue final reminder letter. 

Action Taken Report

Final reminder letter issued on 27.03.2008. Reply received on 11-4-2008 wherein it is mentioned that the matter is under process for submitting the application under Air& Water Act.

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of CMC (MSW) taken on 12.05.2008:

Ask the unit to apply for consent to Establish under Air & Water Act. 

Action Taken Report

EE, DJB has submitted reply on 09.06.08 along with copy of letter of SE,                    Chandrawal Water Works dated 28.05.08 in response to letter issued on 03.06.08 and stated that a request has already been  made to exempt this unit of DJB from any levies. Not applied for consent to establish so far.

Decision of CMC (MSW) taken on 29.07. 2008:

Issue reminder letter to Member (Water), DJB for application for Consent to Establish. 

Action Taken Report

Letter issued to Member (Water), DJB on 18.08.08 with copy to Superintendent Engineer, (WW-I), DJB . The unit has not submitted the application for consent to establish under Air and Water Act so far.  

As per DPCC analysis report dated 08-08-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

As per DPCC analysis report dated 10-09-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of CMC (MSW) taken on 10.10.2008:

Member Secretary, DPCC to issue reminder letter to the Member (Water) to apply for Consent to Establish.

Action Taken Report

As decided by CMC, letter issued on 31.10.08.  No reply received.

As per DPCC Analysis report, dated 13.10.08, all parameters are within the prescribed standard.

As per DPCC Analysis report, dated 04.12.08, parameters Ca is exceeding the prescribed standard. Contd..2..
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Wazirabad Water Treatment Plant

Decision of CMC (MSW) taken on 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.

Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

As per DPCC Analysis report, dated 09.01.2009, parameters Ca (84 mg/l) found exceeding the prescribed limit of 75 mg/l at outlet no. 1.
Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of Decmber 2008 and for other deficiencies.Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Chandrawal  Water Treatment Plant

Consent status:

Not applied for consent under Air & Water Acts. 

Decision of Committee taken on 19.10.2007

Committee has also decided that other two units i.e Wazirabad Water Works & Chandrawal Water Works be also asked to apply for consent to operate under Air & Water Acts.

Action Taken Report

Letter for seeking consent to operate under Air & water Acts issued on 07.11.2007. No reply received so far.

As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of CMC (MSW) taken on 09.01.2008 :

Reminder letter may be issued.

Action taken report

Letter issued on 12.02.2008. No reply received.

Decision of CMC (MSW) taken on 29.02.2008:

Issue final reminder letter. 

Action Taken Report

Letter issued on 27.03.2008. Reply not received.

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of CMC (MSW) taken on 12.05.2008:

Ask the unit to apply for consent to Establish under Air & Water Act. 

Action Taken Report

Letter issued on 03.06.08 however no reply/application of consent to establish has been receive so far.

Decision of CMC (MSW) taken on 29.07. 2008:

Issue reminder letter to Member (Water), DJB for application for Consent to Establish. 

Action Taken Report

Letter issued to Member (Water), DJB on 20.08.08 with copy to Superintendent Engineer, (WW-I), DJB . The unit has not submitted the application for consent to establish under Air and Water Act so far.  

As per DPCC analysis report dated 08-08-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

As per DPCC analysis report dated 10-09-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of CMC (MSW) taken on 10.10.2008:

Member Secretary, DPCC to issue reminder letter to the Member (Water) to apply for Consent to Establish.

Action Taken Report

As decided by CMC, letter issued on 31.10.08.  No reply received.

As per DPCC Analysis report, dated 13.10.08, all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.12.08, parameters Ca is exceeding the prescribed standard.
Contd..2..

..2..

Chandrawal  Water Treatment Plant

Decision of CMC (MSW) taken on 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.

Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

As per DPCC Analysis report, dated 09.01.2009, parameters Ca (84mg/l) found exceeding the prescribed limit of 75 mg/l.
Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of Decmber 2008 and for other deficiencies.Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Bhagirathi Water Treatment Plant   

Consent status:

Not applied for consent under Air & Water Acts. 

As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water).

Decision of CMC (MSW) taken on 09.01.2008 :

Issue letter for asking to apply for consent under Air & water Acts.

Action taken report

Letter issued on 13.02.2008. No reply received. 

Decision of CMC (MSW) taken on 29.02.2008:

Issue  reminder letter. 

Action Taken Report

Reminder letter issued on 27.03.2008 to apply for consent to operate. Submitted reply on 22.04.2008, that this office shall formally apply for consent shortly and also raise the query that the fee for Air Act is required to be paid or not. 

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of CMC (MSW) taken on 12.05.2008:

Ask the unit to apply for consent to Establish under Air & Water Act at Enquiry Counter of DPCC and clarify his point for fee. 

Action Taken Report

Letter issued on 03.06.08 to apply for consent to establish at inquiry counter of DPCC on prescribe format along with requisite fee and documents SE, DJB has submitted a letter on 16.07.08 an requested that necessary information/verification may be provided to this office enable this office to apply for consent.  This plant is operating since 1983 and the observation from DPCC to seek consent, has been received for the first time. Being new issue to this plant matter was discussed with DPCC an accordingly this office shall formally apply for consent shortly. Requested to provide as to how much fee is require to be paid and to know if the ‘fees’ are required for “Air-Act” also. As plant is noting engaged in aspects like Air Emission and have no DG Set.

Decision of CMC (MSW) taken on 29.07.2008:

Issue reminder letter to Member (Water), DJB for application for Consent to Establish. 

Action Taken Report

Letter issued to Member (Water), DJB on 18.08.08 with copy to Superintendent Engineer, (WW-III), DJB . The unit has not submitted the application for consent to establish under Air and Water Act so far.  

As per DPCC analysis report dated 08-08-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

As per DPCC analysis report dated 10-09-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.

Decision of CMC (MSW) taken on 10.10.2008:

Member Secretary, DPCC to issue reminder letter to the Member (Water) to apply for Consent to Establish.

Action Taken Report

As decided by CMC, letter issued on 31.10.08.  No reply received. No reply received.

As per DPCC Analysis report, dated 13.10.08, all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.12.08, all parameters are within the prescribed standard.
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Bhagirathi Water Treatment Plant   

Decision of CMC (MSW) taken on 05.12.2008:

A D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of November 2008 and for other deficiencies.

Action Taken Report

As decided by CMC, D.O. letter issued on 05.01.2009 to CEO, Delhi Jal Board.  No reply received so far.

Applied for consent to Establish on 16.12.2008.

As per DPCC Analysis report, dated 09.01.2009, all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

A reminder D.O. letter be sent to CEO, Delhi Jal Board by Chairman, DPCC to take action for complying with the norms w.r.t cases of STP & WTP which were found exceeding the prescribed limits/ non operational during the monitoring by DPCC in month of December 2008 and for other deficiencies. Put up in next CMC (MSW) meeting.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Sonia Vihar Water Treatment Plant
Consent status:

Consent to operate granted on 13.03.2007. 

Decision of Committee taken on 19.10.2007

Ask the unit to compliance report of consent condition. MS to direct lab officials of DPCC to do regular monthly lab testing for drinking water standards.  

Committee has also decided that  other two units i.e Wazirabad Water Works & Chandrawal Water Works be also asked to apply for consent to operate under Air & Water Acts.

Action Taken Report

Letter for seeking compliance report of consent to operate under Air & water Acts issued on 06.11.2007. 

Reply received on 02.01.2008.

As per DPCC analysis report dated 10.12.2007,water quality at outlet of treatment plant is meeting the desirable limits for drinking water except Hardness ( as CaCo3-360mg/l ).

Decision of CMC (MSW) taken on 09.01.2008 :

No action.

Action taken report

No action. 

Decision of CMC (MSW) taken on 29.02.2008:

No action. 

Action Taken Report

As per DPCC analysis report dated 09-04-2008, water quality at outlet of treatment plant is meeting the desirable limits for drinking water.
Decision of CMC (MSW) taken on 12.05.2008:

No action. 

Decision of CMC (MSW) taken on 29.07. 2008:

No action. 

Decision of CMC (MSW) taken on 10.10.2008:

No action.
Action Taken Report

As per DPCC Analysis report, dated 13.10.08, all parameters are within the prescribed standard.
As per DPCC Analysis report, dated 04.12.08, all parameters are within the prescribed standard.

Decision of CMC (MSW) taken on 05.12.2008:

No action.
Action Taken Report

As per DPCC Analysis report, dated 04.12.08, all parameters are within the prescribed standard.
Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

No action.
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Action taken/ Status after the meeting held on 12.05.08:

Comments received from Town & Country Planning Organization, UD forwarded to IL&FS on 03.06.08 and reminder has also been issued on 03.06.08.  No reply/comments received so far from others (i.e. DDA, CGWA and Air Force) and also from IL&FS. 

Decision of Consent Management Committee in its meeting dated 29.07.2008:
EE & both AEEs will ensure that the complete status report with all inputs and will be put up in the next meeting. 

Action taken/ Status after the meeting held on 29.07.08:

Reminder has also been issued to DDA, CGWA and Air Force on 14.08.08. CGWA has replied on 19.09.08 and requested for detail project report for there perusal and necessary action. Similarly,  DDA has asked for the details on 16.09.08 of the project.  IL&FS has informed on 29.09.08 in the case of compost plant at Okhla that they are in touch with CGWA and DDA for the clarification and comments by DPCC and it was also informed that they have provided required information about the project for their consideration and perusal. A letter was again issued on 06.10.08 to DDA, CGWA and Air force enclosing the detail project report and ILF&S.

Decision of CMC (MSW) in its meeting dated 10.10.2008:

Issue reminder to the three agencies to file reply & also comments from ILF&S. To be taken up in next CMC (MSW). 

Action taken/ Status after the meeting held on 10.10.08:

Letter issued on 27.10.2008.  A reply dated 21.11.08 has been received informing that they have taken up the matter with the concerned department and have been promised by them for a direct reply from their end, to DPCC, at an early date. 
· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

SEE, EE, AEE & Trainee to inspect and report. File to be submitted administratively with action taken report by 19.01.2009.

Action taken/ Status after the meeting held on 05.12.08:
The unit has been inspected on 15.01.09 and submitted the file of the unit administratively as per decision in CMC (MSW) meeting held on 05.12.08.
Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Put up administratively on file.

Chairman
  M. S.
        Member      
Prof. S.K Gupta

SEE

EE
AEE 

   DPCC
  DPCC      Env. Deptt.
Member (Acd. Inst)      
(MSW) 
MSWM Cell

Compost Plant of Municipal Corporation of Delhi at By Pass, Bhalswa, Delhi

Name of the agency: Nature Waste Management India Pvt. Ltd. MCD Compost Plant, G. T. Karnal Road, By Pass, Bhalswa, Delhi-110042

Status of Consent: 

Applied for Consent to establish under Green category on 26.09.08. 

Status of authorization under MSW Rules: 

Not applied for authorization under MSW Rules.

Particulars of the project: 

Compost Plant of Municipal Corporation of Delhi at G. T. Karnal Road, By Pass, Bhalswa, Delhi-110042

Details of the project: 

a. Processing technology is composting through open
air aerobic by Excel Technology.

b. Quantity of waste to be processed is 600 TPD.

c. Investment on the project is Rs.10 Crores.

d. Plot Area is 48552 sq m and Built up area- 16000 sq m 

e. Sanctioned Power Load – 125 KVA (K.No. 451099026136)

f. Water consumption for domestic is 500 LPD &  for processing  is 1,000 LPD (In summer months 3,000 LPD).

g. Quantity of domestic waste generated is Nil.

h. No trade effluent generated.  Only effluent from the rain water-re circulated to the waste heap.  

i. 82.5 KVA DG Set installed which is without acoustic enclosure and proper stack height. 

j. Agreement for sub-contractor is placed at (C/1-25).

Decision of CMC (MSW) in its meeting dated 10.10.2008:

Ask the unit to apply for consent under orange category and authorization under MSW Rules within a month. Call in November, 2008 CMC (MSW). 

Action taken/ Status after the meeting held on 10.10.08:

Letter issued on 03.11.2008.  The unit has submitted a reply on 26.11.08 informing that application for consent to establish under orange category and authorization will be submitted within a forthnight.  
· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

SEE, EE, AEE & Trainee to inspect and report. File to be submitted administratively with action taken report by 19.01.2009.

Action taken/ Status after the meeting held on 05.12.08:
The unit has been inspected on 15.01.09 and submitted the file of the unit administratively as per decision in CMC (MSW) meeting held on 05.12.08.
Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Put up administratively on file.
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Wholesale Flower market at IFC, Ghazipur, NH-24, New Delhi

Name of the agency: M/s Delhi Agriculture Marketing Board, 9, Institutional Area, Pankha Road, Janakpuri, New Delhi-110058.
Particulars of the project: Setting up Wholesale Flower market at IFC, Ghazipur, NH24, New Delhi.

Status of Consent: 

Applied for consent to establish under Air & Water Acts vided ID. No. 27420 dt. 19.09.08.
Details of the project: 

a. Proposed activities is setting up wholesale flower market and multilevel parking. 

b. Proposed Investment on the project is Rs.116.89 crores.

c. Total Plot Area is 150866.22 sq m
d. Built up area- 103049.84 sq m.
e. Sanctioned Power Load /power required– 4000 KW.
f. Proposed to be commissioned from December, 2008.

g. No of workers: 

a) During construction phase – 100 b) During operational phase-   25

h. Water consumption:

Domestic – 154.5 KLD, 
Industrial cooling - 52 KLD, 
processing   - 50 KLD,
Other (Gardening) – 108 KLD

i. Quantity of domestic waste generated is 136 KLD and Industrial is Nil.
j. Proposed Sewage Treatment Plant of 150 KLD with primary and secondary treatment and treated domestic effluent will be partly utilized for green belt, DG. Set and AC Cooling and rest will be discharge into sewerage system.

k. Sludge Generating from STP will be used as manure for gardening purpose/ Sold as per standard practices.

l. DG Sets proposed to be installed – 3 X 1250 KVA + 1 X 1650 KVA with acoustic enclosure.

m. Perpetual lease by DDA for this land is enclosed.  
n. As per application unit will be taken authorization under Hazardous Waste Rules for storage of hazardous waste (used oil from DG Set) during operational phase. 
Remarks:

As per the provisions of EIA notification dated 14.09.06 the following construction projects are to be required Environmental Clearance from MoEF:

c) Building and Construction Projects having built up area ≥ 20000 sqm and < 150000 sqm of built up area. 

d) Townships and Area Development Projects having covering an area ≥ 50 ha and or built up area ≥150000 sqm.   

· Decision of Consent Management Committee (MSW) its meeting dated 05.12.2008:

Member Secretary, DPCC to write to VC, DAMB to seek immediate EIA clearance enclosing a copy of the EIA notification.  Meanwhile, an inspection may also be carried out based on the Consent to Establish.

Action taken/ Status after the meeting held on 05.12.08:

· Letter issued on 29.12.08. As per letter dated 11.12.08 of the unit, they have applied for Environmental Clearance about two months back. They requested for EC as well as CTE at the earliest to enable to start the project & complete before Commonwealth Games.

Contd…2

Wholesale Flower market at IFC, Ghazipur, NH-24, New Delhi
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· The site of the unit was inspected on 07.01.09. Following are the observations:

a. No excavation/ construction activity has been started for this project.

b. As informed they are applying again for CTE and EC with revised proposal for flower, fruit and vegetable market.

c. w.r.t. fruit and vegetable market, construction of 8 blocks out of 12 blocks is almost completed.
Decision of Consent Management Committee (MSW) its meeting dated 23.01.2009:

Ask to apply for CTE for the revised project for Flowers, Fruit and Vegetable market
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	S. No.
	Name of Unit
	Applicant :

	1
	Modern Poultry & Egg market                                           at Ghazipur, New Delhi.      

Applicant :M/s Delhi Agriculture Marketing Board,                       9, Institutional Area, Pankha Road, Janakpuri,                         New Delhi-110058.
	M/s Delhi Agriculture Marketing Board, 9, Institutional Area, Pankha Road, Janakpuri, New Delhi-110058.

	2
	Municipal Waste Complex                                                                at Gazipur Bio-gas Plant Site

Applicant :M/s New Delhi Waste Processing Company Ltd.
	M/s New Delhi Waste Processing Company Ltd.

	3
	Development of Engineered Landfill site                            at Jaitpur/Tajpur

Applicant : Municipal Corporation of Delhi 
	Municipal Corporation of Delhi 

	4
	Setting up of Integrated Waste Complex                                  at NDMC Plant Site,                                          Sukhdev vihar,Okhla

Applicant : New Delhi Municipal Council.                                  (M/s Timarpur-Okhla Waste Management Company Private Ltd).  
	New Delhi Municipal Council. (M/s Timarpur-Okhla Waste Management Company Private Ltd).  

	5
	Integrated Municipal Solid Waste Complex                            at Timarpur  

Applicant : New Delhi Municipal Council.                                 (M/s Timarpur-Okhla Waste Management Company Private Ltd).  
	New Delhi Municipal Council. (M/s Timarpur-Okhla Waste Management Company Private Ltd).  

	6
	Delhi Food  Processing Complex (Meat), Slaughter House at Ghazipur, Delhi 

Applicant : Municipal Corporation of Delhi
	Municipal Corporation of Delhi

	7
	Revival of the Compost Plant of Municipal Corporation of Delhi at Okhla, Delhi.

Applicant : Municipal Corporation of Delhi and IL & FS 
	Municipal Corporation of Delhi and IL & FS 

	8
	Upgradation of the A.P.M.C. Compost Plant                        at Tikri Khurd/ Khampur,                                              G.T. Karnal Road, Delhi-40.

Applicant :Spiral Services, New Sabzi Mandi, Azad Pur, Delhi-33.
	Spiral Services, New Sabzi Mandi, Azad Pur, Delhi-33.

	9
	Compost Plant of Municipal Corp. of Delhi                        at Bypass, Bhalswa, Delhi

Applicant : Natural Waste Management India Pvt. Ltd.
	Natural Waste Management India Pvt. Ltd.

	S. No. 
	Name of STP
	Installed capacity

	1
	Dr. Sen Nursing Home
	2.2 MGD

	2
	Delhi Gate
	2.2 MGD

	3
	Kondli Phase-I
	10 MGD

	4
	Kondli Phase-II
	25 MGD

	5
	Kondli Phase-III
	10 MGD

	6
	Oxidation pond (Nehru Vihar)
	6 MGD

	7
	Kesho pur (Plant no. I & II)
	60 MGD

	8
	Mehrauli
	5 MGD

	9
	Yamuna Vihar Ph-I
	10 MGD

	10
	Yamuna Vihar Ph-II
	10 MGD

	11
	Rithala Ph-I
	40 MGD

	12
	Rithala Ph-II
	40 MGD

	13
	Pappan kalan
	20 MGD

	14
	Najafgarh
	5 MGD

	15
	Nilothi
	40 MGD

	16
	Rohini
	15 MGD

	17
	Coronation Pillar 
	40 (4 x 10) MGD

	18
	Vasant Kunj (Plant 1 & 2)
	5.2 MGD

	19
	Narela
	10 MGD

	20
	Okhla (Plant -I, II, III & IV)
	124  MGD (12+30+37+45)

	21
	Okhla (Plant -V)
	16 MGD

	22
	C Dot Campus (Mehrauli)
	125 kLD

	23
	Bakarwala
	3 MGD

	24
	Molarband
	3 MGD

	25
	Holambi
	2 MGD

	26
	Tikri khurd
	2 MGD

	27
	Gitorni
	5 MGD

	28
	Pusa Campus
	29 MGD

	S. No.
	Name 

	1
	Haiderpur Water Treatment Plant

	2
	Nangloi Water Treatment Plant

	3
	Wazirabad Water Treatment Plant

	4
	Chandrawal Water Treatment Plant

	5
	Bhagirathi Water Treatment Plant

	6
	Sonia Vihar Water Treatment Plant

	Agenda No.
	
	Ageda item

	
	
	

	7
	
	Implementation of use of beneficiated coal in Thermal Power Plants-rg.

	8
	
	MCD landfill sites, Dhalaos and segregation of Municipal Solid Waste material including plastic waste.

	9
	
	Complaint regarding public nuisance causing environment degradation inside the district park (DDA), Brij Vihar, Pitampura, Delhi.

	10
	
	Representation of Confederation of Delhi Industries and CETP Societies regarding Reutilization of treated effluent from CETPs.

	S. No.
	Name of Power Plant
	Address

	1
	NTPC, Badarpur Thermal Power Station
	Badarpur

	2
	I P Thermal Power Station
	IP Estate

	3
	Rajghat Power Station
	Rajghat

	4
	Pragati Power Station
	ITO

	5
	I. P. Gas Turbine Power Plant
	ITO

	6
	Pragati Power Station
	Bawana

	7
	108 MW Combined Cycle Power Plant BY NDPL
	Sector-11, Rohini, Delhi 

	
	
	

	S. No.
	Name of Unit
	Applicant 

	1
	Modern Poultry & Egg market at Ghazipur, New Delhi.
	M/s Delhi Agriculture Marketing Board, 9, Institutional Area, Pankha Road, Janakpuri, New Delhi-110058.

	2
	Municipal Waste Complex at Gazipur Bio-gas Plant Site
	M/s New Delhi Waste Processing Company Ltd.

	3
	Development of Engineered Landfill site at Jaitpur/Tajpur
	Municipal Corporation of Delhi 

	4
	Setting up of Integrated Waste Complex at NDMC Plant Site, Sukhdev vihar,Okhla 
	New Delhi Municipal Council. (M/s Timarpur-Okhla Waste Management Company Private Ltd).  

	5
	Integrated Municipal Solid Waste Complex at Timarpur  
	New Delhi Municipal Council. (M/s Timarpur-Okhla Waste Management Company Private Ltd).  

	6
	Delhi Food  Processing Complex (Meat), Slaughter House at Ghazipur, Delhi 
	Municipal Corporation of Delhi

	7
	Revival of the Compost Plant of Municipal Corporation of Delhi at Okhla, Delhi.
	Municipal Corporation of Delhi and IL & FS 

	8
	Upgradation of the A.P.M.C. Compost Plant at Tikri Khurd/ Khampur, G.T. Karnal Road, Delhi-40.
	Spiral Services, New Sabzi Mandi, Azad Pur, Delhi-33.

	9
	Compost Plant of Municipal Corporation of Delhi at Bypass, Bhalswa, Delhi
	Natural Waste Management India Pvt. Ltd.

	10
	Setting up Wholesale Flower Market  and Multilevel Parking,  at IFC, Ghazipur, NH-24,               New Delhi.
	M/s Delhi Agriculture Marketing Board, 9, Institutional Area, Pankha Road, Janakpuri, New Delhi-110058.


	S. No.
	Name of CETP
	Installed Capacity
	Operating Agency

	1
	Jhilmil CETP
	16.8 MLD
	CETP Society

	2
	GTK Road CETP
	6 MLD
	CETP Society

	3
	Lawrence Road CETP
	12 MLD
	DSIDC

	4
	Badli CETP
	12 MLD
	CETP Society

	5
	Mayapuri CETP
	12 MLD
	CETP Society

	6
	Mangolpuri CETP
	2.4 MLD
	CETP Society

	7
	Wazirpur CETP
	24 MLD
	CETP Society

	8
	DSIDC & Udyog Nagar CETP
	12 MLD
	CETP Society

	9
	SMA CETP
	12 MLD
	CETP Society

	10
	Okhla Industrial Area  CETP
	24 MLD
	CETP Society

	11
	Narela CETP
	22.5 MLD
	DSIDC

	12
	Udyog Vihar, (Bawana Industrial Area) CETP
	35 MLD
	Under construction by DSIIDC

	13
	Najafgarh road CETP
	9.6 MLD
	Construction suspended

	14
	Naraina CETP
	21.6 MLD
	Under construction by DSIIDC

	15
	Okhla Estate CETP
	1.2 MLD
	Kept in abeyance by EPCA

	16
	Anand Parbat CETP
	24 MLD
	Kept in abeyance by EPCA
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