Inspections carried out as per Hon’ble NGT Court for different Rain Water Harvesting System installed by various Departments/ Authorities/Agencies as per petition.
	Sr.  No 
	Name & Address of the site
	Inspecting officials and Representative Authority
	RWHS inspected
	Observation & Remarks

	01.
	DJB(A) (as per photograph attached by complainant in petetion)

Harvesting Bore well, near G-1916, shop no. 2, JJ colony, shop no. 2, Tigriopp- vayusenabad, MB Road, Delhi
	Inspecting officials:

Sh.K.Kumar, EE (DPCC CMC-III)

Sh.M.K.Garg-

Scientist (CGWA)

Sh.Nawab Ahmed, (AE,DJB)

Sh. Mohit Kumar,

 ( JE,DJB)

Representative Authority:  Not available
	01
	During inspection it is observed that one bore well is existing in a Park opp. to Vayusenabad near SeemaSuraksha Training. School.
- It seems that structure is not properly designed and maintained (only bore well is seems at the site).
- Nobody told this harvesting bore pertains to which Authority.

-As per photograph enclosed by the complainant it pertains to DJB.

	
	(B) VasantKunj, Pkt- I, Sector-D

(DJB)


	Inspecting officials:

Sh.K.Kumar, EE (DPCC CMC-III)

Sh. SiddharthGautam , EE DPCC(CMC-1)

Sh.Nawab Ahmed, (AE,DJB)

Sh. Mohit Kumar,

 ( JE,DJB)

Representative Authority:  Not available


	01
	During inspection, following was observed:

RWHS  installed in the campus/premises near the main gate of the pocket, 1, Sector-D.  The chamber was silted and maintenance is required, slotted pipe observed above the filter media of the RWHS.

Only recharge bore is visible  above the ground and seems non functional

	
	(C) Tube well No.6, JJR colony, Khanpur Delhi. (DJB)


	Inspecting officials:

Sh.K.Kumar, EE (DPCC CMC-III)

Sh.M.K.Garg-Scientist (CGWA) 

Sh.Nawab Ahmed, (AE,DJB)

Sh. Mohit Kumar,

 ( JE,DJB)

Representative Authority:Sh. Vijender Kumar

	01
	During inspection, following was observed :

Only recharge bore was visible  above the ground and seems non functional


	
	(D) Saket D Block overhead tank behind XEN (E&M) (DJB)


	Inspecting officials:

Sh.K.Kumar, EE (DPCC CMC-III)

Sh.Nawab Ahmed, (AE,DJB)

Sh. Mohit Kumar,

 ( JE,DJB)

Representative Authority:  Not available


	01
	During inspection it is observed that:-

1. The chamber is silted and maintenance required.

2. Slotter pipe observed above the filter media.

3. This site pertains to DJB.



	
	(D) Water Engineering GK-I

(DJB)


	Inspecting officials:

Sh.K.Kumar, EE (DPCC CMC-III)

Sh.Nawab Ahmed, (AE,DJB)

Sh. Mohit Kumar,

 ( JE,DJB)

Representative Authority:  Sh. Vijendra Kumar JE(DJB)
	01
	      During inspection, following was observed :

1. Filter media was silted in the chamber and recharge bore pipe was slotted above from the filter media.

      2. RWHS requires maintenance



	02.
	DMRC(A)Chhatarpur Metro station to Arjungarh (Ayanagar metro station)
	 Inspecting officials:

Sh.K.Kumar, EE DPCC (CMC-III)

Sh.M.K.Garg-Scientist (CGWA)

D.Joshi, AE, (DJB)

Representative Authority:
Sh.Vijay Singh, JE, Civil
	06
	Inspections of the DMRC sites Chhaterpur to AyaNagar  belt conducted and it is observed that :-
1.Chhatarpur Metro Station: -
    - Two Nos. of RWHS provided.
    - The RWHS installed between pillar no. 21 and 22 seems non functional, filled with garbage, bore well not exist, no over flow pipe provided & Cover of the pit was found broken.
    - The another RWHS provided between Pillar No. 22F & 23F bore well not visible, garbage observed in chamber, convence system was not proper for the collection of rain water in re-charge pit. 

2. Sultanpur Depot: -
    - Two nos. of RWHS bore well existing at site but proper filter chamber is not available. However the representative of DMRC Mr. Vijay Singh says on apprised that modular system exists around the bore well and same is filled up with earth. Due to this existence of Modular system cannot be verified.
3. Ghitorini :-
    - One no. Of RWHS of 8 dia bore well exist. The filter chamber is not properly cleaned no over flow      arrangement available.
4. ArjunGarh (Aya Nagar):-
    - As per the statement of representative of DMRC one no. RWHS exist but the same is occupied by the hotel Claremont. Due to this, the same is not visible.


	
	DMRC(B)  Metro Station Pillar No. 187B & 187 A
	Inspecting officials:

Sh.K.Kumar, EE (DPCC CMC-III)

Sh.Nawab Ahmed, (AE,DJB)

Sh. Mohit Kumar,

 ( JE,DJB)

Representative Authority:
Sh.Vijay Singh, JE, Civil
	01/129
	During inspection, following was  observed  :

1. RWHS are installed in between two pillars alternatively.

2. Total structures are 129. Qutab Metro station to pillar No. P-224 after ArjunGarh metro station falls  in Delhi region only (List of 129 RWHS attached) 

3. Filter media observed in RWHS.

4. No bore well provided in all the RWHS as reported by Sh. Vijay Singh, JE Civil. No bore well  seen in the said pit which was inspected (in between pillar no 187B & 187 A).




	03.
	NHAI/PWD, between Pillar no 177 & 178, Arjungarh metro station
	Inspecting officials:

Sh.K.Kumar, EE (DPCC CMC-III)

Sh.Nawab Ahmed, (AE,DJB)

Sh. Mohit Kumar,

 ( JE,DJB)

Representative Authority:
Mukammal Khan (AE PWD)
	1/100
	During inspection, following was observed  :

1. RWHS are installed at Chhatarpur metro station to ArjunGarh metro station on both side of the main road  (distance about 75 meter each  approximately.

2. Heavy sewage observed nearby RWHS.

3. Garbage also observed in the pit.

4.  RWHS is non-functional.

5. Near Metro Pillar No.115 Waste water flows through the drain in which RWHS have been   provided by NHAI/PWD. Waste water flowing nearGhitorni Metro station & petrol pump of IOC mixes with storm water drain connected to RWHs and enter NBCC campus trough Metro Pillar No. 95 and 96. 

6. Waste water/public sewage also discharged in storm water drain & RWHS are also provided in the same.

	04.
	PWD Sites, MB Road, Bandarwala park, New Delhi
	 Inspecting officials:

Sh.K.Kumar, EE (DPCC CMC-III)

Sh.M.K.Garg-

Scientist (CGWA)

Sh.Nawab Ahmed, (AE,DJB)

Sh. Mohit Kumar,

 ( JE,DJB)

Representative Authority:  Not available


	03
	Structure No. I
During Inspection it was observed that:-
1. No bore well observed in the structure.
2. Garbage observed in the pit.
3. It seems pits are non-functional.
4. Inlet not observed.
5. It was reported that these trenches are not made for Rain Water Harvesting purpose but these two trenches were made for fountain during common wealth games and same are being used as garbage pits. 

Structure No. II 
One Rain Water Harvesting structure exists at a distance of 100m from the above trench opposite bus stand & Air force station.
1. Bore well observed at the earth level in damaged condition.
2. Found filled with garbage & coconut shell.
3. Not working condition.
4. It is used as a garbage/ waste pit.

	05.
	PushpVihar, Maintenance Division, CPWD, Room No.120, Ist Floor, Pushpa, Bhawan, New Delhi.
.
	Inspecting officials:

Sh.K.Kumar, EE (CMC-III)

Mr. Harish Chander (EE,DJB)

,Representative Authority:

 Sh. R.K. Singh (EE, PVMD),

Sector-4 (Mr. BhagwanRai&Mr.ShailendraMeena),

Sh. R.K. Singh (EE, PVMD), 
Sector-7 (Mr.Bharti),

Sector-1 (Mr.Chop Singh Sh. Swapnil ,JEE) AEE &Sangode),  
Sector-3(Mr. Ranjeet

 Singh, (AE III),
Sector-5 (Mr. BhagwanRai&Mr.ShailendraMeena),
	16+22=38
	During inspection, following were observed:

RWHs pits were inspected for Sector-IV PushpVihar observed that

-Many of the bore pipes are slotted above from the filter media.
-Post monsoon silt was observed in all the rain water harvesting pits (16 nos)
-RWHs are maintained but annually maintenance is required.

	
	
	
	
	-RWHs are constructed as per typical drawing of rain water harvesting manual issued by CPWD.
-Details of rain water harvesting system are enclosed herewith for sector IV 16 NOs of pits.


	06.
	Forest Department
	Inspecting Officials:
O/O the Dy.Conservator Forest (South)
	01
	Inspection conducted & Report Enclosed At ANNEXURE-III

	07.
	All India of Medical Sciences, East Ansari Nagar, New Delhi.
	Inspecting Officials:

Sh.K.Kumar, EE (CMC-III)

Sh.S.K.Goel EE (CMC-III)
Sh. Sanjay Vats, EE (WMC-I)

Sh. Jyoti Kumar (Scientist-C, CGWA)

Representative Authority:

Mr.Bhaskar (Ex. Engineer).


	23
	During inspection, following were observed:

Inspection of the AIIMS hospital was carried out in respect of RWH system as per Hon’ble NGT order.

· Total no. of Harvesting System installed 23.

· Two nos are found dead due to Metro Work as reported.

· As informed the design of RWH pits were wetted by CGWA, New Delhi.

· Deficiencies observed:

· Post monsoon silt observed in almost all RWHS



	08.
	Safdarjung Hospital, New Delhi-29
	Inspecting Officials:

Sh.K.Kumar, EE (CMC-III) 

Sh. Sanjay Vats EE (WMC-I)

Sh.Jyoti Kumar, Scientist-C, (CGWA)

Representative Authority :

Sh. V.K. Singh Ex. Engineer (CPWD)

Sh. MadanLal,AE (CPWD) 
	24
	During inspection, following were observed:

Inspection of the Safdarjung hospital was carried out in respect by RWH system as per Hon'ble NGT order:

· Total no of system are 24 & out of them 21 are working.

· Three nos. are dead due to construction of a new building in the hospital.

· The RWH pit has been maintained as conveyed by Sh. V.K.SinghEx.Eng. & Sh. MadanLal, AEE.,

The RWH pits were inspected & garbage dump, construction Malba observed in many pits & post monsoon silt was observed.

General Comments:-
a. Out of 24 RWHS three no of system are disconnected due to construction and rest of 21 RWHS are installed in the hospital are not satisfactorily & properly constructed & maintained. All these Rain Water Harvesting Pits & soak pit have installed in the hospital without any approved design from the Authority. 



	09.
	(A) NDMC DTEA Sr. Sec. School MandirMarg NP Boys Sr. Sec School


	DPCC Officials:

Sh. K.Kumar, EE (CMC-III)

Sh. SiddharthGautam , EE DPCC(CMC-1)

Sh. AK Gupta (SE DJB)

Sh. Jyoti Kumar 

Scientist (CGWA)

Representative of Authority:

Mr.Khan, AE (Civil)


	01
	During inspection, following was observed :

1. One RWHS observed in front of NP Boys Sr. School in non- functional condition.

2. It was observed that RWHS filled with Solid waste material and is defunct condition.

3. Inlet pipe to the recharge trench not observed. Agency maintaining the RWHS is to ensure that rain water run off is diverted to the recharge trench for its utilization.

4. Mr. M Khan, EE R-S NDMC is present during the inspection and informed that the said RWHS is not maintained by them. He has verbally advised to check up in his department to ascertain the section who maintaining the RWHS for necessary remedial action



	
	(B)NDMC Lodhi Garden, Lodhi Road 
	DPCC Officials:

Sh. K.Kumar, EE DPCC (CMC-III)

Sh. SiddharthGautam , EE DPCC(CMC-1)
Sh. AK Gupta (SE DJB)

Sh. Jyoti Kumar 

Scientist (CGWA)

Representative of Authority:

Sh. Vijay Kumar Meena, JE (Civil)


	09
	During inspection, following was observed: 

1. Lodhi garden is having 09 Nos. of RWHS, 07 structures are functional but requires pre-monsoon maintenance and cleaning.

2. 02 Nos. of RWHS arrangements are required to be made to bring Rain Water run off in the pits for their proper utilization.

	
	(C) NDMC: (A) York Palace round about Motilal Nehru Marg
	DPCC Officials:

Sh. K.Kumar, EE DPCC(CMC-1II)

Sh. SiddharthGautam , EE DPCC(CMC-1)
Sh. D Joshi (AE DJB)

Representative of Authority:

Sh. Vijay Kumar Meena, JE (Civil)


	04
	During inspection, following was observed  :

1. Four nos. of RWHS provided in circular park.
2. All RWHS found well maintained.

All RWHS provided with two bore well each.

	10.
	DSIIDC Complex, Ph-I, Okhla Ind. Area, Ph-1, New Delhi.
	DPCC Officials:

Sh. K.Kumar, EE (CMC-III)

Sh.S.K.Goel,EE (CMC-III)
	01
	During inspection, following were observed:

1) One No of RWH pit is found installed at left hand side of main gate.
2) Found covered with MS bar jali. The pit is found filled with post monsoon silt & paper/polythene.
3) As reported by Chowkidar the pit is required to be maintained. At present the pit is not maintained as there is no    use of premises by DSIIDC since last 1& 1/2  years.
4) Only a post office and police chowki is running at the site and most of the premisesis lying vacant.

	11.
	Military Engineering Services:

(A)VayuSena Bad 7 BRD, 7 Base Repair Depot, MB Road, Air force station, New Delhi
	Inspecting officials:

Sh.K.Kumar, EE (DPCC CMC-III)

Sh.M.K.Garg-

Scientist (CGWA)

Sh.Nawab Ahmed, (AE,DJB)

Sh. Mohit Kumar,

 ( JE,DJB)

Representative Authority:

Sh.Pradeep Singh, JE (Civil)
	07
	During inspection it is observed that there are 7 rainwater harvesting structures as detailed below:-

These three RWHS Pits inspected and found satisfactory. Post-monsoon silt is deposited in the RWH structures need annual maintenance:-
1. Logistic (E)
2. Logistic (W)
3. Old Tetra School

These four sites are in the technical area. As reported these structures are working satisfactorily. Could not be inspected :-
4. Production Wing-I
5. Production Wing-III
6. Site-1
7. Spider

	
	(B). Vayusenabad, Air force station, vayusenabaddelhi, MB Road, Delhi
	 Inspecting officials:

Sh.K.Kumar, EE (DPCC CMC-III)

Sh.M.K.Garg-

Scientist (CGWA)

Sh.Nawab Ahmed, (AE,DJB)

Sh. Mohit Kumar,

 ( JE,DJB)

Representative Authority:

Sh.RajeshChauhan, JE,Civil


	05
	During inspection it is observed that there are five Nos. of Pits in the premises namely :-
1. Hereby GyanMandir School
2. Air Billete
3. Shiv Mandir
4. Children Park (Air man institute)
5. In front of CSD

All the above RWHS were inspected found satisfactory, post monsoon silt was observed need maintenance (annual).

	12.
	MCD (primary School), Aya Nagar, New Delhi-110047
	Inspecting officials:

Sh.K.Kumar, EE (DPCC CMC-III)

Representative Authority:

Smt. Achla Bajaj (2nd shift incharge)
	02
	During inspection, following was observed:

1. Two Nos. of RWHS installed found non- functional.

2. Conveyance system is not proper.

3. Garbage and other waste (plastic) observed in the RWHS. 

	13.
	DDA: (A) Mega Housing Project (1904) D-6, VasantKunj


	Inspecting  Officials

Mr.K.Kumar,EE,DPCC

Mr.SiddarthGautam,EE,DPCC

Representative Authority:

Mr.SarvjeetYadav,AE

Mr. S.K. Sharma,EE

Mr. Y.A. Bansal,AE


	29
	During inspection, following was observed:

1. In the projecttotal nos.of  RWHSare 27.
2. Post monsoon silt observed in all the pit during inspection.

3. Near N/1UGR RWHS water observed in the pit indicating that the pit is choked.

4. At periphery road, two no. of RWHS found temporarily re-developed and found non-functional.

5. Maintenance required in all pits.

	14.
	IOC, Lotus Automobiles, MG Road New Delhi
	Inspecting officials:

Sh.K.Kumar, EE (CMC-III)

Sh.Nawab Ahmed, (AE,DJB)

Sh. Mohit Kumar,

 ( JE,DJB)

Representative Authority:

Sh. Jogendra Singh(GM Service Station)

	01
	During inspection, following was observed :
1. RWHS provided in the premises found non-functional.

2. Waste/garbage observed in the pit

3. Bore well not seen.

	15.
	Saket City Hospital (A unit of GM Modi Hospital), MandirMarg press Enclave Road, New Delhi.
	Inspecting officials:

Sh.K.Kumar, EE (CMC-III)
Sh.Shyam Sunder, EE (WMC-I) 

Sh.A.K.Verma,SEE (DJB)
Sh.Jyoti Kumar, 

Scientist-C, (CGWA)

Representative Authority:

Sh.MahipalBhannot(GM)

Sh.SubhasChander (HE)


	03
	During inspection, following were observed:
1. RWHs of the hospital is partially constructed, RWH structures have waste water & not functioning properly.

2. Health Care Establishment authorities have to submit layout drawings of the hospital premises/premise showing type of catchment & their area, alignment of rainwater conveyance system showing locations of rain water harvesting structures. Detailed design/drawing of RWH structures is also required to be submitted

3Settiling tank not constructed.

4 Recharge pit (Circular) does not have recharge bore & filter media

5 Settling tank at recharge pit (circular) are filled with waste water 

6 Rain water conveyance system connected to this structure is not clear on the ground & is not well designed.




	16.
	M/s Batra Hospital, Plot no 1, Tuglakabad, Institutional area, Delhi
	Inspecting Officials:

Sh.K.Kumar, EE (CMC-III)

Shyam Sunder, EE (WMC-I)

Sh. Jyoti kumar (Scientist-C, CGWA), A.K.Verma SEE,DJB), 

Dr. Chetna (Scientist, Dept. of Environment)

Representative  Authority:

Dr. Naveen Kumar (Addl.MS), 


	     10
	During inspection, following were observed:

1. Rain Water Harvesting (RWH) System has been designed by Centre for Science & Environment. 
2. RWH system consists of 10 nos recharge structure for the purpose of ground water recharge. Each structure has inlet chamber, which may also be serving as a small settling pit prior to filtration chamber. All filtration chamber have recharge bore consist of PVC pipe bore. All the RWH structure is connected to the rain water conveyance system.
3 As per the drawing shown of the installed filtration chamber have two layers of filter media i.e. gravel & coarse sand.
4. The RWH conveyance systems was found silted up & needs proper maintenance.
5. Inlet pipe from the inlet cum settling chambers to the recharging pits found to be completely choked in six no’s recharging structures.
6. No waste water was found in any of the RWH filtration chambers. Top layers of the filter media found to be recently replaced.
7. Over flow pipes from recharge structure (No. 1 & 2 near A block) found to be connected in the main holes which reported by the HCE Authorities is/are the part of a strom water line to the MCD drain outside the hospital premises. Man holes of the stated strom water lines were found to be filled with waste water, it was observed that waste water from the hospital laundry was being discharged into the said storm water drain. During monsoon this waste water may mix with the rain water & may contaminate the ground water.
8. Hospitals Authorities to immediately disconnect the discharge of the laundry waste water into the storm
 water drain & to make its proper disposal after treatment.

9. As deficiencies observed during inspection in respect to bio-medical waste. Photocopy of inspection report has been send to waste management cell for further necessary action at their end




	17.
	A)Delhi Sainik co-op Housing Building Society Ltd. ((Farm Wing) Near Gate no. 1, Sainik Farm
	 Inspecting officials:

Sh.K.Kumar, EE (CMC-III)

Sh.M.K.Garg-Scientist (CGWA)

D.Joshi, AE, (DJB)

Representative Authority: Not available
	10
	During visit, office of the Society was closed and Sh. Jagpal, Manager of the Society was telephonically contacted.
As reported these are four tube wells and RWHS are installed individually by the residents. Nos. of RWHS not exactly known/ Shown. These are three more residents societies in the Sainik Farm area, could not be contacted due to evening house as office may be close.

	
	(B).    Western Avenue Reidents Welfare Associates (Regd.), W-13B/15, MB Road, Western Avenue, New Delhi
	 Inspecting officials:

Sh.K.Kumar, EE (CMC-III)

Sh.M.K.Garg-Scientist (CGWA)

D.Joshi, AE, (DJB)

Representative Authority:

Sh.M.C.Jain


	---
	The details of RWH Systems are as follows:-
- 1 & 2 near the houses of Mr. N.C. Jain: - The structures are small constructed without technical guidance and permission. The Chamber is not designed properly. At present it is in working condition.
- 10 RWH structures have been seen along the road side These have also been constructed in similar design but without any technical guidance and permission. Reported and observed, these structures are in working condition and are being annual maintained.
- As reported all other structures are of similar type and have not been visited due to evening (sunset) 6:15 P.M. 

	18
	Irrigation & Flood Control Department
	Inspecting Official

Mr.K.Kumar

Representative Authority

Mr. S.C. Rohilla (JE)
	06
	During inspection, following was observed:

1. All RWHS non-functional & found choked.

2. Rain water during inspection was stored near SangamAppartment (nearby pit) indicating non-functional RWH.
3.   Improper Conveyance system.


Inspections of three agencies carried for Rain Water Harvesting System which are not named in the applicationfiled by the applicant.
	01.
	JPN Apex Trauma Centre (AIIMS), Ring Road.


	Inspecting Official

Sh.K.Kumar (EE,DPCC), Sh. Jyotikumar (Scientist-C, CGWA), A.K.Verma (SEE,DJB)
Representative Authority
Mohd. Naeem JE (Civil),     
	16
	1. Sixteen nos Ground water Recharge structures consisting of only filtration chambers only  with recharge bore.
2. Trauma centre is reported to have surface storage of rain water near gali no having capacity of 2.83. Surface storage in used for gardening puposes. Excess Rain water during heavy rains in monsoons reported to be pumped out in public authority drainage system
The details of the pits & observation  in respect of  of recharge pits are as follows:
A) Dr.Hostal - 3 pits + 1 pit (Filtration chamber)
B) Park (behind Dr.Hostal left hand site)
C) Main park 3 nos. recharge pit.
D) Peepalwala park 3 Nos recharge pit (cleaning required)
E) Recharge pit (near exit pump)
F) Recharge pit (Near jal board meter & parking)
G) Recharge pit (SBI ATM) filled with stagnant water of road washing.
H) recharge pit in park near gali no 2 filled with water.
-Out of the sixteen recharge pits thirteen nos. were found to be in good condition with little bit cleaning of floating materials. No stagnant water was foumd in these pits.
-Three recharge pits were found filled with stagnant water, indicating taht these pit are not functioning properly. 
Recharge bore could not be seen due to filled up water. 
Filled up water doesnotapppear to be waste water because no foul odour was felt. 
Hospital authority with identity the source of water found in the pit.



	02.
	Rockland Hos[ital, B-33-34, qutab Institutional Areea, Delhi


	Inspecting Official

Sh.K.Kumar (EE,DPCC), Sanjay Vats (EE,DPCC), A.K.Verma (SEE,DJB)
Representative Authority

Sarvesh Kumar (Head Maintenance),

	01
	A'- 
- Mr.Sarvesh informed that hospital has one rain water harvesting system for the purpose of ground water recharge & which is located dietic/kitvhen department .(Building of the hospital)
-Onlly part of the rain water runoff is directed into in the reported pit. No design drawing could be provided at the time of the inspection.
'B'- The stated recharge pit is found to be filled with sludge. No inlet to the stated pit was observed. As per the physical observation the reported pit does not appear to be rain water harvesting pit.
-The said pit is within the building premises with no practical feasibility of its maintenance.
-open surface drain covers with iron grill (jali) along the kitchen/dietic department building was found to be carrying waste water.



	03.
	NCERT (Maintained by CPWD), EE Civil, DIV. 5, Director NCERT AurobindoMarg, New Delhi.


	Inspecting Official

Sh.K.Kumar (EE,DPCC)
A.K.Verma (SEE,DJB)
Representative Authority

 Sh. R.K. Aggarwal (AE), Sh. Parmanand (JEE)


	09
	1. Installation of RWHs. Nine Nos. of RWHs fot the purpose of ground water recharge.
2. Seven structures consist of recharge trenchs will rechage bore, two Nos. of rain water harvesting structures in baratghar do not have recharge bore.(As reported).
3. One of the recharge chamber in the baratghar within the kitchen area was found filled with waste water. 
4. Recharge structures in the baratghar within the enclosed premises making their maintenance difficult.
5. Only part of the roof top of the baratghar is connected with the recharge pits.
6. Recharge structure has gate no 1 and in mini forest are connected with the storm water drainage system. however, appropriate meaures are need for diversion of rain water run off into recharge trenches.
7. Other recharge structures need to be suitably connected for bringing rain water run off from the adjoining buildings and road water run off in the recharge pits.
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